## Unit Performance
Determination of Typical AC and HP Performance by SEER Level
for Residential Applications
The building simulation models used in this analysis are based on the single-family residential models developed for the 2001 DEER Update Study.
The 2001 DEER models were improved with detailed HVAC performance data and utilize the latest DOE2.2 simulation program. Building
characteristics for the models were translated from the forecasting climate zones used in the 2001 report to the standard Title-24 climate zones.
99 actual AC and HP units were simulated for the 16 Title-24 climate zones and 4 vintages. These units were based on analysis of more than 600
air-conditioners and heat pumps.
| A/C Units | no. of Units |  | HP Units | no. of Units
| SEER 10 | 65 |  | SEER 10 | 49
| SEER 13 | 63 |  | SEER 13 | 57
| SEER 14 | 20 |  | SEER 14 | 17
| SEER 15 | 14 |  | SEER 15 | 13
| SEER 16 | 77 |  | SEER 16 | 33
| SEER 17 | 55 |  | SEER 17 | 6
| SEER 18 | 18 |  | SEER 18 | 16
The performance of the 500+ units examined were distilled down to 99 individual units. Single-speed units were grouped by the slope
of the EER curve and the value of the cycling degradation coefficient. Two-speed units were chosen by manufacture and rated EER.
Details on the simulation inputs for these units can be found on the "AC-HP Unit Data" tab.
A median performing unit was chosen for each SEER level, based on its performance in each climate zone and for each house vintage.
The criteria for selecting the median unit is based on minimizing the maximum and RMS error associated with using a single unit
across all climate zones and construction vintages. The table below shows the results of this selection process.
Table 1. Median Unit Selection | [6 empty] | Median
Unit | Efficiency |  |  | Median | Maximum | RMS | Demand
Type | Level | Type | EER | Unit | Error | Error | Unit
AC | SEER 10 | 1-Speed | 9.17 | SA-10-HH | 2.925% | 0.902% | SA-10-HH
AC | SEER 13 | 1-Speed | 11.09 | SA-13-ML | 2.721% | 2.063% | SA-13-ML
AC | SEER 14 | 1-Speed | 12.15 | SA-14-ML | 1.859% | 0.9979% | SA-14-ML
AC | SEER 15 | 1-Speed | 12.72 | SA-15-ML | 1.893% | 0.9165% | SA-15-MM
AC | SEER 16 | 2-Speed | 11.61 | SA-16-LL | 4.285% | 1.302% | SA-16-LL
AC | SEER 17 | 2-Speed | 12.28 | SA-17-LL | 5.919% | 1.916% | SA-17-LL
AC | SEER 18 | 2-Speed | 13.37 | SA-18-TM | 4.621% | 2.334% | SA-18-TM
HP | SEER 10 | 1-Speed | 9.01 | SH-10-MM | 2.484% | 1.591% | SH-10-MM
HP | SEER 13 | 1-Speed | 11.07 | SH-13-MM | 3.789% | 2.314% | SH-13-MM
HP | SEER 14 | 1-Speed | 12.19 | SH-14-HM | 4.58% | 3.48% | SH-14-HM
HP | SEER 15 | 1-Speed | 12.7 | SH-15-ML | 4.754% | 2.761% | SH-15-ML
HP | SEER 16 | 2-Speed | 12.06 | SH-16-LM | 5.336% | 3.859% | SH-16-CH
HP | SEER 17 | 2-Speed | 12.52 | SH-17-TH | 14.57% | 12.14% | SH-17-TH
HP | SEER 18 | 2-Speed | 12.88 | SH-18-LM | 3.891% | 2.65% | SH-18-LM
Notes: | ● the AC units in table 1 were chosen based on Cooling energy + Supply Fan energy during Cooling
● the HP units in table 1 chosen based on Annual outdoor unit energy + Supply Fan energy
● "Maximum Error" is the largest deviation of the chosen unit's energy use from the mean across all
climate zones and vintages
● RMS Error is the standard deviation of the chosen unit's energy use compared to the mean across
all climate zones and vintages

## Results All Units
This worksheet compares the energy use of all the simulated AC or HP units for a given Climate Zone and Vintage
The higher SEER, two-speed units are in blue, and the single speed units are in red. The median unit
choosen within a SEER level is outlined. Demand values can also be chosen as the "Plot" variable.
| Unit Type |  | Climate Zone |  |  |  | Vintage |  | Plot
| Notes: | ● the units in red are single-speed compressors
● the units in blue are higher-SEER, two-speed compressors
● the median units (circled) were chosen based on Outdoor Unit energy + Supply Fan energy during Cooling
for AC units, and Outdoor Unit energy + Supply Fan for HP units
● there is no cooling load in CZ01, and therefore no cooling energy use
Chart Data:
| CZ09 | 9 |  | V5 | 5 |  | 1 | 4 | 2 |  | 1 | 1 | 1=kWh,2=kW,3=HP Cool Only kWh)
Outdoor Unit + Indoor Fan (Clg Only) kWh
| Min | 1410.7659 | 1400 | 200 |  |  | AC
| Max | 2256.6129 | 2400
| Title: | AC Energy Use, Region: CZ09 Vintage: Weighted
|  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 5 | Unit 6 | Unit 7 | Unit 8 | Unit 9 |  | Median Unit
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | SEER 10 | SA-10-LL | SA-10-LM | SA-10-LH | SA-10-ML | SA-10-MM | SA-10-MH | SA-10-HL | SA-10-HM | SA-10-HH |  | SA-10-HH | median
| SEER 10 (EER 9.17) | 2199.3659 | 2050.8916 | 2026.1663 | 2253.8322 | 2019.8942 | 2052.8923 | 2256.6129 | 2203.3279 | 2182.0931 |  | 2182.0931
2182.0931
2 | SEER 13 | SA-13-LL | SA-13-LM | SA-13-LH | SA-13-ML | SA-13-MM | SA-13-MH | SA-13-HL | SA-13-HM | SA-13-HH |  | SA-13-ML | median
| SEER 13 (EER 11.09) | 1651.2858 | 1631.285 | 1568.2386 | 1645.0042 | 1596.8979 | 1607.8348 | 1631.3265 | 1675.1345 | 1684.8014 |  | 1645.0042
1645.0042
3 | SEER 14 | SA-14-ML | SA-14-MM | SA-14-MH | SA-14-HL | SA-14-HM | SA-14-HH | na | na | na |  | SA-14-ML | median
| SEER 14 (EER 12.15) | 1516.2653 | 1509.8548 | 1557.938 | 1526.309 | 1535.2476 | 1606.5327 |  |  |  |  | 1516.2653
1516.2653
4 | SEER 15 | SA-15-ML | SA-15-MM | SA-15-MH | SA-15-HL | SA-15-HM | SA-15-HH | na | na | na |  | SA-15-ML | median
| SEER 15 (EER 12.72) | 1437.1946 | 1410.7659 | 1435.6547 | 1414.1555 | 1456.8633 | 1458.5455 |  |  |  |  | 1437.1946
1437.1946
5 | SEER 16 | SA-16-CL | SA-16-CM | SA-16-CH | SA-16-LL | SA-16-LM | SA-16-LH | SA-16-NM | SA-16-TL | SA-16-TH |  | SA-16-LL | median
| SEER 16 (EER 11.61) | 1663.2523 | 1712.9433 | 1748.7996 | 1632.1758 | 1614.1402 | 1542.1945 | 1478.3536 | 1709.0626 | 1836.8457 |  | 1632.1758
1632.1758
6 | SEER 17 | SA-17-CL | SA-17-CM | SA-17-CH | SA-17-LL | SA-17-LM | SA-17-LH | SA-17-TL | SA-17-TM | SA-17-TH |  | SA-17-LL | median
| SEER 17 (EER 12.28) | 1615.6798 | 1638.5187 | 1614.12 | 1563.9551 | 1553.6937 | 1488.3462 | 1456.0337 | 1733.5096 | 1538.0269 |  | 1563.9551
1563.9551
7 | SEER 18 | SA-18-LL | SA-18-LH | SA-18-TL | SA-18-TM | SA-18-TH | na | na | na | na |  | SA-18-TM | median
| SEER 18 (EER 13.37) | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: 1414.4506; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 2 2: 1466.6406; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 3 3: 1605.9026; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 4 4: 1521.874; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: 1489.7101 |  | 1521.874
1521.874
|  | Control Labels: Climate Zones |  |  |  | Control Labels: Vintages |  |  |  | Control Labels: Plot
| CZ01 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ01, Arcata (North Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: V1; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 6 6: Vintage: Pre-1978; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 9 9: Outdoor Unit + Ind Fan (Clg Only)
| CZ02 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ02, Santa Rosa (North Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: V2; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 6 6: Vintage: 1978-1992; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 9 9: Peak Demand (during Heat Wave)
| CZ03 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ03, Oakland (North Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: V3; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 6 6: Vintage: 1992-1998
| CZ04 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ04, Sunnyvale (North Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: V4; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 6 6: Vintage: Post-1998; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 9 9: Control Labels: Unit Type
| CZ05 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ05, Santa Maria (North Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: V5; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 6 6: Vintage: Weighted; AC Energy Use, Region: CZ09 Vintage: Weighted Unit 9 9: AC
| CZ06 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ06, Los Angeles (South Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 9 9: HP
| CZ07 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ07, San Diego (South Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: Y-axis Labels
| CZ08 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ08, El Toro (South Coast); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: Outdoor Unit + Indoor Fan (Clg Only) kWh
| CZ09 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ09, Pasadena (South Inland); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: Outdoor Unit + Indoor Fan (Cool + Heat) kWh
| CZ10 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ10, Riverside (South Inland); AC Energy Use, Region: CZ09 Vintage: Weighted Unit 5 5: Peak Demand (during Heat Wave)
| CZ11 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ11, Red Bluff (Central Valley)
| CZ12 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ12, Sacramento (Central Valley)
| CZ13 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ13, Fresno (Central Valley)
| CZ14 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ14, China Lake (Desert)
| CZ15 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ15, El Centro (Desert)
| CZ16 | AC Energy Use, Region: CZ09 Vintage: Weighted Unit 1 1: CZ16, Mount Shasta (North Coast)

## Results All CZs
Energy Use and Demand Comparison
This worksheet presents energy and demand values for all of the units within a given SEER level across all climate zones.
Values in these graphs have been normalized to the median unit demand or energy use within the same climate zone and
vintage. The unit labels (e.g. SA-13-LL) refer to the unit IDs in the "AC-HP Unit Data" tab, the value in parenthesis are
the unit EERs.
Type: |  |  | AC SEER Level: |  |  |  |  | Building Vintage: |  |  |  | Non-Normalized versions of the same graphs:
"Median" is the unit chosen to represent this SEER level. (SA-10-HH)
| Median Unit: | SA-10-HH
"Max-Dem" is the unit with the maximum average normalized demand across all vintages and climate zones.
"Min-Dem" is the unit with the minimum average normalized demand across all vintages and climate zones.
"Max-En" is the unit with the maximum average normalized energy across all vintages and climate zones.
"Min-En" is the unit with the minimum average normalized energy use across all vintages and climate zones.
| seer level |  | Vint |  | Type |  | DataCol |  | AC |  | Min | 0.7978 | 0.75 | 0.05 | Min | 0.91777 | 0.9 | 0.05
| 1 | (1-7) | 5 | (1-4) | 1 | (1-2) | 4 |  | HP |  | Max | 1.294 | 1.3 |  | Max | 1.0759 | 1.1
| 10 |  | Vintage: Weighted |  | AC | [34 empty] | SA-10-HL | SA-10-MH
SEER |  | SA-10-LL (8.87) | SA-10-LM (9.29) | SA-10-LH (9.51) | SA-10-ML (8.77) | SA-10-MM (9.08) | SA-10-MH (9.83) | SA-10-HL (8.46) | SA-10-HM (8.79) | SA-10-HH (9.17) | 8.46 | 9.83 | 9.17
[11 empty] | average | [28 empty] | average
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | max | min | Median | [17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | max | min | Median
|  | SA-10-LL | SA-10-LM | SA-10-LH | SA-10-ML | SA-10-MM | SA-10-MH | SA-10-HL | SA-10-HM | SA-10-HH | SA-10-HL | SA-10-MH | SA-10-HH |  |  |  |  | SA-10-LL | SA-10-LM | SA-10-LH | SA-10-ML | SA-10-MM | SA-10-MH | SA-10-HL | SA-10-HM | SA-10-HH | Max-Dem (8.46)) | Min-Dem (9.83) |  |  | SA-10-LL | SA-10-LM | SA-10-LH | SA-10-ML | SA-10-MM | SA-10-MH | SA-10-HL | SA-10-HM | SA-10-HH | SA-10-ML | SA-10-MM | SA-10-HH |  | SA-10-LL | SA-10-LM | SA-10-LH | SA-10-ML | SA-10-MM | SA-10-MH | SA-10-HL | SA-10-HM | SA-10-HH | Max-En | Min-En
1 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1 | CZ02 | 4.0582 | 3.781 | 3.74 | 4.1275 | 3.8071 | 3.6406 | 4.2897 | 4.0178 | 3.8336 | 4.2897 | 3.6406 | 3.8336 |  |  |  | CZ02 | 1.0586 | 0.98627 | 0.97557 | 1.0766 | 0.99307 | 0.94965 | 1.119 | 1.048 | 1 | 1.119 | 0.94965 |  | CZ02 | 1456.2053 | 1416.134 | 1413.2931 | 1494.2169 | 1421.2738 | 1419.6224 | 1495.9053 | 1466.1015 | 1440.0708 | 1494.2169 | 1421.2738 | 1440.0708 | CZ02 | 1.0112 | 0.98338 | 0.98141 | 1.0376 | 0.98695 | 0.9858 | 1.0388 | 1.0181 | 1 | 1.0376 | 0.98695
1 | CZ03 | 2.2673 | 2.1534 | 2.1086 | 2.3136 | 2.0453 | 2.1079 | 2.2472 | 2.2375 | 2.2029 | 2.2472 | 2.1079 | 2.2029 |  |  |  | CZ03 | 1.0292 | 0.97755 | 0.95721 | 1.0503 | 0.92846 | 0.9569 | 1.0201 | 1.0157 | 1 | 1.0201 | 0.9569 |  | CZ03 | 327.6699 | 312.6413 | 309.947 | 332.0421 | 305.7687 | 316.452 | 322.6924 | 323.451 | 324.7956 | 332.0421 | 305.7687 | 324.7956 | CZ03 | 1.0088 | 0.96258 | 0.95428 | 1.0223 | 0.94142 | 0.97431 | 0.99352 | 0.99586 | 1 | 1.0223 | 0.94142
1 | CZ04 | 3.734 | 3.4273 | 3.332 | 3.7934 | 3.4274 | 3.2732 | 3.7878 | 3.6413 | 3.5663 | 3.7878 | 3.2732 | 3.5663 |  |  |  | CZ04 | 1.047 | 0.96101 | 0.9343 | 1.0637 | 0.96105 | 0.9178 | 1.0621 | 1.021 | 1 | 1.0621 | 0.9178 |  | CZ04 | 1267.5235 | 1205.4988 | 1185.7231 | 1289.824 | 1183.3537 | 1205.3722 | 1263.7457 | 1257.9797 | 1272.0892 | 1289.824 | 1183.3537 | 1272.0892 | CZ04 | 0.99641 | 0.94765 | 0.93211 | 1.0139 | 0.93024 | 0.94755 | 0.99344 | 0.98891 | 1 | 1.0139 | 0.93024
1 | CZ05 | 2.5116 | 2.3662 | 2.3393 | 2.5383 | 2.3225 | 2.323 | 2.4878 | 2.4596 | 2.3881 | 2.4878 | 2.323 | 2.3881 |  |  |  | CZ05 | 1.0517 | 0.99084 | 0.97956 | 1.0629 | 0.97253 | 0.97276 | 1.0418 | 1.0299 | 1 | 1.0418 | 0.97276 |  | CZ05 | 277.796 | 266.5307 | 264.4612 | 280.4493 | 261.3752 | 270.6153 | 270.9298 | 272.9857 | 275.7985 | 280.4493 | 261.3752 | 275.7985 | CZ05 | 1.0072 | 0.9664 | 0.95889 | 1.0169 | 0.9477 | 0.98121 | 0.98235 | 0.9898 | 1 | 1.0169 | 0.9477
1 | CZ06 | 1.8806 | 1.7798 | 1.7466 | 1.8967 | 1.7256 | 1.7311 | 1.8221 | 1.8241 | 1.7951 | 1.8221 | 1.7311 | 1.7951 |  |  |  | CZ06 | 1.0477 | 0.99148 | 0.973 | 1.0566 | 0.96128 | 0.96436 | 1.0151 | 1.0162 | 1 | 1.0151 | 0.96436 |  | CZ06 | 785.1407 | 754.7057 | 743.9819 | 789.6776 | 736.7782 | 759.2968 | 763.8354 | 769.6439 | 780.6359 | 789.6776 | 736.7782 | 780.6359 | CZ06 | 1.0058 | 0.96678 | 0.95305 | 1.0116 | 0.94382 | 0.97266 | 0.97848 | 0.98592 | 1 | 1.0116 | 0.94382
1 | CZ07 | 2.4288 | 2.3164 | 2.275 | 2.4658 | 2.2683 | 2.2377 | 2.3949 | 2.3605 | 2.3255 | 2.3949 | 2.2377 | 2.3255 |  |  |  | CZ07 | 1.0444 | 0.99609 | 0.97827 | 1.0603 | 0.97542 | 0.96225 | 1.0298 | 1.0151 | 1 | 1.0298 | 0.96225 |  | CZ07 | 1073.7336 | 1028.9665 | 1013.2603 | 1083.8653 | 1009.2428 | 1029.309 | 1053.733 | 1056.8251 | 1071.1724 | 1083.8653 | 1009.2428 | 1071.1724 | CZ07 | 1.0024 | 0.9606 | 0.94594 | 1.0118 | 0.94219 | 0.96092 | 0.98372 | 0.98661 | 1 | 1.0118 | 0.94219
1 | CZ08 | 3.4754 | 3.3 | 3.2777 | 3.5195 | 3.0851 | 3.1831 | 3.587 | 3.459 | 3.2868 | 3.587 | 3.1831 | 3.2868 |  |  |  | CZ08 | 1.0574 | 1.004 | 0.99722 | 1.0708 | 0.93863 | 0.96846 | 1.0913 | 1.0524 | 1 | 1.0913 | 0.96846 |  | CZ08 | 1741.2689 | 1643.2635 | 1615.9815 | 1775.2781 | 1598.9867 | 1635.4804 | 1749.0612 | 1731.3505 | 1735.8992 | 1775.2781 | 1598.9867 | 1735.8992 | CZ08 | 1.0031 | 0.94664 | 0.93092 | 1.0227 | 0.92113 | 0.94215 | 1.0076 | 0.99738 | 1 | 1.0227 | 0.92113
1 | CZ09 | 4.2202 | 3.8917 | 3.8101 | 4.2804 | 3.665 | 3.7308 | 4.4226 | 3.8975 | 4.052 | 4.4226 | 3.7308 | 4.052 |  |  |  | CZ09 | 1.0415 | 0.96045 | 0.94031 | 1.0564 | 0.90449 | 0.92075 | 1.0915 | 0.96188 | 1 | 1.0915 | 0.92075 |  | CZ09 | 2140.4288 | 1996.7426 | 1970.3421 | 2196.887 | 1961.1061 | 1999.1179 | 2199.01 | 2146.5669 | 2136.827 | 2196.887 | 1961.1061 | 2136.827 | CZ09 | 1.0017 | 0.93444 | 0.92209 | 1.0281 | 0.91777 | 0.93555 | 1.0291 | 1.0046 | 1 | 1.0281 | 0.91777
1 | CZ10 | 4.607 | 4.2742 | 4.2148 | 4.698 | 3.9871 | 4.1043 | 4.9866 | 4.5765 | 4.4253 | 4.9866 | 4.1043 | 4.4253 |  |  |  | CZ10 | 1.041 | 0.96585 | 0.95243 | 1.0616 | 0.90098 | 0.92746 | 1.1268 | 1.0342 | 1 | 1.1268 | 0.92746 |  | CZ10 | 2796.794 | 2690.8312 | 2677.6716 | 2882.3138 | 2666.2102 | 2689.2673 | 2918.9022 | 2838.7816 | 2788.1003 | 2882.3138 | 2666.2102 | 2788.1003 | CZ10 | 1.0031 | 0.96511 | 0.96039 | 1.0338 | 0.95628 | 0.96455 | 1.0469 | 1.0182 | 1 | 1.0338 | 0.95628
1 | CZ11 | 4.2629 | 4.0476 | 4.0088 | 4.3532 | 4.0597 | 3.9011 | 4.6184 | 4.4144 | 4.1222 | 4.6184 | 3.9011 | 4.1222 |  |  |  | CZ11 | 1.0341 | 0.98192 | 0.97249 | 1.056 | 0.98484 | 0.94637 | 1.1204 | 1.0709 | 1 | 1.1204 | 0.94637 |  | CZ11 | 3059.4397 | 3004.0686 | 2998.0151 | 3149.2325 | 3024.747 | 2994.3971 | 3198.7849 | 3113.6638 | 3041.2074 | 3149.2325 | 3024.747 | 3041.2074 | CZ11 | 1.006 | 0.98779 | 0.9858 | 1.0355 | 0.99459 | 0.98461 | 1.0518 | 1.0238 | 1 | 1.0355 | 0.99459
1 | CZ12 | 4.2074 | 3.9675 | 3.9166 | 4.2839 | 4.0115 | 3.8154 | 4.5442 | 4.221 | 4.0834 | 4.5442 | 3.8154 | 4.0834 |  |  |  | CZ12 | 1.0304 | 0.97161 | 0.95915 | 1.0491 | 0.9824 | 0.93438 | 1.1129 | 1.0337 | 1 | 1.1129 | 0.93438 |  | CZ12 | 2258.8945 | 2145.9062 | 2130.5474 | 2325.2908 | 2137.4259 | 2143.4285 | 2342.2219 | 2275.1898 | 2229.347 | 2325.2908 | 2137.4259 | 2229.347 | CZ12 | 1.0133 | 0.96257 | 0.95568 | 1.043 | 0.95877 | 0.96146 | 1.0506 | 1.0206 | 1 | 1.043 | 0.95877
1 | CZ13 | 4.5175 | 4.2442 | 4.1875 | 4.5876 | 4.3066 | 4.0744 | 4.9516 | 4.6215 | 4.4359 | 4.9516 | 4.0744 | 4.4359 |  |  |  | CZ13 | 1.0184 | 0.9568 | 0.944 | 1.0342 | 0.97086 | 0.91852 | 1.1163 | 1.0419 | 1 | 1.1163 | 0.91852 |  | CZ13 | 4406.1378 | 4207.772 | 4178.9342 | 4535.2546 | 4208.7007 | 4163.8221 | 4619.9632 | 4458.7109 | 4345.8121 | 4535.2546 | 4208.7007 | 4345.8121 | CZ13 | 1.0139 | 0.96824 | 0.9616 | 1.0436 | 0.96845 | 0.95812 | 1.0631 | 1.026 | 1 | 1.0436 | 0.96845
1 | CZ14 | 5.199 | 4.9137 | 4.8867 | 5.2801 | 4.2006 | 4.7566 | 5.8371 | 5.5445 | 5.0762 | 5.8371 | 4.7566 | 5.0762 |  |  |  | CZ14 | 1.0242 | 0.96799 | 0.96267 | 1.0402 | 0.82751 | 0.93704 | 1.1499 | 1.0923 | 1 | 1.1499 | 0.93704 |  | CZ14 | 4777.6806 | 4828.3666 | 4836.8609 | 4914.9267 | 4824.8194 | 4825.602 | 5005.6654 | 4886.845 | 4866.475 | 4914.9267 | 4824.8194 | 4866.475 | CZ14 | 0.98175 | 0.99217 | 0.99391 | 1.01 | 0.99144 | 0.9916 | 1.0286 | 1.0042 | 1 | 1.01 | 0.99144
1 | CZ15 | 5.3412 | 5.0516 | 4.9983 | 5.4481 | 4.5852 | 4.3152 | 6.1579 | 5.814 | 5.4089 | 6.1579 | 4.3152 | 5.4089 |  |  |  | CZ15 | 0.98749 | 0.93395 | 0.92409 | 1.0072 | 0.84773 | 0.7978 | 1.1385 | 1.0749 | 1 | 1.1385 | 0.7978 |  | CZ15 | 10340.0977 | 10035.6754 | 9972.6196 | 10617.4794 | 9834.6717 | 9535.0433 | 11114.1175 | 10640.5426 | 10330.5189 | 10617.4794 | 9834.6717 | 10330.5189 | CZ15 | 1.0009 | 0.97146 | 0.96536 | 1.0278 | 0.952 | 0.923 | 1.0759 | 1.03 | 1 | 1.0278 | 0.952
1 | CZ16 | 3.343 | 3.2477 | 3.2355 | 3.3983 | 3.2419 | 3.1609 | 3.4251 | 3.3589 | 3.2188 | 3.4251 | 3.1609 | 3.2188 |  |  |  | CZ16 | 1.0386 | 1.009 | 1.0052 | 1.0558 | 1.0072 | 0.982 | 1.0641 | 1.0435 | 1 | 1.0641 | 0.982 |  | CZ16 | 937.7874 | 930.675 | 931.8929 | 959.8222 | 938.6973 | 940.0151 | 947.6509 | 948.2805 | 939.9697 | 959.8222 | 938.6973 | 939.9697 | CZ16 | 0.99768 | 0.99011 | 0.99141 | 1.0211 | 0.99865 | 1 | 1.0082 | 1.0088 | 1 | 1.0211 | 0.99865
2 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | CZ02 | 3.3539 | 3.1405 | 3.1142 | 3.4227 | 3.154 | 3.0418 | 3.536 | 3.3062 | 3.1775 | 3.536 | 3.0418 | 3.1775 |  |  |  | CZ02 | 1.0555 | 0.98836 | 0.9801 | 1.0772 | 0.99262 | 0.95729 | 1.1128 | 1.0405 | 1 | 1.1128 | 0.95729 |  | CZ02 | 924.3391 | 898.1345 | 898.0173 | 949.5251 | 901.6303 | 911.6204 | 953.5008 | 931.9703 | 920.6979 | 949.5251 | 901.6303 | 920.6979 | CZ02 | 1.004 | 0.97549 | 0.97537 | 1.0313 | 0.97929 | 0.99014 | 1.0356 | 1.0122 | 1 | 1.0313 | 0.97929
2 | CZ03 | 1.5782 | 1.5168 | 1.4934 | 1.6024 | 1.4491 | 1.5042 | 1.5586 | 1.5511 | 1.5458 | 1.5586 | 1.5042 | 1.5458 |  |  |  | CZ03 | 1.021 | 0.98122 | 0.96613 | 1.0366 | 0.93746 | 0.9731 | 1.0083 | 1.0035 | 1 | 1.0083 | 0.9731 |  | CZ03 | 153.4098 | 147.6838 | 146.6207 | 155.9462 | 144.7638 | 150.7245 | 152.7769 | 152.2332 | 154.0685 | 155.9462 | 144.7638 | 154.0685 | CZ03 | 0.99572 | 0.95856 | 0.95166 | 1.0122 | 0.93961 | 0.97829 | 0.99162 | 0.98809 | 1 | 1.0122 | 0.93961
2 | CZ04 | 3.0493 | 2.7804 | 2.683 | 3.102 | 2.7314 | 2.6668 | 3.0995 | 2.9522 | 2.9523 | 3.0995 | 2.6668 | 2.9523 |  |  |  | CZ04 | 1.0329 | 0.94179 | 0.90879 | 1.0507 | 0.92519 | 0.90331 | 1.0499 | 0.99996 | 1 | 1.0499 | 0.90331 |  | CZ04 | 766.0518 | 735.6033 | 724.0435 | 780.0485 | 722.3772 | 737.1403 | 765.6707 | 761.2871 | 773.7622 | 780.0485 | 722.3772 | 773.7622 | CZ04 | 0.99004 | 0.95068 | 0.93574 | 1.0081 | 0.93359 | 0.95267 | 0.98954 | 0.98388 | 1 | 1.0081 | 0.93359
2 | CZ05 | 1.9223 | 1.8259 | 1.809 | 1.9405 | 1.7863 | 1.8092 | 1.9031 | 1.8834 | 1.8409 | 1.9031 | 1.8092 | 1.8409 |  |  |  | CZ05 | 1.0442 | 0.99188 | 0.98267 | 1.0541 | 0.97037 | 0.98278 | 1.0338 | 1.0231 | 1 | 1.0338 | 0.98278 |  | CZ05 | 121.2991 | 117.8685 | 116.8835 | 122.5477 | 115.7438 | 120.4291 | 118.9136 | 119.782 | 121.5227 | 122.5477 | 115.7438 | 121.5227 | CZ05 | 0.99816 | 0.96993 | 0.96182 | 1.0084 | 0.95245 | 0.991 | 0.97853 | 0.98568 | 1 | 1.0084 | 0.95245
2 | CZ06 | 1.7345 | 1.5638 | 1.5313 | 1.6762 | 1.5632 | 1.5102 | 1.6041 | 1.6055 | 1.5735 | 1.6041 | 1.5102 | 1.5735 |  |  |  | CZ06 | 1.1023 | 0.99378 | 0.97313 | 1.0652 | 0.9934 | 0.95972 | 1.0194 | 1.0203 | 1 | 1.0194 | 0.95972 |  | CZ06 | 534.2671 | 509.4271 | 502.1234 | 535.2077 | 498.8094 | 509.7908 | 517.3845 | 520.0555 | 527.1028 | 535.2077 | 498.8094 | 527.1028 | CZ06 | 1.0136 | 0.96647 | 0.95261 | 1.0154 | 0.94632 | 0.96716 | 0.98156 | 0.98663 | 1 | 1.0154 | 0.94632
2 | CZ07 | 2.2804 | 2.1652 | 2.1236 | 2.3084 | 2.139 | 2.0795 | 2.2359 | 2.2011 | 2.1636 | 2.2359 | 2.0795 | 2.1636 |  |  |  | CZ07 | 1.054 | 1.0007 | 0.98151 | 1.0669 | 0.98861 | 0.96112 | 1.0334 | 1.0173 | 1 | 1.0334 | 0.96112 |  | CZ07 | 802.1987 | 768.5973 | 755.6309 | 811.2816 | 754.4027 | 764.9182 | 789.2 | 789.2333 | 800.2544 | 811.2816 | 754.4027 | 800.2544 | CZ07 | 1.0024 | 0.96044 | 0.94424 | 1.0138 | 0.9427 | 0.95584 | 0.98619 | 0.98623 | 1 | 1.0138 | 0.9427
2 | CZ08 | 3.0575 | 2.8752 | 2.8541 | 3.0821 | 2.8482 | 2.7702 | 3.1465 | 3.0298 | 2.8776 | 3.1465 | 2.7702 | 2.8776 |  |  |  | CZ08 | 1.0625 | 0.99917 | 0.99184 | 1.0711 | 0.98977 | 0.96267 | 1.0934 | 1.0529 | 1 | 1.0934 | 0.96267 |  | CZ08 | 1415.4055 | 1331.6334 | 1308.2121 | 1442.7922 | 1304.4479 | 1319.9038 | 1421.6302 | 1401.8356 | 1406.4554 | 1442.7922 | 1304.4479 | 1406.4554 | CZ08 | 1.0064 | 0.9468 | 0.93015 | 1.0258 | 0.92747 | 0.93846 | 1.0108 | 0.99672 | 1 | 1.0258 | 0.92747
2 | CZ09 | 3.8882 | 3.6029 | 3.5381 | 3.9429 | 3.5985 | 3.4579 | 4.0629 | 3.5824 | 3.7207 | 4.0629 | 3.4579 | 3.7207 |  |  |  | CZ09 | 1.045 | 0.96835 | 0.95094 | 1.0597 | 0.96716 | 0.92938 | 1.092 | 0.96283 | 1 | 1.092 | 0.92938 |  | CZ09 | 2145.3149 | 1998.4734 | 1974.26 | 2198.8565 | 1974.5995 | 1999.585 | 2199.5187 | 2145.2312 | 2124.0586 | 2198.8565 | 1974.5995 | 2124.0586 | CZ09 | 1.01 | 0.94087 | 0.92948 | 1.0352 | 0.92964 | 0.9414 | 1.0355 | 1.01 | 1 | 1.0352 | 0.92964
2 | CZ10 | 4.1828 | 3.9061 | 3.8615 | 4.2754 | 3.4266 | 3.7595 | 4.5101 | 4.1271 | 4.0268 | 4.5101 | 3.7595 | 4.0268 |  |  |  | CZ10 | 1.0388 | 0.97002 | 0.95894 | 1.0617 | 0.85094 | 0.93363 | 1.12 | 1.0249 | 1 | 1.12 | 0.93363 |  | CZ10 | 2722.916 | 2609.463 | 2597.6629 | 2803.2789 | 2569.8693 | 2608.6637 | 2836.0265 | 2754.5598 | 2698.2567 | 2803.2789 | 2569.8693 | 2698.2567 | CZ10 | 1.0091 | 0.96709 | 0.96272 | 1.0389 | 0.95242 | 0.9668 | 1.0511 | 1.0209 | 1 | 1.0389 | 0.95242
2 | CZ11 | 3.737 | 3.5411 | 3.5109 | 3.8073 | 3.5354 | 3.4174 | 4.0428 | 3.8639 | 3.607 | 4.0428 | 3.4174 | 3.607 |  |  |  | CZ11 | 1.036 | 0.98172 | 0.97336 | 1.0555 | 0.98015 | 0.94744 | 1.1208 | 1.0712 | 1 | 1.1208 | 0.94744 |  | CZ11 | 2999.433 | 2927.0168 | 2920.4732 | 3083.4679 | 2949.0855 | 2913.2865 | 3123.2068 | 3039.3176 | 2966.8645 | 3083.4679 | 2949.0855 | 2966.8645 | CZ11 | 1.011 | 0.98657 | 0.98436 | 1.0393 | 0.99401 | 0.98194 | 1.0527 | 1.0244 | 1 | 1.0393 | 0.99401
2 | CZ12 | 3.6908 | 3.4766 | 3.4358 | 3.7562 | 3.5148 | 3.3477 | 3.977 | 3.672 | 3.5814 | 3.977 | 3.3477 | 3.5814 |  |  |  | CZ12 | 1.0306 | 0.97074 | 0.95934 | 1.0488 | 0.9814 | 0.93474 | 1.1105 | 1.0253 | 1 | 1.1105 | 0.93474 |  | CZ12 | 2254.2739 | 2131.2924 | 2115.4724 | 2315.9393 | 2120.8835 | 2124.9866 | 2325.539 | 2258.6831 | 2210.0627 | 2315.9393 | 2120.8835 | 2210.0627 | CZ12 | 1.02 | 0.96436 | 0.9572 | 1.0479 | 0.95965 | 0.96151 | 1.0523 | 1.022 | 1 | 1.0479 | 0.95965
2 | CZ13 | 3.9354 | 3.6984 | 3.6558 | 4.0033 | 3.5934 | 3.556 | 4.3112 | 4.0142 | 3.86 | 4.3112 | 3.556 | 3.86 |  |  |  | CZ13 | 1.0195 | 0.95815 | 0.9471 | 1.0371 | 0.93094 | 0.92125 | 1.1169 | 1.0399 | 1 | 1.1169 | 0.92125 |  | CZ13 | 4226.4857 | 4014.8182 | 3985.5665 | 4346.296 | 3992.1755 | 3969.567 | 4413.155 | 4252.7857 | 4140.4283 | 4346.296 | 3992.1755 | 4140.4283 | CZ13 | 1.0208 | 0.96966 | 0.9626 | 1.0497 | 0.96419 | 0.95873 | 1.0659 | 1.0271 | 1 | 1.0497 | 0.96419
2 | CZ14 | 4.4921 | 3.8981 | 3.8809 | 4.1866 | 3.6968 | 3.7796 | 5.0218 | 4.7679 | 4.0055 | 5.0218 | 3.7796 | 4.0055 |  |  |  | CZ14 | 1.1215 | 0.97318 | 0.96888 | 1.0452 | 0.92293 | 0.9436 | 1.2537 | 1.1903 | 1 | 1.2537 | 0.9436 |  | CZ14 | 3567.0259 | 3585.7385 | 3595.4286 | 3637.0093 | 3677.528 | 3599.6048 | 3744.5943 | 3662.1302 | 3621.3719 | 3637.0093 | 3677.528 | 3621.3719 | CZ14 | 0.98499 | 0.99016 | 0.99284 | 1.0043 | 1.0155 | 0.99399 | 1.034 | 1.0113 | 1 | 1.0043 | 1.0155
2 | CZ15 | 4.2273 | 3.9948 | 3.9593 | 4.3097 | 3.9676 | 3.8498 | 4.8798 | 4.6074 | 4.2618 | 4.8798 | 3.8498 | 4.2618 |  |  |  | CZ15 | 0.9919 | 0.93736 | 0.92904 | 1.0112 | 0.93097 | 0.90334 | 1.145 | 1.0811 | 1 | 1.145 | 0.90334 |  | CZ15 | 8180.1226 | 7948.5107 | 7904.0832 | 8413.282 | 8021.503 | 7849.6457 | 8785.9432 | 8401.4732 | 8166.3556 | 8413.282 | 8021.503 | 8166.3556 | CZ15 | 1.0017 | 0.97332 | 0.96788 | 1.0302 | 0.98226 | 0.96122 | 1.0759 | 1.0288 | 1 | 1.0302 | 0.98226
2 | CZ16 | 2.504 | 2.4372 | 2.4323 | 2.5458 | 2.4848 | 2.3995 | 2.5682 | 2.5066 | 2.4246 | 2.5682 | 2.3995 | 2.4246 |  |  |  | CZ16 | 1.0328 | 1.0052 | 1.0032 | 1.05 | 1.0248 | 0.98965 | 1.0592 | 1.0338 | 1 | 1.0592 | 0.98965 |  | CZ16 | 569.6315 | 564.0834 | 565.6068 | 583.7347 | 569.4785 | 575.8551 | 578.9741 | 579.7443 | 573.3603 | 583.7347 | 569.4785 | 573.3603 | CZ16 | 0.9935 | 0.98382 | 0.98648 | 1.0181 | 0.99323 | 1.0044 | 1.0098 | 1.0111 | 1 | 1.0181 | 0.99323
3 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | CZ02 | 3.9481 | 3.7288 | 3.7033 | 3.9956 | 3.426 | 3.6049 | 4.1384 | 3.8479 | 3.7681 | 4.1384 | 3.6049 | 3.7681 |  |  |  | CZ02 | 1.0478 | 0.9896 | 0.98282 | 1.0604 | 0.90922 | 0.9567 | 1.0983 | 1.0212 | 1 | 1.0983 | 0.9567 |  | CZ02 | 1796.4183 | 1742.0408 | 1741.7542 | 1835.6898 | 1730.5324 | 1744.2046 | 1830.851 | 1797.52 | 1762.5204 | 1835.6898 | 1730.5324 | 1762.5204 | CZ02 | 1.0192 | 0.98838 | 0.98822 | 1.0415 | 0.98185 | 0.98961 | 1.0388 | 1.0199 | 1 | 1.0415 | 0.98185
3 | CZ03 | 2.6094 | 2.4834 | 2.4382 | 2.65 | 2.3751 | 2.4139 | 2.5711 | 2.5464 | 2.503 | 2.5711 | 2.4139 | 2.503 |  |  |  | CZ03 | 1.0425 | 0.99217 | 0.97409 | 1.0587 | 0.94888 | 0.96436 | 1.0272 | 1.0173 | 1 | 1.0272 | 0.96436 |  | CZ03 | 550.6606 | 531.3233 | 527.3923 | 554.2584 | 517.0936 | 532.9031 | 537.6181 | 541.0932 | 540.0302 | 554.2584 | 517.0936 | 540.0302 | CZ03 | 1.0197 | 0.98388 | 0.9766 | 1.0263 | 0.95753 | 0.9868 | 0.99553 | 1.002 | 1 | 1.0263 | 0.95753
3 | CZ04 | 3.6054 | 3.3123 | 3.2374 | 3.6488 | 3.2862 | 3.1803 | 3.6526 | 3.455 | 3.3988 | 3.6526 | 3.1803 | 3.3988 |  |  |  | CZ04 | 1.0608 | 0.97454 | 0.9525 | 1.0735 | 0.96686 | 0.93571 | 1.0747 | 1.0165 | 1 | 1.0747 | 0.93571 |  | CZ04 | 1653.5043 | 1573.2416 | 1552.7451 | 1671.4684 | 1523.5617 | 1568.8915 | 1640.0695 | 1634.678 | 1627.4604 | 1671.4684 | 1523.5617 | 1627.4604 | CZ04 | 1.016 | 0.96669 | 0.95409 | 1.027 | 0.93616 | 0.96401 | 1.0077 | 1.0044 | 1 | 1.027 | 0.93616
3 | CZ05 | 2.918 | 2.7427 | 2.7176 | 2.9337 | 2.7041 | 2.6692 | 2.872 | 2.8264 | 2.7418 | 2.872 | 2.6692 | 2.7418 |  |  |  | CZ05 | 1.0642 | 1.0003 | 0.99114 | 1.07 | 0.98623 | 0.9735 | 1.0475 | 1.0308 | 1 | 1.0475 | 0.9735 |  | CZ05 | 521.3937 | 505.8893 | 502.7976 | 523.2156 | 495.0785 | 510.0804 | 505.1596 | 511.3675 | 511.329 | 523.2156 | 495.0785 | 511.329 | CZ05 | 1.0197 | 0.98936 | 0.98332 | 1.0232 | 0.96822 | 0.99756 | 0.98793 | 1.0001 | 1 | 1.0232 | 0.96822
3 | CZ06 | 2.4391 | 2.2862 | 2.2502 | 2.4336 | 2.26 | 2.1981 | 2.3181 | 2.3287 | 2.2554 | 2.3181 | 2.1981 | 2.2554 |  |  |  | CZ06 | 1.0814 | 1.0137 | 0.99769 | 1.079 | 1.002 | 0.97459 | 1.0278 | 1.0325 | 1 | 1.0278 | 0.97459 |  | CZ06 | 1180.6284 | 1131.7981 | 1116.0381 | 1179.2403 | 1100.709 | 1119.5424 | 1135.7464 | 1143.7759 | 1142.4181 | 1179.2403 | 1100.709 | 1142.4181 | CZ06 | 1.0334 | 0.9907 | 0.97691 | 1.0322 | 0.96349 | 0.97998 | 0.99416 | 1.0012 | 1 | 1.0322 | 0.96349
3 | CZ07 | 2.7072 | 2.5601 | 2.5209 | 2.7316 | 2.5097 | 2.4531 | 2.6485 | 2.5996 | 2.534 | 2.6485 | 2.4531 | 2.534 |  |  |  | CZ07 | 1.0684 | 1.0103 | 0.99483 | 1.078 | 0.99041 | 0.96807 | 1.0452 | 1.0259 | 1 | 1.0452 | 0.96807 |  | CZ07 | 1443.8589 | 1381.5639 | 1362.7036 | 1445.5359 | 1351.1926 | 1363.203 | 1405.0199 | 1405.4692 | 1408.7464 | 1445.5359 | 1351.1926 | 1408.7464 | CZ07 | 1.0249 | 0.9807 | 0.96732 | 1.0261 | 0.95915 | 0.96767 | 0.99735 | 0.99767 | 1 | 1.0261 | 0.95915
3 | CZ08 | 3.3303 | 3.1269 | 3.1089 | 3.3559 | 3.0688 | 3.0124 | 3.4263 | 3.3012 | 3.1335 | 3.4263 | 3.0124 | 3.1335 |  |  |  | CZ08 | 1.0628 | 0.99789 | 0.99215 | 1.071 | 0.97935 | 0.96135 | 1.0934 | 1.0535 | 1 | 1.0934 | 0.96135 |  | CZ08 | 2160.3134 | 2037.5196 | 2008.87 | 2188.3538 | 1994.3847 | 2006.0957 | 2151.4819 | 2127.6874 | 2101.6797 | 2188.3538 | 1994.3847 | 2101.6797 | CZ08 | 1.0279 | 0.96947 | 0.95584 | 1.0412 | 0.94895 | 0.95452 | 1.0237 | 1.0124 | 1 | 1.0412 | 0.94895
3 | CZ09 | 4.5596 | 3.9376 | 3.887 | 4.2554 | 3.9413 | 3.7901 | 4.7493 | 4.2364 | 4.0239 | 4.7493 | 3.7901 | 4.0239 |  |  |  | CZ09 | 1.1331 | 0.97855 | 0.96598 | 1.0575 | 0.97947 | 0.9419 | 1.1803 | 1.0528 | 1 | 1.1803 | 0.9419 |  | CZ09 | 2646.66 | 2466.2434 | 2450.2087 | 2685.2427 | 2447.1734 | 2465.4093 | 2702.8055 | 2647.4796 | 2553.2685 | 2685.2427 | 2447.1734 | 2553.2685 | CZ09 | 1.0366 | 0.96592 | 0.95964 | 1.0517 | 0.95845 | 0.96559 | 1.0586 | 1.0369 | 1 | 1.0517 | 0.95845
3 | CZ10 | 4.4035 | 4.1873 | 4.1547 | 4.5137 | 4.153 | 4.047 | 4.7325 | 4.3343 | 4.2879 | 4.7325 | 4.047 | 4.2879 |  |  |  | CZ10 | 1.027 | 0.97654 | 0.96894 | 1.0527 | 0.96854 | 0.94382 | 1.1037 | 1.0108 | 1 | 1.1037 | 0.94382 |  | CZ10 | 3209.316 | 3088.5841 | 3084.7223 | 3295.0704 | 3111.6291 | 3086.736 | 3328.6161 | 3239.5522 | 3151.266 | 3295.0704 | 3111.6291 | 3151.266 | CZ10 | 1.0184 | 0.98011 | 0.97888 | 1.0456 | 0.98742 | 0.97952 | 1.0563 | 1.028 | 1 | 1.0456 | 0.98742
3 | CZ11 | 4.1422 | 4.0539 | 4.0386 | 4.2333 | 3.8294 | 3.9454 | 4.4588 | 4.2651 | 4.1072 | 4.4588 | 3.9454 | 4.1072 |  |  |  | CZ11 | 1.0085 | 0.98702 | 0.9833 | 1.0307 | 0.93236 | 0.96061 | 1.0856 | 1.0384 | 1 | 1.0856 | 0.96061 |  | CZ11 | 2816.2592 | 2779.9924 | 2787.9275 | 2898.6044 | 2790.7873 | 2807.9654 | 2937.0645 | 2862.0886 | 2818.6046 | 2898.6044 | 2790.7873 | 2818.6046 | CZ11 | 0.99917 | 0.9863 | 0.98912 | 1.0284 | 0.99013 | 0.99623 | 1.042 | 1.0154 | 1 | 1.0284 | 0.99013
3 | CZ12 | 4.0567 | 3.8769 | 3.8525 | 4.1765 | 3.7174 | 3.771 | 4.3675 | 4.0197 | 3.9516 | 4.3675 | 3.771 | 3.9516 |  |  |  | CZ12 | 1.0266 | 0.9811 | 0.97492 | 1.0569 | 0.94073 | 0.9543 | 1.1052 | 1.0172 | 1 | 1.1052 | 0.9543 |  | CZ12 | 2105.8108 | 2016.8669 | 2014.3732 | 2161.9234 | 2005.7442 | 2038.0293 | 2172.2182 | 2113.3738 | 2072.0646 | 2161.9234 | 2005.7442 | 2072.0646 | CZ12 | 1.0163 | 0.97336 | 0.97216 | 1.0434 | 0.96799 | 0.98357 | 1.0483 | 1.0199 | 1 | 1.0434 | 0.96799
3 | CZ13 | 4.5105 | 4.3617 | 4.3279 | 4.6721 | 4.054 | 3.9433 | 4.9138 | 4.5528 | 4.4803 | 4.9138 | 3.9433 | 4.4803 |  |  |  | CZ13 | 1.0067 | 0.97353 | 0.96598 | 1.0428 | 0.90485 | 0.88014 | 1.0968 | 1.0162 | 1 | 1.0968 | 0.88014 |  | CZ13 | 4005.665 | 3860.6086 | 3857.7415 | 4124.9842 | 3843.0608 | 3830.6382 | 4186.7716 | 4042.4002 | 3945.9124 | 4124.9842 | 3843.0608 | 3945.9124 | CZ13 | 1.0151 | 0.97838 | 0.97766 | 1.0454 | 0.97393 | 0.97079 | 1.061 | 1.0245 | 1 | 1.0454 | 0.97393
3 | CZ14 | 3.9558 | 3.8657 | 3.8426 | 4.0373 | 3.3418 | 3.7746 | 4.4057 | 4.1881 | 3.9349 | 4.4057 | 3.7746 | 3.9349 |  |  |  | CZ14 | 1.0053 | 0.98241 | 0.97654 | 1.026 | 0.84927 | 0.95926 | 1.1196 | 1.0643 | 1 | 1.1196 | 0.95926 |  | CZ14 | 2905.0219 | 2973.7109 | 2992.8901 | 2993.3984 | 3030.859 | 3029.233 | 3046.0952 | 2985.0288 | 3022.8835 | 2993.3984 | 3030.859 | 3022.8835 | CZ14 | 0.96101 | 0.98373 | 0.99008 | 0.99025 | 1.0026 | 1.0021 | 1.0077 | 0.98748 | 1 | 0.99025 | 1.0026
3 | CZ15 | 4.3865 | 3.6916 | 3.6645 | 3.9707 | 3.446 | 3.5706 | 5.0485 | 4.7629 | 3.9016 | 5.0485 | 3.5706 | 3.9016 |  |  |  | CZ15 | 1.1243 | 0.94618 | 0.93923 | 1.0177 | 0.88323 | 0.91516 | 1.294 | 1.2208 | 1 | 1.294 | 0.91516 |  | CZ15 | 6625.5756 | 6467.6304 | 6452.9588 | 6785.4157 | 6530.3447 | 6459.4931 | 7113.9586 | 6833.7573 | 6617.3179 | 6785.4157 | 6530.3447 | 6617.3179 | CZ15 | 1.0012 | 0.97738 | 0.97516 | 1.0254 | 0.98686 | 0.97615 | 1.0751 | 1.0327 | 1 | 1.0254 | 0.98686
3 | CZ16 | 3.58 | 3.383 | 3.3819 | 3.5915 | 3.3155 | 3.2915 | 3.6354 | 3.5161 | 3.3575 | 3.6354 | 3.2915 | 3.3575 |  |  |  | CZ16 | 1.0663 | 1.0076 | 1.0073 | 1.0697 | 0.98751 | 0.98034 | 1.0828 | 1.0472 | 1 | 1.0828 | 0.98034 |  | CZ16 | 1254.4041 | 1246.6085 | 1249.4581 | 1281.3662 | 1260.3802 | 1253.5228 | 1258.5691 | 1260.4607 | 1256.8617 | 1281.3662 | 1260.3802 | 1256.8617 | CZ16 | 0.99804 | 0.99184 | 0.99411 | 1.0195 | 1.0028 | 0.99734 | 1.0014 | 1.0029 | 1 | 1.0195 | 1.0028
4 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | CZ02 | 3.9086 | 3.7012 | 3.6761 | 3.9653 | 3.6989 | 3.5793 | 4.0979 | 3.8127 | 3.7421 | 4.0979 | 3.5793 | 3.7421 |  |  |  | CZ02 | 1.0445 | 0.98908 | 0.98235 | 1.0597 | 0.98847 | 0.95651 | 1.0951 | 1.0189 | 1 | 1.0951 | 0.95651 |  | CZ02 | 1745.106 | 1695.3357 | 1695.2341 | 1785.3949 | 1706.2384 | 1698.6261 | 1778.8441 | 1747.8215 | 1715.1076 | 1785.3949 | 1706.2384 | 1715.1076 | CZ02 | 1.0175 | 0.98847 | 0.98841 | 1.041 | 0.99483 | 0.99039 | 1.0372 | 1.0191 | 1 | 1.041 | 0.99483
4 | CZ03 | 2.6055 | 2.4916 | 2.4514 | 2.6486 | 2.3588 | 2.4423 | 2.5751 | 2.5584 | 2.4815 | 2.5751 | 2.4423 | 2.4815 |  |  |  | CZ03 | 1.0499 | 1.004 | 0.98785 | 1.0673 | 0.95053 | 0.9842 | 1.0377 | 1.031 | 1 | 1.0377 | 0.9842 |  | CZ03 | 541.605 | 522.7546 | 519.3315 | 545.3996 | 505.4427 | 527.8066 | 529.0653 | 532.2119 | 528.7623 | 545.3996 | 505.4427 | 528.7623 | CZ03 | 1.0243 | 0.98864 | 0.98216 | 1.0315 | 0.9559 | 0.99819 | 1.0006 | 1.0065 | 1 | 1.0315 | 0.9559
4 | CZ04 | 3.8874 | 3.3133 | 3.2377 | 3.6429 | 3.2858 | 3.1806 | 3.6463 | 3.4487 | 3.4013 | 3.6463 | 3.1806 | 3.4013 |  |  |  | CZ04 | 1.1429 | 0.9741 | 0.95189 | 1.071 | 0.96604 | 0.93508 | 1.072 | 1.0139 | 1 | 1.072 | 0.93508 |  | CZ04 | 1639.0789 | 1542.3611 | 1521.5563 | 1640.1655 | 1494.902 | 1538.5384 | 1610.677 | 1605.0106 | 1603.0849 | 1640.1655 | 1494.902 | 1603.0849 | CZ04 | 1.0225 | 0.96212 | 0.94914 | 1.0231 | 0.93252 | 0.95974 | 1.0047 | 1.0012 | 1 | 1.0231 | 0.93252
4 | CZ05 | 2.9209 | 2.7616 | 2.7397 | 2.9394 | 2.6782 | 2.7098 | 2.8815 | 2.8424 | 2.7173 | 2.8815 | 2.7098 | 2.7173 |  |  |  | CZ05 | 1.0749 | 1.0163 | 1.0083 | 1.0817 | 0.98563 | 0.99722 | 1.0604 | 1.046 | 1 | 1.0604 | 0.99722 |  | CZ05 | 508.0125 | 494.9449 | 492.0494 | 510.3954 | 477.7445 | 501.6127 | 493.0122 | 499.5818 | 494.6119 | 510.3954 | 477.7445 | 494.6119 | CZ05 | 1.0271 | 1.0007 | 0.99482 | 1.0319 | 0.9659 | 1.0142 | 0.99677 | 1.01 | 1 | 1.0319 | 0.9659
4 | CZ06 | 2.5297 | 2.4306 | 2.3929 | 2.5339 | 2.3224 | 2.3485 | 2.4631 | 2.4743 | 2.3539 | 2.4631 | 2.3485 | 2.3539 |  |  |  | CZ06 | 1.0747 | 1.0326 | 1.0166 | 1.0765 | 0.98662 | 0.99771 | 1.0464 | 1.0511 | 1 | 1.0464 | 0.99771 |  | CZ06 | 1164.89 | 1127.2232 | 1113.6298 | 1163.8567 | 1090.9254 | 1122.5468 | 1125.9052 | 1136.8208 | 1137.9087 | 1163.8567 | 1090.9254 | 1137.9087 | CZ06 | 1.0237 | 0.99061 | 0.97866 | 1.0228 | 0.95871 | 0.9865 | 0.98945 | 0.99904 | 1 | 1.0228 | 0.95871
4 | CZ07 | 2.8267 | 2.6885 | 2.6468 | 2.8569 | 2.5099 | 2.5904 | 2.7719 | 2.729 | 2.6654 | 2.7719 | 2.5904 | 2.6654 |  |  |  | CZ07 | 1.0605 | 1.0087 | 0.99302 | 1.0718 | 0.94166 | 0.97186 | 1.04 | 1.0239 | 1 | 1.04 | 0.97186 |  | CZ07 | 1431.7888 | 1379.4002 | 1361.381 | 1437.7432 | 1313.6212 | 1363.0562 | 1392.9807 | 1395.7766 | 1402.5311 | 1437.7432 | 1313.6212 | 1402.5311 | CZ07 | 1.0209 | 0.98351 | 0.97066 | 1.0251 | 0.93661 | 0.97185 | 0.99319 | 0.99518 | 1 | 1.0251 | 0.93661
4 | CZ08 | 3.3288 | 3.1262 | 3.1076 | 3.3534 | 3.0661 | 3.0114 | 3.424 | 3.296 | 3.1312 | 3.424 | 3.0114 | 3.1312 |  |  |  | CZ08 | 1.0631 | 0.9984 | 0.99246 | 1.071 | 0.97921 | 0.96174 | 1.0935 | 1.0526 | 1 | 1.0935 | 0.96174 |  | CZ08 | 2092.1434 | 1973.4998 | 1945.2416 | 2122.0498 | 1931.3377 | 1944.5746 | 2087.2182 | 2062.6827 | 2041.6091 | 2122.0498 | 1931.3377 | 2041.6091 | CZ08 | 1.0248 | 0.96664 | 0.9528 | 1.0394 | 0.94599 | 0.95247 | 1.0223 | 1.0103 | 1 | 1.0394 | 0.94599
4 | CZ09 | 4.8991 | 4.3676 | 4.315 | 5.015 | 4.3658 | 4.2129 | 5.1118 | 4.5883 | 4.4629 | 5.1118 | 4.2129 | 4.4629 |  |  |  | CZ09 | 1.0977 | 0.97865 | 0.96686 | 1.1237 | 0.97824 | 0.94398 | 1.1454 | 1.0281 | 1 | 1.1454 | 0.94398 |  | CZ09 | 2789.4987 | 2606.0768 | 2590.3906 | 2849.993 | 2580.9254 | 2615.0749 | 2847.8725 | 2790.6782 | 2709.8769 | 2849.993 | 2580.9254 | 2709.8769 | CZ09 | 1.0294 | 0.9617 | 0.95591 | 1.0517 | 0.95241 | 0.96502 | 1.0509 | 1.0298 | 1 | 1.0517 | 0.95241
4 | CZ10 | 5.1395 | 4.6576 | 4.6203 | 5.0385 | 4.6399 | 4.5091 | 5.5316 | 5.1206 | 4.7632 | 5.5316 | 4.5091 | 4.7632 |  |  |  | CZ10 | 1.079 | 0.97783 | 0.97 | 1.0578 | 0.97411 | 0.94665 | 1.1613 | 1.075 | 1 | 1.1613 | 0.94665 |  | CZ10 | 3358.2235 | 3229.6311 | 3228.3374 | 3433.9969 | 3253.9539 | 3242.9421 | 3488.8886 | 3401.5111 | 3299.3495 | 3433.9969 | 3253.9539 | 3299.3495 | CZ10 | 1.0178 | 0.97887 | 0.97848 | 1.0408 | 0.98624 | 0.9829 | 1.0574 | 1.031 | 1 | 1.0408 | 0.98624
4 | CZ11 | 3.727 | 3.6663 | 3.6517 | 3.8143 | 3.6637 | 3.5719 | 4.0132 | 3.8389 | 3.7116 | 4.0132 | 3.5719 | 3.7116 |  |  |  | CZ11 | 1.0041 | 0.9878 | 0.98386 | 1.0277 | 0.98709 | 0.96236 | 1.0813 | 1.0343 | 1 | 1.0813 | 0.96236 |  | CZ11 | 2478.6542 | 2446.9399 | 2455.2586 | 2551.4458 | 2475.1252 | 2478.0458 | 2585.666 | 2520.1806 | 2484.1905 | 2551.4458 | 2475.1252 | 2484.1905 | CZ11 | 0.99777 | 0.985 | 0.98835 | 1.0271 | 0.99635 | 0.99753 | 1.0408 | 1.0145 | 1 | 1.0271 | 0.99635
4 | CZ12 | 3.6465 | 3.5022 | 3.4807 | 3.7538 | 3.5151 | 3.4098 | 3.9255 | 3.6252 | 3.5711 | 3.9255 | 3.4098 | 3.5711 |  |  |  | CZ12 | 1.0211 | 0.98071 | 0.97469 | 1.0512 | 0.98432 | 0.95483 | 1.0992 | 1.0151 | 1 | 1.0992 | 0.95483 |  | CZ12 | 1830.3093 | 1752.8145 | 1751.1654 | 1878.7276 | 1753.8343 | 1776.247 | 1887.0925 | 1837.7622 | 1804.8081 | 1878.7276 | 1753.8343 | 1804.8081 | CZ12 | 1.0141 | 0.97119 | 0.97028 | 1.041 | 0.97176 | 0.98417 | 1.0456 | 1.0183 | 1 | 1.041 | 0.97176
4 | CZ13 | 4.0721 | 3.9461 | 3.918 | 4.2199 | 3.9381 | 3.8249 | 4.4393 | 4.1205 | 4.0568 | 4.4393 | 3.8249 | 4.0568 |  |  |  | CZ13 | 1.0038 | 0.97271 | 0.96579 | 1.0402 | 0.97074 | 0.94284 | 1.0943 | 1.0157 | 1 | 1.0943 | 0.94284 |  | CZ13 | 3559.7999 | 3430.3886 | 3428.6875 | 3666.8224 | 3442.5358 | 3453.2861 | 3721.6257 | 3593.6687 | 3512.9423 | 3666.8224 | 3442.5358 | 3512.9423 | CZ13 | 1.0133 | 0.9765 | 0.97602 | 1.0438 | 0.97996 | 0.98302 | 1.0594 | 1.023 | 1 | 1.0438 | 0.97996
4 | CZ14 | 4.7995 | 4.4378 | 4.4104 | 4.6605 | 4.259 | 4.3246 | 5.3214 | 5.0531 | 4.5135 | 5.3214 | 4.3246 | 4.5135 |  |  |  | CZ14 | 1.0634 | 0.98323 | 0.97716 | 1.0326 | 0.94361 | 0.95815 | 1.179 | 1.1196 | 1 | 1.179 | 0.95815 |  | CZ14 | 3527.7698 | 3587.8155 | 3608.472 | 3619.0738 | 3693.5859 | 3642.1118 | 3694.5666 | 3623.5525 | 3644.3896 | 3619.0738 | 3693.5859 | 3644.3896 | CZ14 | 0.968 | 0.98448 | 0.99014 | 0.99305 | 1.0135 | 0.99937 | 1.0138 | 0.99428 | 1 | 0.99305 | 1.0135
4 | CZ15 | 4.9435 | 4.6772 | 4.647 | 5.0443 | 4.0443 | 4.5236 | 5.7014 | 5.3795 | 4.9534 | 5.7014 | 4.5236 | 4.9534 |  |  |  | CZ15 | 0.998 | 0.94424 | 0.93814 | 1.0184 | 0.81647 | 0.91323 | 1.151 | 1.086 | 1 | 1.151 | 0.91323 |  | CZ15 | 7932.3893 | 7819.4045 | 7806.1398 | 8184.6344 | 7829.1544 | 7835.9895 | 8503.0824 | 8164.6012 | 8002.7345 | 8184.6344 | 7829.1544 | 8002.7345 | CZ15 | 0.99121 | 0.97709 | 0.97543 | 1.0227 | 0.97831 | 0.97916 | 1.0625 | 1.0202 | 1 | 1.0227 | 0.97831
4 | CZ16 | 3.572 | 3.3786 | 3.3772 | 3.5852 | 3.3101 | 3.2872 | 3.6297 | 3.509 | 3.3524 | 3.6297 | 3.2872 | 3.3524 |  |  |  | CZ16 | 1.0655 | 1.0078 | 1.0074 | 1.0694 | 0.98738 | 0.98054 | 1.0827 | 1.0467 | 1 | 1.0827 | 0.98054 |  | CZ16 | 1218.4751 | 1211.6202 | 1214.4973 | 1248.3892 | 1226.8676 | 1220.0738 | 1225.9953 | 1228.5486 | 1224.5932 | 1248.3892 | 1226.8676 | 1224.5932 | CZ16 | 0.995 | 0.98941 | 0.99176 | 1.0194 | 1.0019 | 0.99631 | 1.0011 | 1.0032 | 1 | 1.0194 | 1.0019
5 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | CZ02 | 3.7352 | 3.4973 | 3.4655 | 3.801 | 3.4833 | 3.3779 | 3.9378 | 3.6807 | 3.5409 | 3.9378 | 3.3779 | 3.5409 |  |  |  | CZ02 | 1.0549 | 0.98769 | 0.97872 | 1.0735 | 0.98372 | 0.95397 | 1.1121 | 1.0395 | 1 | 1.1121 | 0.95397 |  | CZ02 | 1291.6556 | 1255.1385 | 1253.9586 | 1324.5777 | 1258.5006 | 1262.7097 | 1325.8178 | 1299.0555 | 1277.7628 | 1324.5777 | 1258.5006 | 1277.7628 | CZ02 | 1.0109 | 0.98229 | 0.98137 | 1.0366 | 0.98493 | 0.98822 | 1.0376 | 1.0167 | 1 | 1.0366 | 0.98493
5 | CZ03 | 2.1403 | 2.041 | 2.0036 | 2.1777 | 1.9446 | 2.0007 | 2.1155 | 2.1026 | 2.0727 | 2.1155 | 2.0007 | 2.0727 |  |  |  | CZ03 | 1.0326 | 0.98472 | 0.96665 | 1.0507 | 0.93816 | 0.96527 | 1.0206 | 1.0144 | 1 | 1.0206 | 0.96527 |  | CZ03 | 335.6641 | 322.4735 | 319.9879 | 339.21 | 314.5011 | 325.6094 | 329.76 | 330.8729 | 331.4935 | 339.21 | 314.5011 | 331.4935 | CZ03 | 1.0126 | 0.97279 | 0.96529 | 1.0233 | 0.94874 | 0.98225 | 0.99477 | 0.99813 | 1 | 1.0233 | 0.94874
5 | CZ04 | 3.5954 | 3.2636 | 3.1718 | 3.6133 | 3.2477 | 3.1226 | 3.6102 | 3.4535 | 3.3997 | 3.6102 | 3.1226 | 3.3997 |  |  |  | CZ04 | 1.0576 | 0.95997 | 0.93296 | 1.0628 | 0.95529 | 0.91849 | 1.0619 | 1.0158 | 1 | 1.0619 | 0.91849 |  | CZ04 | 1232.0562 | 1171.2323 | 1153.0686 | 1249.5304 | 1145.9088 | 1170.7066 | 1225.2052 | 1219.7793 | 1230.0201 | 1249.5304 | 1145.9088 | 1230.0201 | CZ04 | 1.0017 | 0.95221 | 0.93744 | 1.0159 | 0.93162 | 0.95178 | 0.99609 | 0.99167 | 1 | 1.0159 | 0.93162
5 | CZ05 | 2.3057 | 2.1783 | 2.1556 | 2.3284 | 2.1351 | 2.1442 | 2.2825 | 2.2566 | 2.1944 | 2.2825 | 2.1442 | 2.1944 |  |  |  | CZ05 | 1.0507 | 0.99267 | 0.98231 | 1.0611 | 0.97296 | 0.97715 | 1.0401 | 1.0284 | 1 | 1.0401 | 0.97715 |  | CZ05 | 232.0641 | 223.6991 | 221.9961 | 234.1204 | 219.1417 | 227.2685 | 226.3698 | 228.2539 | 230.2779 | 234.1204 | 219.1417 | 230.2779 | CZ05 | 1.0078 | 0.97143 | 0.96404 | 1.0167 | 0.95164 | 0.98693 | 0.98303 | 0.99121 | 1 | 1.0167 | 0.95164
5 | CZ06 | 1.9876 | 1.8607 | 1.8267 | 1.9769 | 1.8172 | 1.8016 | 1.8999 | 1.9039 | 1.8558 | 1.8999 | 1.8016 | 1.8558 |  |  |  | CZ06 | 1.071 | 1.0026 | 0.98433 | 1.0653 | 0.97922 | 0.97081 | 1.0237 | 1.0259 | 1 | 1.0237 | 0.97081 |  | CZ06 | 803.257 | 771.7149 | 761.1321 | 805.2782 | 751.9833 | 772.0085 | 778.3939 | 784.2297 | 791.333 | 805.2782 | 751.9833 | 791.333 | CZ06 | 1.0151 | 0.97521 | 0.96184 | 1.0176 | 0.95027 | 0.97558 | 0.98365 | 0.99102 | 1 | 1.0176 | 0.95027
5 | CZ07 | 2.4807 | 2.3572 | 2.3162 | 2.5115 | 2.3057 | 2.2681 | 2.4361 | 2.3974 | 2.3522 | 2.4361 | 2.2681 | 2.3522 |  |  |  | CZ07 | 1.0546 | 1.0021 | 0.98471 | 1.0677 | 0.98024 | 0.96425 | 1.0357 | 1.0192 | 1 | 1.0357 | 0.96425 |  | CZ07 | 1108.2075 | 1061.9717 | 1046.1527 | 1115.664 | 1037.9975 | 1055.3496 | 1084.3643 | 1085.8735 | 1095.9791 | 1115.664 | 1037.9975 | 1095.9791 | CZ07 | 1.0112 | 0.96897 | 0.95454 | 1.018 | 0.9471 | 0.96293 | 0.9894 | 0.99078 | 1 | 1.018 | 0.9471
5 | CZ08 | 3.3265 | 3.1444 | 3.1232 | 3.3617 | 3.0117 | 3.0315 | 3.4287 | 3.3044 | 3.1391 | 3.4287 | 3.0315 | 3.1391 |  |  |  | CZ08 | 1.0597 | 1.0017 | 0.99492 | 1.0709 | 0.95941 | 0.96571 | 1.0923 | 1.0527 | 1 | 1.0923 | 0.96571 |  | CZ08 | 1710.4267 | 1612.7528 | 1586.4146 | 1741.5811 | 1573.8163 | 1599.9784 | 1715.2067 | 1695.8047 | 1695.5506 | 1741.5811 | 1573.8163 | 1695.5506 | CZ08 | 1.0088 | 0.95117 | 0.93563 | 1.0271 | 0.9282 | 0.94363 | 1.0116 | 1.0001 | 1 | 1.0271 | 0.9282
5 | CZ09 | 4.1794 | 3.8339 | 3.7599 | 4.2123 | 3.6894 | 3.6784 | 4.3739 | 3.8614 | 3.9756 | 4.3739 | 3.6784 | 3.9756 |  |  |  | CZ09 | 1.0513 | 0.96437 | 0.94577 | 1.0595 | 0.92803 | 0.92526 | 1.1002 | 0.97129 | 1 | 1.1002 | 0.92526 |  | CZ09 | 2199.3659 | 2050.8916 | 2026.1663 | 2253.8322 | 2019.8942 | 2052.8923 | 2256.6129 | 2203.3279 | 2182.0931 | 2253.8322 | 2019.8942 | 2182.0931 | CZ09 | 1.0079 | 0.93987 | 0.92854 | 1.0329 | 0.92567 | 0.94079 | 1.0342 | 1.0097 | 1 | 1.0329 | 0.92567
5 | CZ10 | 4.4543 | 4.1403 | 4.0944 | 4.52 | 3.8272 | 3.9884 | 4.8044 | 4.4088 | 4.2641 | 4.8044 | 3.9884 | 4.2641 |  |  |  | CZ10 | 1.0446 | 0.97097 | 0.96022 | 1.06 | 0.89755 | 0.93534 | 1.1267 | 1.0339 | 1 | 1.1267 | 0.93534 |  | CZ10 | 2890.0646 | 2775.4209 | 2765.7304 | 2971.6475 | 2756.076 | 2776.3899 | 3008.7026 | 2925.8383 | 2860.5519 | 2971.6475 | 2756.076 | 2860.5519 | CZ10 | 1.0103 | 0.97024 | 0.96685 | 1.0388 | 0.96348 | 0.97058 | 1.0518 | 1.0228 | 1 | 1.0388 | 0.96348
5 | CZ11 | 3.9957 | 3.8227 | 3.793 | 4.0787 | 3.7947 | 3.6957 | 4.3201 | 4.1299 | 3.8879 | 4.3201 | 3.6957 | 3.8879 |  |  |  | CZ11 | 1.0277 | 0.98324 | 0.9756 | 1.0491 | 0.97603 | 0.95056 | 1.1112 | 1.0622 | 1 | 1.1112 | 0.95056 |  | CZ11 | 2936.8096 | 2880.7193 | 2878.0748 | 3021.5391 | 2901.4376 | 2879.4902 | 3064.2821 | 2983.283 | 2919.0383 | 3021.5391 | 2901.4376 | 2919.0383 | CZ11 | 1.0061 | 0.98687 | 0.98597 | 1.0351 | 0.99397 | 0.98645 | 1.0498 | 1.022 | 1 | 1.0351 | 0.99397
5 | CZ12 | 3.9497 | 3.735 | 3.6935 | 4.03 | 3.7506 | 3.6022 | 4.2597 | 3.9424 | 3.8377 | 4.2597 | 3.6022 | 3.8377 |  |  |  | CZ12 | 1.0292 | 0.97323 | 0.96243 | 1.0501 | 0.9773 | 0.93864 | 1.11 | 1.0273 | 1 | 1.11 | 0.93864 |  | CZ12 | 2199.4806 | 2088.9453 | 2076.1813 | 2261.2907 | 2080.3497 | 2090.2188 | 2273.9904 | 2209.6213 | 2164.4964 | 2261.2907 | 2080.3497 | 2164.4964 | CZ12 | 1.0162 | 0.9651 | 0.9592 | 1.0447 | 0.96112 | 0.96568 | 1.0506 | 1.0208 | 1 | 1.0447 | 0.96112
5 | CZ13 | 4.2707 | 4.0456 | 4.0005 | 4.3634 | 3.9748 | 3.8444 | 4.6727 | 4.3498 | 4.2063 | 4.6727 | 3.8444 | 4.2063 |  |  |  | CZ13 | 1.0153 | 0.96179 | 0.95107 | 1.0373 | 0.94496 | 0.91395 | 1.1109 | 1.0341 | 1 | 1.1109 | 0.91395 |  | CZ13 | 4197.186 | 4009.6479 | 3987.7016 | 4319.3206 | 3999.7488 | 3973.4556 | 4390.9427 | 4235.9095 | 4128.9268 | 4319.3206 | 3999.7488 | 4128.9268 | CZ13 | 1.0165 | 0.97111 | 0.9658 | 1.0461 | 0.96871 | 0.96235 | 1.0635 | 1.0259 | 1 | 1.0461 | 0.96871
5 | CZ14 | 4.503 | 4.0059 | 3.9867 | 4.285 | 3.7207 | 3.8875 | 5.0326 | 4.779 | 4.1125 | 5.0326 | 3.8875 | 4.1125 |  |  |  | CZ14 | 1.0949 | 0.97407 | 0.96941 | 1.0419 | 0.90471 | 0.94527 | 1.2237 | 1.1621 | 1 | 1.2237 | 0.94527 |  | CZ14 | 3595.2445 | 3624.3813 | 3635.5127 | 3674.2939 | 3703.9488 | 3643.2601 | 3772.575 | 3689.8303 | 3662.6463 | 3674.2939 | 3703.9488 | 3662.6463 | CZ14 | 0.9816 | 0.98955 | 0.99259 | 1.0032 | 1.0113 | 0.99471 | 1.03 | 1.0074 | 1 | 1.0032 | 1.0113
5 | CZ15 | 4.6319 | 4.3124 | 4.2727 | 4.6499 | 4.0892 | 3.9841 | 5.342 | 5.0431 | 4.5998 | 5.342 | 3.9841 | 4.5998 |  |  |  | CZ15 | 1.007 | 0.9375 | 0.92888 | 1.0109 | 0.88898 | 0.86613 | 1.1614 | 1.0964 | 1 | 1.1614 | 0.86613 |  | CZ15 | 8623.1028 | 8384.3216 | 8339.6905 | 8860.2784 | 8366.7661 | 8176.9475 | 9263.2799 | 8867.9185 | 8615.01 | 8860.2784 | 8366.7661 | 8615.01 | CZ15 | 1.0009 | 0.97322 | 0.96804 | 1.0285 | 0.97118 | 0.94915 | 1.0752 | 1.0294 | 1 | 1.0285 | 0.97118
5 | CZ16 | 3.0848 | 2.9873 | 2.9789 | 3.1303 | 2.9924 | 2.9166 | 3.1577 | 3.0868 | 2.9643 | 3.1577 | 2.9166 | 2.9643 |  |  |  | CZ16 | 1.0406 | 1.0077 | 1.0049 | 1.056 | 1.0095 | 0.98391 | 1.0652 | 1.0413 | 1 | 1.0652 | 0.98391 |  | CZ16 | 849.1535 | 842.5029 | 844.0169 | 869.0915 | 850.3192 | 852.4014 | 858.2016 | 859.0337 | 851.9299 | 869.0915 | 850.3192 | 851.9299 | CZ16 | 0.99674 | 0.98893 | 0.99071 | 1.0201 | 0.99811 | 1.0006 | 1.0074 | 1.0083 | 1 | 1.0201 | 0.99811
The Normalized Demand Graph Data: |  | 3: SEER 10 AC - Normalized Peak Demand (Outdoor Unit + Fan) for Vintage: Weighted | [18 empty] | The Normalized Energy Graph Data: |  |  |  | SEER 10 AC - Normalized Electric Energy Use for Vintage: Weighted
0 |  | SA-10-LL (8.87) | SA-10-LM (9.29) | SA-10-LH (9.51) | SA-10-ML (8.77) | SA-10-MM (9.08) | SA-10-MH (9.83) | SA-10-HL (8.46) | SA-10-HM (8.79) | SA-10-HH (9.17) | Max-Dem (8.46)) | Min-Dem (9.83) |  |  |  |  | clean up the data to avoid errors when less than all the columns are filled | [13 empty] | SA-10-LL (8.87) | SA-10-LM (9.29) | SA-10-LH (9.51) | SA-10-ML (8.77) | SA-10-MM (9.08) | SA-10-MH (9.83) | SA-10-HL (8.46) | SA-10-HM (8.79) | SA-10-HH (9.17) | Max-Dem (8.46)) | Min-Dem (9.83) |  | clean up the data to avoid errors when less than all the columns are filled
1 | CZ01 | [9 empty] | 1 | 1 |  |  |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 to 9
2 | CZ02 | 1.0549 | 0.98769 | 0.97872 | 1.0735 | 0.98372 | 0.95397 | 1.1121 | 1.0395 | 1 | 1.1121 | 0.95397 |  |  |  |  | CZ02 | 1.0586 | 0.98627 | 0.97557 | 1.0766 | 0.99307 | 0.94965 | 1.119 | 1.048 | 1 |  |  | 2 | CZ02 | 1.0109 | 0.98229 | 0.98137 | 1.0366 | 0.98493 | 0.98822 | 1.0376 | 1.0167 | 1 | 1.0366 | 0.98493 |  | CZ02 | 1.0112 | 0.98338 | 0.98141 | 1.0376 | 0.98695 | 0.9858 | 1.0388 | 1.0181 | 1
3 | CZ03 | 1.0326 | 0.98472 | 0.96665 | 1.0507 | 0.93816 | 0.96527 | 1.0206 | 1.0144 | 1 | 1.0206 | 0.96527 |  |  |  |  | CZ03 | 1.0292 | 0.97755 | 0.95721 | 1.0503 | 0.92846 | 0.9569 | 1.0201 | 1.0157 | 1 |  |  | 3 | CZ03 | 1.0126 | 0.97279 | 0.96529 | 1.0233 | 0.94874 | 0.98225 | 0.99477 | 0.99813 | 1 | 1.0233 | 0.94874 |  | CZ03 | 1.0088 | 0.96258 | 0.95428 | 1.0223 | 0.94142 | 0.97431 | 0.99352 | 0.99586 | 1
4 | CZ04 | 1.0576 | 0.95997 | 0.93296 | 1.0628 | 0.95529 | 0.91849 | 1.0619 | 1.0158 | 1 | 1.0619 | 0.91849 |  |  |  |  | CZ04 | 1.047 | 0.96101 | 0.9343 | 1.0637 | 0.96105 | 0.9178 | 1.0621 | 1.021 | 1 |  |  | 4 | CZ04 | 1.0017 | 0.95221 | 0.93744 | 1.0159 | 0.93162 | 0.95178 | 0.99609 | 0.99167 | 1 | 1.0159 | 0.93162 |  | CZ04 | 0.99641 | 0.94765 | 0.93211 | 1.0139 | 0.93024 | 0.94755 | 0.99344 | 0.98891 | 1
5 | CZ05 | 1.0507 | 0.99267 | 0.98231 | 1.0611 | 0.97296 | 0.97715 | 1.0401 | 1.0284 | 1 | 1.0401 | 0.97715 |  |  |  |  | CZ05 | 1.0517 | 0.99084 | 0.97956 | 1.0629 | 0.97253 | 0.97276 | 1.0418 | 1.0299 | 1 |  |  | 5 | CZ05 | 1.0078 | 0.97143 | 0.96404 | 1.0167 | 0.95164 | 0.98693 | 0.98303 | 0.99121 | 1 | 1.0167 | 0.95164 |  | CZ05 | 1.0072 | 0.9664 | 0.95889 | 1.0169 | 0.9477 | 0.98121 | 0.98235 | 0.9898 | 1
6 | CZ06 | 1.071 | 1.0026 | 0.98433 | 1.0653 | 0.97922 | 0.97081 | 1.0237 | 1.0259 | 1 | 1.0237 | 0.97081 |  |  |  |  | CZ06 | 1.0477 | 0.99148 | 0.973 | 1.0566 | 0.96128 | 0.96436 | 1.0151 | 1.0162 | 1 |  |  | 6 | CZ06 | 1.0151 | 0.97521 | 0.96184 | 1.0176 | 0.95027 | 0.97558 | 0.98365 | 0.99102 | 1 | 1.0176 | 0.95027 |  | CZ06 | 1.0058 | 0.96678 | 0.95305 | 1.0116 | 0.94382 | 0.97266 | 0.97848 | 0.98592 | 1
7 | CZ07 | 1.0546 | 1.0021 | 0.98471 | 1.0677 | 0.98024 | 0.96425 | 1.0357 | 1.0192 | 1 | 1.0357 | 0.96425 |  |  |  |  | CZ07 | 1.0444 | 0.99609 | 0.97827 | 1.0603 | 0.97542 | 0.96225 | 1.0298 | 1.0151 | 1 |  |  | 7 | CZ07 | 1.0112 | 0.96897 | 0.95454 | 1.018 | 0.9471 | 0.96293 | 0.9894 | 0.99078 | 1 | 1.018 | 0.9471 |  | CZ07 | 1.0024 | 0.9606 | 0.94594 | 1.0118 | 0.94219 | 0.96092 | 0.98372 | 0.98661 | 1
8 | CZ08 | 1.0597 | 1.0017 | 0.99492 | 1.0709 | 0.95941 | 0.96571 | 1.0923 | 1.0527 | 1 | 1.0923 | 0.96571 |  |  |  |  | CZ08 | 1.0574 | 1.004 | 0.99722 | 1.0708 | 0.93863 | 0.96846 | 1.0913 | 1.0524 | 1 |  |  | 8 | CZ08 | 1.0088 | 0.95117 | 0.93563 | 1.0271 | 0.9282 | 0.94363 | 1.0116 | 1.0001 | 1 | 1.0271 | 0.9282 |  | CZ08 | 1.0031 | 0.94664 | 0.93092 | 1.0227 | 0.92113 | 0.94215 | 1.0076 | 0.99738 | 1
9 | CZ09 | 1.0513 | 0.96437 | 0.94577 | 1.0595 | 0.92803 | 0.92526 | 1.1002 | 0.97129 | 1 | 1.1002 | 0.92526 |  |  |  |  | CZ09 | 1.0415 | 0.96045 | 0.94031 | 1.0564 | 0.90449 | 0.92075 | 1.0915 | 0.96188 | 1 |  |  | 9 | CZ09 | 1.0079 | 0.93987 | 0.92854 | 1.0329 | 0.92567 | 0.94079 | 1.0342 | 1.0097 | 1 | 1.0329 | 0.92567 |  | CZ09 | 1.0017 | 0.93444 | 0.92209 | 1.0281 | 0.91777 | 0.93555 | 1.0291 | 1.0046 | 1
10 | CZ10 | 1.0446 | 0.97097 | 0.96022 | 1.06 | 0.89755 | 0.93534 | 1.1267 | 1.0339 | 1 | 1.1267 | 0.93534 |  |  |  |  | CZ10 | 1.041 | 0.96585 | 0.95243 | 1.0616 | 0.90098 | 0.92746 | 1.1268 | 1.0342 | 1 |  |  | 10 | CZ10 | 1.0103 | 0.97024 | 0.96685 | 1.0388 | 0.96348 | 0.97058 | 1.0518 | 1.0228 | 1 | 1.0388 | 0.96348 |  | CZ10 | 1.0031 | 0.96511 | 0.96039 | 1.0338 | 0.95628 | 0.96455 | 1.0469 | 1.0182 | 1
11 | CZ11 | 1.0277 | 0.98324 | 0.9756 | 1.0491 | 0.97603 | 0.95056 | 1.1112 | 1.0622 | 1 | 1.1112 | 0.95056 |  |  |  |  | CZ11 | 1.0341 | 0.98192 | 0.97249 | 1.056 | 0.98484 | 0.94637 | 1.1204 | 1.0709 | 1 |  |  | 11 | CZ11 | 1.0061 | 0.98687 | 0.98597 | 1.0351 | 0.99397 | 0.98645 | 1.0498 | 1.022 | 1 | 1.0351 | 0.99397 |  | CZ11 | 1.006 | 0.98779 | 0.9858 | 1.0355 | 0.99459 | 0.98461 | 1.0518 | 1.0238 | 1
12 | CZ12 | 1.0292 | 0.97323 | 0.96243 | 1.0501 | 0.9773 | 0.93864 | 1.11 | 1.0273 | 1 | 1.11 | 0.93864 |  |  |  |  | CZ12 | 1.0304 | 0.97161 | 0.95915 | 1.0491 | 0.9824 | 0.93438 | 1.1129 | 1.0337 | 1 |  |  | 12 | CZ12 | 1.0162 | 0.9651 | 0.9592 | 1.0447 | 0.96112 | 0.96568 | 1.0506 | 1.0208 | 1 | 1.0447 | 0.96112 |  | CZ12 | 1.0133 | 0.96257 | 0.95568 | 1.043 | 0.95877 | 0.96146 | 1.0506 | 1.0206 | 1
13 | CZ13 | 1.0153 | 0.96179 | 0.95107 | 1.0373 | 0.94496 | 0.91395 | 1.1109 | 1.0341 | 1 | 1.1109 | 0.91395 |  |  |  |  | CZ13 | 1.0184 | 0.9568 | 0.944 | 1.0342 | 0.97086 | 0.91852 | 1.1163 | 1.0419 | 1 |  |  | 13 | CZ13 | 1.0165 | 0.97111 | 0.9658 | 1.0461 | 0.96871 | 0.96235 | 1.0635 | 1.0259 | 1 | 1.0461 | 0.96871 |  | CZ13 | 1.0139 | 0.96824 | 0.9616 | 1.0436 | 0.96845 | 0.95812 | 1.0631 | 1.026 | 1
14 | CZ14 | 1.0949 | 0.97407 | 0.96941 | 1.0419 | 0.90471 | 0.94527 | 1.2237 | 1.1621 | 1 | 1.2237 | 0.94527 |  |  |  |  | CZ14 | 1.0242 | 0.96799 | 0.96267 | 1.0402 | 0.82751 | 0.93704 | 1.1499 | 1.0923 | 1 |  |  | 14 | CZ14 | 0.9816 | 0.98955 | 0.99259 | 1.0032 | 1.0113 | 0.99471 | 1.03 | 1.0074 | 1 | 1.0032 | 1.0113 |  | CZ14 | 0.98175 | 0.99217 | 0.99391 | 1.01 | 0.99144 | 0.9916 | 1.0286 | 1.0042 | 1
15 | CZ15 | 1.007 | 0.9375 | 0.92888 | 1.0109 | 0.88898 | 0.86613 | 1.1614 | 1.0964 | 1 | 1.1614 | 0.86613 |  |  |  |  | CZ15 | 0.98749 | 0.93395 | 0.92409 | 1.0072 | 0.84773 | 0.7978 | 1.1385 | 1.0749 | 1 |  |  | 15 | CZ15 | 1.0009 | 0.97322 | 0.96804 | 1.0285 | 0.97118 | 0.94915 | 1.0752 | 1.0294 | 1 | 1.0285 | 0.97118 |  | CZ15 | 1.0009 | 0.97146 | 0.96536 | 1.0278 | 0.952 | 0.923 | 1.0759 | 1.03 | 1
16 | CZ16 | 1.0406 | 1.0077 | 1.0049 | 1.056 | 1.0095 | 0.98391 | 1.0652 | 1.0413 | 1 | 1.0652 | 0.98391 |  |  |  |  | CZ16 | 1.0386 | 1.009 | 1.0052 | 1.0558 | 1.0072 | 0.982 | 1.0641 | 1.0435 | 1 |  |  | 16 | CZ16 | 0.99674 | 0.98893 | 0.99071 | 1.0201 | 0.99811 | 1.0006 | 1.0074 | 1.0083 | 1 | 1.0201 | 0.99811 |  | CZ16 | 0.99768 | 0.99011 | 0.99141 | 1.0211 | 0.99865 | 1 | 1.0082 | 1.0088 | 1
[17 empty] | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [16 empty] | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[17 empty] | CZ02 | 1.0555 | 0.98836 | 0.9801 | 1.0772 | 0.99262 | 0.95729 | 1.1128 | 1.0405 | 1 | [16 empty] | CZ02 | 1.004 | 0.97549 | 0.97537 | 1.0313 | 0.97929 | 0.99014 | 1.0356 | 1.0122 | 1
[17 empty] | CZ03 | 1.021 | 0.98122 | 0.96613 | 1.0366 | 0.93746 | 0.9731 | 1.0083 | 1.0035 | 1 | [16 empty] | CZ03 | 0.99572 | 0.95856 | 0.95166 | 1.0122 | 0.93961 | 0.97829 | 0.99162 | 0.98809 | 1
The Demand Graph Data: |  | 3: SEER 10 AC - Peak Demand (Outdoor Unit + Fan) for Vintage: Weighted | [6 empty] | CZ04 | 1.0329 | 0.94179 | 0.90879 | 1.0507 | 0.92519 | 0.90331 | 1.0499 | 0.99996 | 1 |  |  | The Normalized Energy Graph Data: |  |  |  | SEER 10 AC - Electric Energy Use for Vintage: Weighted | [9 empty] | CZ04 | 0.99004 | 0.95068 | 0.93574 | 1.0081 | 0.93359 | 0.95267 | 0.98954 | 0.98388 | 1
|  | SA-10-LL (8.87) | SA-10-LM (9.29) | SA-10-LH (9.51) | SA-10-ML (8.77) | SA-10-MM (9.08) | SA-10-MH (9.83) | SA-10-HL (8.46) | SA-10-HM (8.79) | SA-10-HH (9.17) | Median | [5 empty] | CZ05 | 1.0442 | 0.99188 | 0.98267 | 1.0541 | 0.97037 | 0.98278 | 1.0338 | 1.0231 | 1 |  |  |  |  | SA-10-LL (8.87) | SA-10-LM (9.29) | SA-10-LH (9.51) | SA-10-ML (8.77) | SA-10-MM (9.08) | SA-10-MH (9.83) | SA-10-HL (8.46) | SA-10-HM (8.79) | SA-10-HH (9.17) | Median |  |  | CZ05 | 0.99816 | 0.96993 | 0.96182 | 1.0084 | 0.95245 | 0.991 | 0.97853 | 0.98568 | 1
1 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | CZ06 | 1.1023 | 0.99378 | 0.97313 | 1.0652 | 0.9934 | 0.95972 | 1.0194 | 1.0203 | 1 |  |  | 1 | CZ01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CZ06 | 1.0136 | 0.96647 | 0.95261 | 1.0154 | 0.94632 | 0.96716 | 0.98156 | 0.98663 | 1
2 | CZ02 | 3.7352 | 3.4973 | 3.4655 | 3.801 | 3.4833 | 3.3779 | 3.9378 | 3.6807 | 3.5409 | 3.5409 | [5 empty] | CZ07 | 1.054 | 1.0007 | 0.98151 | 1.0669 | 0.98861 | 0.96112 | 1.0334 | 1.0173 | 1 |  |  | 2 | CZ02 | 1291.6556 | 1255.1385 | 1253.9586 | 1324.5777 | 1258.5006 | 1262.7097 | 1325.8178 | 1299.0555 | 1277.7628 | 1277.7628 |  |  | CZ07 | 1.0024 | 0.96044 | 0.94424 | 1.0138 | 0.9427 | 0.95584 | 0.98619 | 0.98623 | 1
3 | CZ03 | 2.1403 | 2.041 | 2.0036 | 2.1777 | 1.9446 | 2.0007 | 2.1155 | 2.1026 | 2.0727 | 2.0727 | [5 empty] | CZ08 | 1.0625 | 0.99917 | 0.99184 | 1.0711 | 0.98977 | 0.96267 | 1.0934 | 1.0529 | 1 |  |  | 3 | CZ03 | 335.6641 | 322.4735 | 319.9879 | 339.21 | 314.5011 | 325.6094 | 329.76 | 330.8729 | 331.4935 | 331.4935 |  |  | CZ08 | 1.0064 | 0.9468 | 0.93015 | 1.0258 | 0.92747 | 0.93846 | 1.0108 | 0.99672 | 1
4 | CZ04 | 3.5954 | 3.2636 | 3.1718 | 3.6133 | 3.2477 | 3.1226 | 3.6102 | 3.4535 | 3.3997 | 3.3997 | [5 empty] | CZ09 | 1.045 | 0.96835 | 0.95094 | 1.0597 | 0.96716 | 0.92938 | 1.092 | 0.96283 | 1 |  |  | 4 | CZ04 | 1232.0562 | 1171.2323 | 1153.0686 | 1249.5304 | 1145.9088 | 1170.7066 | 1225.2052 | 1219.7793 | 1230.0201 | 1230.0201 |  |  | CZ09 | 1.01 | 0.94087 | 0.92948 | 1.0352 | 0.92964 | 0.9414 | 1.0355 | 1.01 | 1
5 | CZ05 | 2.3057 | 2.1783 | 2.1556 | 2.3284 | 2.1351 | 2.1442 | 2.2825 | 2.2566 | 2.1944 | 2.1944 | [5 empty] | CZ10 | 1.0388 | 0.97002 | 0.95894 | 1.0617 | 0.85094 | 0.93363 | 1.12 | 1.0249 | 1 |  |  | 5 | CZ05 | 232.0641 | 223.6991 | 221.9961 | 234.1204 | 219.1417 | 227.2685 | 226.3698 | 228.2539 | 230.2779 | 230.2779 |  |  | CZ10 | 1.0091 | 0.96709 | 0.96272 | 1.0389 | 0.95242 | 0.9668 | 1.0511 | 1.0209 | 1
6 | CZ06 | 1.9876 | 1.8607 | 1.8267 | 1.9769 | 1.8172 | 1.8016 | 1.8999 | 1.9039 | 1.8558 | 1.8558 | [5 empty] | CZ11 | 1.036 | 0.98172 | 0.97336 | 1.0555 | 0.98015 | 0.94744 | 1.1208 | 1.0712 | 1 |  |  | 6 | CZ06 | 803.257 | 771.7149 | 761.1321 | 805.2782 | 751.9833 | 772.0085 | 778.3939 | 784.2297 | 791.333 | 791.333 |  |  | CZ11 | 1.011 | 0.98657 | 0.98436 | 1.0393 | 0.99401 | 0.98194 | 1.0527 | 1.0244 | 1
7 | CZ07 | 2.4807 | 2.3572 | 2.3162 | 2.5115 | 2.3057 | 2.2681 | 2.4361 | 2.3974 | 2.3522 | 2.3522 | [5 empty] | CZ12 | 1.0306 | 0.97074 | 0.95934 | 1.0488 | 0.9814 | 0.93474 | 1.1105 | 1.0253 | 1 |  |  | 7 | CZ07 | 1108.2075 | 1061.9717 | 1046.1527 | 1115.664 | 1037.9975 | 1055.3496 | 1084.3643 | 1085.8735 | 1095.9791 | 1095.9791 |  |  | CZ12 | 1.02 | 0.96436 | 0.9572 | 1.0479 | 0.95965 | 0.96151 | 1.0523 | 1.022 | 1
8 | CZ08 | 3.3265 | 3.1444 | 3.1232 | 3.3617 | 3.0117 | 3.0315 | 3.4287 | 3.3044 | 3.1391 | 3.1391 | [5 empty] | CZ13 | 1.0195 | 0.95815 | 0.9471 | 1.0371 | 0.93094 | 0.92125 | 1.1169 | 1.0399 | 1 |  |  | 8 | CZ08 | 1710.4267 | 1612.7528 | 1586.4146 | 1741.5811 | 1573.8163 | 1599.9784 | 1715.2067 | 1695.8047 | 1695.5506 | 1695.5506 |  |  | CZ13 | 1.0208 | 0.96966 | 0.9626 | 1.0497 | 0.96419 | 0.95873 | 1.0659 | 1.0271 | 1
9 | CZ09 | 4.1794 | 3.8339 | 3.7599 | 4.2123 | 3.6894 | 3.6784 | 4.3739 | 3.8614 | 3.9756 | 3.9756 | [5 empty] | CZ14 | 1.1215 | 0.97318 | 0.96888 | 1.0452 | 0.92293 | 0.9436 | 1.2537 | 1.1903 | 1 |  |  | 9 | CZ09 | 2199.3659 | 2050.8916 | 2026.1663 | 2253.8322 | 2019.8942 | 2052.8923 | 2256.6129 | 2203.3279 | 2182.0931 | 2182.0931 |  |  | CZ14 | 0.98499 | 0.99016 | 0.99284 | 1.0043 | 1.0155 | 0.99399 | 1.034 | 1.0113 | 1
10 | CZ10 | 4.4543 | 4.1403 | 4.0944 | 4.52 | 3.8272 | 3.9884 | 4.8044 | 4.4088 | 4.2641 | 4.2641 | [5 empty] | CZ15 | 0.9919 | 0.93736 | 0.92904 | 1.0112 | 0.93097 | 0.90334 | 1.145 | 1.0811 | 1 |  |  | 10 | CZ10 | 2890.0646 | 2775.4209 | 2765.7304 | 2971.6475 | 2756.076 | 2776.3899 | 3008.7026 | 2925.8383 | 2860.5519 | 2860.5519 |  |  | CZ15 | 1.0017 | 0.97332 | 0.96788 | 1.0302 | 0.98226 | 0.96122 | 1.0759 | 1.0288 | 1
11 | CZ11 | 3.9957 | 3.8227 | 3.793 | 4.0787 | 3.7947 | 3.6957 | 4.3201 | 4.1299 | 3.8879 | 3.8879 | [5 empty] | CZ16 | 1.0328 | 1.0052 | 1.0032 | 1.05 | 1.0248 | 0.98965 | 1.0592 | 1.0338 | 1 |  |  | 11 | CZ11 | 2936.8096 | 2880.7193 | 2878.0748 | 3021.5391 | 2901.4376 | 2879.4902 | 3064.2821 | 2983.283 | 2919.0383 | 2919.0383 |  |  | CZ16 | 0.9935 | 0.98382 | 0.98648 | 1.0181 | 0.99323 | 1.0044 | 1.0098 | 1.0111 | 1
12 | CZ12 | 3.9497 | 3.735 | 3.6935 | 4.03 | 3.7506 | 3.6022 | 4.2597 | 3.9424 | 3.8377 | 3.8377 | [5 empty] | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 12 | CZ12 | 2199.4806 | 2088.9453 | 2076.1813 | 2261.2907 | 2080.3497 | 2090.2188 | 2273.9904 | 2209.6213 | 2164.4964 | 2164.4964 |  |  | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
13 | CZ13 | 4.2707 | 4.0456 | 4.0005 | 4.3634 | 3.9748 | 3.8444 | 4.6727 | 4.3498 | 4.2063 | 4.2063 | [5 empty] | CZ02 | 1.0478 | 0.9896 | 0.98282 | 1.0604 | 0.90922 | 0.9567 | 1.0983 | 1.0212 | 1 |  |  | 13 | CZ13 | 4197.186 | 4009.6479 | 3987.7016 | 4319.3206 | 3999.7488 | 3973.4556 | 4390.9427 | 4235.9095 | 4128.9268 | 4128.9268 |  |  | CZ02 | 1.0192 | 0.98838 | 0.98822 | 1.0415 | 0.98185 | 0.98961 | 1.0388 | 1.0199 | 1
14 | CZ14 | 4.503 | 4.0059 | 3.9867 | 4.285 | 3.7207 | 3.8875 | 5.0326 | 4.779 | 4.1125 | 4.1125 | [5 empty] | CZ03 | 1.0425 | 0.99217 | 0.97409 | 1.0587 | 0.94888 | 0.96436 | 1.0272 | 1.0173 | 1 |  |  | 14 | CZ14 | 3595.2445 | 3624.3813 | 3635.5127 | 3674.2939 | 3703.9488 | 3643.2601 | 3772.575 | 3689.8303 | 3662.6463 | 3662.6463 |  |  | CZ03 | 1.0197 | 0.98388 | 0.9766 | 1.0263 | 0.95753 | 0.9868 | 0.99553 | 1.002 | 1
15 | CZ15 | 4.6319 | 4.3124 | 4.2727 | 4.6499 | 4.0892 | 3.9841 | 5.342 | 5.0431 | 4.5998 | 4.5998 | [5 empty] | CZ04 | 1.0608 | 0.97454 | 0.9525 | 1.0735 | 0.96686 | 0.93571 | 1.0747 | 1.0165 | 1 |  |  | 15 | CZ15 | 8623.1028 | 8384.3216 | 8339.6905 | 8860.2784 | 8366.7661 | 8176.9475 | 9263.2799 | 8867.9185 | 8615.01 | 8615.01 |  |  | CZ04 | 1.016 | 0.96669 | 0.95409 | 1.027 | 0.93616 | 0.96401 | 1.0077 | 1.0044 | 1
16 | CZ16 | 3.0848 | 2.9873 | 2.9789 | 3.1303 | 2.9924 | 2.9166 | 3.1577 | 3.0868 | 2.9643 | 2.9643 | [5 empty] | CZ05 | 1.0642 | 1.0003 | 0.99114 | 1.07 | 0.98623 | 0.9735 | 1.0475 | 1.0308 | 1 |  |  | 16 | CZ16 | 849.1535 | 842.5029 | 844.0169 | 869.0915 | 850.3192 | 852.4014 | 858.2016 | 859.0337 | 851.9299 | 851.9299 |  |  | CZ05 | 1.0197 | 0.98936 | 0.98332 | 1.0232 | 0.96822 | 0.99756 | 0.98793 | 1.0001 | 1
[17 empty] | CZ06 | 1.0814 | 1.0137 | 0.99769 | 1.079 | 1.002 | 0.97459 | 1.0278 | 1.0325 | 1 | [16 empty] | CZ06 | 1.0334 | 0.9907 | 0.97691 | 1.0322 | 0.96349 | 0.97998 | 0.99416 | 1.0012 | 1
Vintage weighting values: | [16 empty] | CZ07 | 1.0684 | 1.0103 | 0.99483 | 1.078 | 0.99041 | 0.96807 | 1.0452 | 1.0259 | 1 | [16 empty] | CZ07 | 1.0249 | 0.9807 | 0.96732 | 1.0261 | 0.95915 | 0.96767 | 0.99735 | 0.99767 | 1
| 1 | 1: 2; 2: 3; 3: 4; 5: AC | [6 empty] | CZ08 | 1.0628 | 0.99789 | 0.99215 | 1.071 | 0.97935 | 0.96135 | 1.0934 | 1.0535 | 1 | [16 empty] | CZ08 | 1.0279 | 0.96947 | 0.95584 | 1.0412 | 0.94895 | 0.95452 | 1.0237 | 1.0124 | 1
1 | 1 | 1: 0; 2: 0; 3: 0; 5: HP | [6 empty] | CZ09 | 1.1331 | 0.97855 | 0.96598 | 1.0575 | 0.97947 | 0.9419 | 1.1803 | 1.0528 | 1 | [16 empty] | CZ09 | 1.0366 | 0.96592 | 0.95964 | 1.0517 | 0.95845 | 0.96559 | 1.0586 | 1.0369 | 1
2 | 0.38461 | 1: 0.4232; 2: 0.097699; 3: 0.094488 | [6 empty] | CZ10 | 1.027 | 0.97654 | 0.96894 | 1.0527 | 0.96854 | 0.94382 | 1.1037 | 1.0108 | 1 | [16 empty] | CZ10 | 1.0184 | 0.98011 | 0.97888 | 1.0456 | 0.98742 | 0.97952 | 1.0563 | 1.028 | 1
3 | 0.36992 | 1: 0.33195; 2: 0.22729; 3: 0.070842 | [6 empty] | CZ11 | 1.0085 | 0.98702 | 0.9833 | 1.0307 | 0.93236 | 0.96061 | 1.0856 | 1.0384 | 1 | [16 empty] | CZ11 | 0.99917 | 0.9863 | 0.98912 | 1.0284 | 0.99013 | 0.99623 | 1.042 | 1.0154 | 1
4 | 0.58528 | 1: 0.21826; 2: 0.068364; 3: 0.1281 | [6 empty] | CZ12 | 1.0266 | 0.9811 | 0.97492 | 1.0569 | 0.94073 | 0.9543 | 1.1052 | 1.0172 | 1 | [16 empty] | CZ12 | 1.0163 | 0.97336 | 0.97216 | 1.0434 | 0.96799 | 0.98357 | 1.0483 | 1.0199 | 1
5 | 0.53336 | 1: 0.3973; 2: 0.035865; 3: 0.033477 | [6 empty] | CZ13 | 1.0067 | 0.97353 | 0.96598 | 1.0428 | 0.90485 | 0.88014 | 1.0968 | 1.0162 | 1 | [16 empty] | CZ13 | 1.0151 | 0.97838 | 0.97766 | 1.0454 | 0.97393 | 0.97079 | 1.061 | 1.0245 | 1
6 | 0.44529 | 1: 0.30764; 2: 0.093307; 3: 0.15377 | [6 empty] | CZ14 | 1.0053 | 0.98241 | 0.97654 | 1.026 | 0.84927 | 0.95926 | 1.1196 | 1.0643 | 1 | [16 empty] | CZ14 | 0.96101 | 0.98373 | 0.99008 | 0.99025 | 1.0026 | 1.0021 | 1.0077 | 0.98748 | 1
7 | 0.38433 | 1: 0.30005; 2: 0.24363; 3: 0.07199 | [6 empty] | CZ15 | 1.1243 | 0.94618 | 0.93923 | 1.0177 | 0.88323 | 0.91516 | 1.294 | 1.2208 | 1 | [16 empty] | CZ15 | 1.0012 | 0.97738 | 0.97516 | 1.0254 | 0.98686 | 0.97615 | 1.0751 | 1.0327 | 1
8 | 0.53419 | 1: 0.29756; 2: 0.10397; 3: 0.064275 | [6 empty] | CZ16 | 1.0663 | 1.0076 | 1.0073 | 1.0697 | 0.98751 | 0.98034 | 1.0828 | 1.0472 | 1 | [16 empty] | CZ16 | 0.99804 | 0.99184 | 0.99411 | 1.0195 | 1.0028 | 0.99734 | 1.0014 | 1.0029 | 1
9 | 0.63321 | 1: 0.26133; 2: 0.075547; 3: 0.029914 | [6 empty] | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [16 empty] | CZ01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
10 | 0.24895 | 1: 0.4903; 2: 0.1135; 3: 0.14725 | [6 empty] | CZ02 | 1.0445 | 0.98908 | 0.98235 | 1.0597 | 0.98847 | 0.95651 | 1.0951 | 1.0189 | 1 | [16 empty] | CZ02 | 1.0175 | 0.98847 | 0.98841 | 1.041 | 0.99483 | 0.99039 | 1.0372 | 1.0191 | 1
11 | 0.38987 | 1: 0.35714; 2: 0.13547; 3: 0.11752 | [6 empty] | CZ03 | 1.0499 | 1.004 | 0.98785 | 1.0673 | 0.95053 | 0.9842 | 1.0377 | 1.031 | 1 | [16 empty] | CZ03 | 1.0243 | 0.98864 | 0.98216 | 1.0315 | 0.9559 | 0.99819 | 1.0006 | 1.0065 | 1
12 | 0.42772 | 1: 0.3637; 2: 0.11492; 3: 0.093659 | [6 empty] | CZ04 | 1.1429 | 0.9741 | 0.95189 | 1.071 | 0.96604 | 0.93508 | 1.072 | 1.0139 | 1 | [16 empty] | CZ04 | 1.0225 | 0.96212 | 0.94914 | 1.0231 | 0.93252 | 0.95974 | 1.0047 | 1.0012 | 1
13 | 0.37598 | 1: 0.35679; 2: 0.18238; 3: 0.084856 | [6 empty] | CZ05 | 1.0749 | 1.0163 | 1.0083 | 1.0817 | 0.98563 | 0.99722 | 1.0604 | 1.046 | 1 | [16 empty] | CZ05 | 1.0271 | 1.0007 | 0.99482 | 1.0319 | 0.9659 | 1.0142 | 0.99677 | 1.01 | 1
14 | 0.09011 | 1: 0.75248; 2: 0.11994; 3: 0.037469 | [6 empty] | CZ06 | 1.0747 | 1.0326 | 1.0166 | 1.0765 | 0.98662 | 0.99771 | 1.0464 | 1.0511 | 1 | [16 empty] | CZ06 | 1.0237 | 0.99061 | 0.97866 | 1.0228 | 0.95871 | 0.9865 | 0.98945 | 0.99904 | 1
15 | 0.31525 | 1: 0.49623; 2: 0.14634; 3: 0.042177 | [6 empty] | CZ07 | 1.0605 | 1.0087 | 0.99302 | 1.0718 | 0.94166 | 0.97186 | 1.04 | 1.0239 | 1 | [16 empty] | CZ07 | 1.0209 | 0.98351 | 0.97066 | 1.0251 | 0.93661 | 0.97185 | 0.99319 | 0.99518 | 1
16 | 0.54164 | 1: 0.34087; 2: 0.10803; 3: 0.00946 | [6 empty] | CZ08 | 1.0631 | 0.9984 | 0.99246 | 1.071 | 0.97921 | 0.96174 | 1.0935 | 1.0526 | 1 | [16 empty] | CZ08 | 1.0248 | 0.96664 | 0.9528 | 1.0394 | 0.94599 | 0.95247 | 1.0223 | 1.0103 | 1
[17 empty] | CZ09 | 1.0977 | 0.97865 | 0.96686 | 1.1237 | 0.97824 | 0.94398 | 1.1454 | 1.0281 | 1 | [16 empty] | CZ09 | 1.0294 | 0.9617 | 0.95591 | 1.0517 | 0.95241 | 0.96502 | 1.0509 | 1.0298 | 1
[17 empty] | CZ10 | 1.079 | 0.97783 | 0.97 | 1.0578 | 0.97411 | 0.94665 | 1.1613 | 1.075 | 1 | [16 empty] | CZ10 | 1.0178 | 0.97887 | 0.97848 | 1.0408 | 0.98624 | 0.9829 | 1.0574 | 1.031 | 1
Outdoor Drybulb Temp Bins |  | 2: Outdoor Wetbulb Temp Bins | [6 empty] | CZ11 | 1.0041 | 0.9878 | 0.98386 | 1.0277 | 0.98709 | 0.96236 | 1.0813 | 1.0343 | 1 | [16 empty] | CZ11 | 0.99777 | 0.985 | 0.98835 | 1.0271 | 0.99635 | 0.99753 | 1.0408 | 1.0145 | 1
1 |  | 2: 2 | [6 empty] | CZ12 | 1.0211 | 0.98071 | 0.97469 | 1.0512 | 0.98432 | 0.95483 | 1.0992 | 1.0151 | 1 | [16 empty] | CZ12 | 1.0141 | 0.97119 | 0.97028 | 1.041 | 0.97176 | 0.98417 | 1.0456 | 1.0183 | 1
2 | 3 | 1: 4; 2: 6; 3: 7; 4: 8 | [6 empty] | CZ13 | 1.0038 | 0.97271 | 0.96579 | 1.0402 | 0.97074 | 0.94284 | 1.0943 | 1.0157 | 1 | [16 empty] | CZ13 | 1.0133 | 0.9765 | 0.97602 | 1.0438 | 0.97996 | 0.98302 | 1.0594 | 1.023 | 1
72≤ DB < 82 | 82≤ DB < 95 | 1: DB≥ 95; 2: 62≤ WB < 67; 3: 67≤ WB < 72; 4: WB≥ 72 | [6 empty] | CZ14 | 1.0634 | 0.98323 | 0.97716 | 1.0326 | 0.94361 | 0.95815 | 1.179 | 1.1196 | 1 | [16 empty] | CZ14 | 0.968 | 0.98448 | 0.99014 | 0.99305 | 1.0135 | 0.99937 | 1.0138 | 0.99428 | 1
59 | 59 | 1: 59; 2: 244; 3: 278; 4: 278 | [6 empty] | CZ15 | 0.998 | 0.94424 | 0.93814 | 1.0184 | 0.81647 | 0.91323 | 1.151 | 1.086 | 1 | [16 empty] | CZ15 | 0.99121 | 0.97709 | 0.97543 | 1.0227 | 0.97831 | 0.97916 | 1.0625 | 1.0202 | 1
793 | 1320 | 1: 1369; 2: 467; 3: 538; 4: 538 | [6 empty] | CZ16 | 1.0655 | 1.0078 | 1.0074 | 1.0694 | 0.98738 | 0.98054 | 1.0827 | 1.0467 | 1 | [16 empty] | CZ16 | 0.995 | 0.98941 | 0.99176 | 1.0194 | 1.0019 | 0.99631 | 1.0011 | 1.0032 | 1
424 | 492 | 1: 492; 2: 565; 3: 657; 4: 657
1044 | 1322 | 1: 1332; 2: 778; 3: 1379; 4: 1537 | [6 empty] | max | 1.1429 | 1.0326 | 1.0166 | 1.1237 | 1.0248 | 1 | 1.294 | 1.2208 | 1 | 1pt max | 1.294 | [14 empty] | max | 1.0366 | 1.0007 | 1 | 1.0517 | 1.0155 | 1.0142 | 1.0759 | 1.0369 | 1 | 1pt max | 1.0759
690 | 765 | 1: 765; 2: 651; 3: 714; 4: 727 | [6 empty] | min | 0.98749 | 0.93395 | 0.90879 | 1 | 0.81647 | 0.7978 | 1 | 0.96188 | 1 | 1p tmin | 0.7978 | [14 empty] | min | 0.96101 | 0.93444 | 0.92209 | 0.99025 | 0.91777 | 0.923 | 0.97848 | 0.98388 | 1 | 1p tmin | 0.91777
903 | 953 | 1: 953; 2: 1180; 3: 1459; 4: 1474 | [6 empty] | ave | 1.0455 | 0.98412 | 0.97366 | 1.0525 | 0.95644 | 0.95213 | 1.0873 | 1.0385 | 1 | ave max | 1.0873 | [14 empty] | ave | 1.0079 | 0.97533 | 0.96985 | 1.0263 | 0.9675 | 0.97655 | 1.0227 | 1.0087 | 1 | ave max | 1.0263
1082 | 1194 | 1: 1194; 2: 1031; 3: 1539; 4: 1631 | [16 empty] | ave min | 0.95213 | [24 empty] | ave min | 0.9675
1210 | 1663 | 1: 1670; 2: 1078; 3: 1608; 4: 1700
1197 | 1924 | 1: 1998; 2: 925; 3: 1418; 4: 1535
1260 | 2221 | 1: 2374; 2: 979; 3: 1349; 4: 1369
1025 | 1939 | 1: 2136; 2: 693; 3: 815; 4: 815
903 | 1599 | 1: 1719; 2: 842; 3: 1159; 4: 1176
1283 | 2389 | 1: 2739; 2: 972; 3: 1479; 4: 1561
1167 | 2221 | 1: 2563; 2: 263; 3: 269; 4: 269
1609 | 3331 | 1: 4570; 2: 806; 3: 1327; 4: 1696
674 | 1044 | 1: 1047; 2: 216; 3: 295; 4: 298
Note: these values are cummulative, for graphing as a "stack"

## Incremental Savings
Analysis of Energy Savings due to SEER Improvements
using detailed HVAC performance maps.
The following two tabs present energy savings for various levels of SEER improvement.
Savings are based on the simulation of 61 AC an HP units using detailed performance
data for four vintages of homes in 16 climate zones.
Charts present the range of savings that can be expected across all climate zones for
a particular SEER improvement level and vintage. A summary table shows the range
of savings at each SEER improvement level.
Savings Calculations:
Median Savings is calculated as:
(Energy Use of Median Performing Base SEER unit minus
Energy Use of Median Performing Improved SEER unit)
divided by the equipment rated cooling capacity in tons
Note: "Median Performing Unit" may vary by climate zone and vintage
Minimum Savings is calculated as:
(Energy Use of Best Performing Base SEER unit minus
Energy Use of Worst Performing Improved SEER unit)
divided by the equipment rated cooling capacity in tons
Maximum Savings is calculated as:
(Energy Use of Worst Performing Base SEER unit minus
Energy Use of Best Performing Improved SEER unit)
divided by the equipment rated cooling capacity in tons
Median Unit Savings is calculated as:
(Energy Use of selected Median Base SEER unit minus
Energy Use of selected Median Improved SEER unit)
divided by the equipment rated cooling capacity in tons
Note: "selected Median Unit" is the same across all climates and vintages
ACM Savings is calculated as:
(Energy Use of selected Median Base SEER unit times
( 1 - SEERbase/SEERimp))
where SEERbase and SEERimp are the temperature adjusted SEER values from the 2001 ACM
| Where: | Energy Use is defined as the annual outdoor unit kWh + supply fan kWh
Performance is defined by acutal energy use (not equipment specifications)
Calibration of HVAC Energy Use:
UEC based Calibration:
The 2001 DEER Update Study calibrated cooling and heating energy use to prescribed UEC values from the CEC forecasting models.
The calibration values developed were based on DOE2 estimates of cooling and heating energy compared to the UEC values by climate
zone and vintage.
The current building models have changed in a number of ways, including entirely new cooling performance modeling. As such, the
calibration values developed from the 2001 DEER residential analysis have been adjusted to account for the new cooling energy values.
An alternative, RASS-based Calibration:
The recent Thermostat Analysis project developed detailed thermostat schedules based on the RASS database of survey responses.
For this project, the programmable and standard thermostat responses were combined to create region-specific heating and cooling
thermostat tables. (see "Programmable Thermostats Installed into Residential Buildings: Predicting Energy Saving Using Occupant
Behavior and Simulation" for details on the thermostat table approach). These detailed thermostat schedules represent a major
improvement in how occupant behavior is modeled in energy simulations.
Results from simulations using the detailed thermostat tables (which require 59 annual runs to produce one result) were compared to
simulation results using constant 68 F heating and 78 F cooling to develop the RASS-based climate zone and vintage specific calibration
factors.
No Calibration:
The simulation results are not altered by any calibration factor. The simulations were conducted using constant 68 F heating
and 78 F cooling thermostat setpoints.

## AC Savings
Residential Cooling Electricity Savings due to AC equipment SEER improvement
- A comparison of savings based on simulations using detailed performance characteristics
| SEER Increment |  |  |  |  | House Vintage |  |  |  | Calibration Source
|  |  | Median | Min/Max | Min | MedUnit | ACM
|  | CZ01* | 0 | 0 | 0 | 0 | 0 | 1
|  | CZ02 | 85.2309 | 112.5772 | 73.7261 | 86.5493 | 79.4355 | 1
|  | CZ03 | 23.0098 | 29.2995 | 16.3663 | 23.5764 | 20.6714 | 1
|  | CZ04 | 89.3994 | 104.6325 | 61.6469 | 92.6544 | 75.9809 | 1
|  | CZ05 | 15.6441 | 20.2099 | 11.2203 | 16.5569 | 15.0898 | 1
|  | CZ06 | 61.4963 | 79.2976 | 46.7542 | 65.6656 | 60.0418 | 1
|  | CZ07 | 91.2276 | 114.0907 | 69.114 | 95.1947 | 84.6704 | 1
|  | CZ08 | 143.9915 | 177.1407 | 95.5785 | 144.7869 | 117.4593 | 1
|  | CZ09 | 151.9476 | 189.9291 | 92.3279 | 148.1671 | 112.1144 | 1
|  | CZ10 | 173.8317 | 241.9921 | 134.0318 | 175.2833 | 135.9277 | 1
|  | CZ11 | 174.9067 | 244.2188 | 145.2224 | 173.0804 | 140.8856 | 1
|  | CZ12 | 141.5329 | 191.3317 | 105.1863 | 143.2764 | 108.0957 | 1
|  | CZ13 | 265.9995 | 392.9085 | 198.441 | 266.8032 | 193.8076 | 1
|  | CZ14 | 210.6669 | 291.1036 | 154.4899 | 196.6922 | 147.9335 | 1
|  | CZ15 | 492.3809 | 787.9201 | 286.5772 | 467.1942 | 333.3449 | 1
|  | CZ16 | 58.58 | 75.3079 | 48.9442 | 57.3177 | 52.476 | 1
* For the DEER 2001 Update, climate zone CZ01 was prescribed to have no residential cooling load
| Median: | savings determined by comparing the actual median performing unit for each climate zone
| Min/Max: | minimum and maximum savings determined by comparing best and worse performing units at each SEER level
| Med Unit: | savings determined by comparing the chosen "median unit" for these SEER levels
| ACM: | savings determined by applying a ratio of temperature (climate zone) corrected SEER values to the base energy use
Summary Results - Electricity savings per year per ton of cooling equipment installed
- Vintage results weighted based on RASS data for homes with central cooling
Residential AC Energy Savings by Climate Zone and SEER Improvement Level - kWh/yr per ton
| SEER 10 to SEER 13 |  |  |  |  | SEER 10 to SEER 14 |  |  |  |  | SEER 10 to SEER 15 |  |  |  |  | SEER 10 to SEER 16 |  |  |  |  | SEER 10 to SEER 17 |  |  |  |  | SEER 10 to SEER 18 |  |  |  |  | SEER 13 to SEER 14 |  |  |  |  | SEER 13 to SEER 15 |  |  |  |  | SEER 13 to SEER 16 |  |  |  |  | SEER 13 to SEER 17 |  |  |  |  | SEER 13 to SEER 18
| Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM
CZ01* | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CZ02 | 85.2309 | 112.5772 | 73.7261 | 86.5493 | 79.4355 | 99.6408 | 119.9364 | 85.9444 | 101.4311 | 96.0717 | 122.4665 | 143.7288 | 107.2631 | 121.2918 | 110.5811 | 116.247 | 151.1158 | 65.4503 | 113.1695 | 123.6941 | 133.1021 | 158.7275 | 94.094 | 128.7429 | 105.0501 | 130.3335 | 162.3834 | 101.1536 | 123.8058 | 107.7017 | 14.4099 | 23.983 | -4.4055 | 14.8818 | 16.3187 | 37.2357 | 47.7754 | 16.9132 | 34.7426 | 30.5511 | 31.0162 | 55.1623 | -24.8995 | 26.6202 | 43.4139 | 47.8713 | 62.774 | 3.7442 | 42.1937 | 51.9683 | 45.1026 | 66.4299 | 10.8037 | 37.2566 | 56.7545
CZ03 | 23.0098 | 29.2995 | 16.3663 | 23.5764 | 20.6714 | 27.6059 | 32.061 | 20.3544 | 28.6672 | 25.1241 | 32.1161 | 36.8249 | 27.3823 | 32.6635 | 29.0895 | 30.8365 | 35.5684 | 21.1022 | 28.8612 | 32.5547 | 35.0089 | 43.45 | 25.2305 | 33.4398 | 25.9058 | 36.3995 | 41.8111 | 30.525 | 36.6052 | 26.9966 | 4.031 | 8.0996 | -2.4386 | 4.511 | 4.1056 | 9.2991 | 13.6263 | 5.278 | 9.2892 | 7.7619 | 8.0196 | 12.3698 | -1.0021 | 5.4869 | 10.9569 | 12.192 | 20.2515 | 3.1262 | 10.0656 | 13.3497 | 13.3897 | 18.4235 | 8.2467 | 13.0289 | 14.088
CZ04 | 89.3994 | 104.6325 | 61.6469 | 92.6544 | 75.9809 | 109.0082 | 121.6392 | 78.056 | 113.9957 | 92.3475 | 118.9088 | 131.0883 | 95.5592 | 119.4021 | 106.923 | 97.4882 | 118.1938 | 49.8131 | 94.1095 | 119.6599 | 110.8201 | 125.8806 | 63.5005 | 107.6203 | 95.5423 | 120.7114 | 137.2264 | 91.5425 | 120.3178 | 98.3064 | 17.6594 | 28.3393 | 1.5502 | 19.3919 | 15.1416 | 33.0548 | 43.3515 | 23.632 | 30.4485 | 28.6263 | 8.0888 | 26.7951 | -25.0676 | 1.4551 | 40.4099 | 24.9661 | 38.1438 | -8.4267 | 18.6667 | 48.6121 | 29.3626 | 43.9265 | 15.0367 | 25.714 | 50.3502
CZ05 | 15.6441 | 20.2099 | 11.2203 | 16.5569 | 15.0898 | 18.8206 | 22.4884 | 14.2875 | 20.2373 | 18.5888 | 21.8483 | 25.4411 | 19.2537 | 22.8163 | 21.6162 | 20.2697 | 24.1693 | 15.5984 | 20.219 | 24.3162 | 23.9036 | 30.5204 | 18.2341 | 23.2193 | 19.1477 | 25.1811 | 27.9174 | 21.9378 | 25.6733 | 20.4598 | 2.5083 | 6.4161 | -2.4083 | 2.9634 | 3.2372 | 6.3818 | 10.2031 | 3.4142 | 6.4474 | 6.0382 | 4.8032 | 8.9313 | -0.24122 | 3.8502 | 8.5362 | 8.4371 | 15.2824 | 2.3946 | 6.8504 | 10.6302 | 9.537 | 12.5105 | 5.9144 | 9.1164 | 10.8568
CZ06 | 61.4963 | 79.2976 | 46.7542 | 65.6656 | 60.0418 | 74.8916 | 88.8347 | 58.6433 | 79.8847 | 74.2939 | 86.996 | 100.3993 | 76.3662 | 89.7906 | 86.6712 | 77.0216 | 90.895 | 63.3669 | 77.6955 | 97.5209 | 89.596 | 116.1161 | 70.3188 | 89.9439 | 79.3199 | 104.1715 | 118.8034 | 88.3125 | 108.2313 | 82.5894 | 11.8233 | 22.8037 | -4.5619 | 12.5261 | 13.6966 | 26.5844 | 37.1978 | 15.8773 | 25.2374 | 25.5914 | 16.61 | 27.6934 | 2.8779 | 13.1423 | 36.0182 | 29.1844 | 52.9145 | 9.8298 | 25.3907 | 43.5294 | 41.1032 | 52.7724 | 25.1073 | 40.8728 | 45.0649
CZ07 | 91.2276 | 114.0907 | 69.114 | 95.1947 | 84.6704 | 109.2488 | 125.2379 | 84.4158 | 113.7179 | 104.4618 | 121.8688 | 136.9965 | 103.611 | 122.9696 | 121.7238 | 103.7802 | 120.8318 | 79.4861 | 104.5543 | 136.9121 | 121.5272 | 147.6682 | 91.4362 | 121.19 | 113.654 | 141.4962 | 160.0321 | 121.4737 | 145.6598 | 114.9524 | 18.0211 | 29.3585 | -2.9095 | 18.5231 | 19.3438 | 36.615 | 47.4291 | 22.1689 | 33.9233 | 36.2153 | 18.5264 | 31.2644 | -1.9561 | 15.5081 | 51.0602 | 36.2734 | 58.1008 | 9.9941 | 32.1438 | 60.0146 | 50.2686 | 64.1527 | 34.1484 | 50.4651 | 60.9988
CZ08 | 143.9915 | 177.1407 | 95.5785 | 144.7869 | 117.4593 | 177.4459 | 196.5211 | 119.0343 | 178.8269 | 141.2587 | 202.9631 | 226.4878 | 156.2316 | 197.9402 | 162.4259 | 157.3395 | 199.2426 | 86.8713 | 155.8221 | 181.3682 | 190.1746 | 221.8522 | 112.5644 | 184.7621 | 147.5625 | 205.304 | 232.1722 | 146.4832 | 202.1323 | 148.8524 | 32.0689 | 42.3387 | -2.2573 | 32.6545 | 22.1416 | 58.9717 | 73.7851 | 36.2151 | 53.1533 | 41.8344 | 13.348 | 46.5398 | -33.1452 | 11.0352 | 59.4572 | 46.1831 | 69.1495 | -7.4521 | 39.9753 | 70.7393 | 59.927 | 77.9898 | 25.1916 | 55.9599 | 77.627
CZ09 | 151.9476 | 189.9291 | 92.3279 | 148.1671 | 112.1144 | 182.1695 | 209.0614 | 115.4923 | 186.0811 | 131.6053 | 202.3493 | 229.4853 | 152.0281 | 202.1093 | 148.8878 | 154.1496 | 212.7212 | 48.9535 | 150.0714 | 164.6195 | 191.4098 | 224.6043 | 80.6148 | 179.7 | 131.7136 | 193.5723 | 236.9413 | 111.7884 | 185.2013 | 134.3215 | 28.3115 | 49.2455 | -10.8447 | 35.9989 | 17.606 | 52.8744 | 74.4012 | 29.5219 | 56.3548 | 33.2172 | 2.202 | 55.0506 | -75.6328 | 1.9043 | 47.4275 | 39.4622 | 66.9336 | -43.9716 | 31.5329 | 57.1826 | 39.7143 | 77.1254 | -14.5486 | 35.1191 | 62.1324
CZ10 | 173.8317 | 241.9921 | 134.0318 | 175.2833 | 135.9277 | 213.7259 | 267.072 | 162.0115 | 214.9057 | 155.1781 | 247.1713 | 296.0713 | 203.3541 | 246.215 | 172.8134 | 214.9601 | 312.067 | 98.4797 | 207.9893 | 189.0059 | 252.8228 | 307.1227 | 151.5568 | 237.0617 | 153.6622 | 256.4953 | 330.3633 | 168.0183 | 244.9175 | 159.0476 | 35.0891 | 55.7332 | -13.6461 | 34.6552 | 17.5037 | 73.3396 | 90.5373 | 32.8642 | 70.9317 | 33.5388 | 38.5589 | 103.4544 | -74.7871 | 30.0674 | 48.262 | 78.991 | 101.5888 | -18.9331 | 61.7784 | 59.6227 | 77.8585 | 119.0245 | -7.6392 | 64.667 | 64.5716
CZ11 | 174.9067 | 244.2188 | 145.2224 | 173.0804 | 140.8856 | 217.4314 | 272.2662 | 181.4404 | 216.8622 | 158.9784 | 252.0279 | 304.7053 | 218.2393 | 249.5731 | 174.9887 | 244.6746 | 348.6111 | 137.8815 | 243.219 | 190.2897 | 280.9256 | 348.267 | 197.8482 | 273.1034 | 152.4828 | 278.7264 | 362.3293 | 208.5846 | 267.5002 | 162.3805 | 33.1041 | 61.8585 | -18.8641 | 34.3465 | 16.122 | 77.1212 | 105.2331 | 28.2703 | 76.4927 | 30.3882 | 60.3473 | 138.2034 | -62.4229 | 60.7032 | 44.0226 | 96.5983 | 137.8593 | -2.4562 | 90.5877 | 56.7876 | 94.3991 | 151.9216 | 8.2801 | 84.9844 | 59.5912
CZ12 | 141.5329 | 191.3317 | 105.1863 | 143.2764 | 108.0957 | 175.7262 | 216.0464 | 136.0535 | 179.0897 | 123.5929 | 196.2801 | 234.3174 | 164.681 | 196.2849 | 137.356 | 169.9298 | 243.639 | 72.9271 | 167.3165 | 149.5879 | 195.7478 | 237.3087 | 101.6224 | 188.1251 | 117.2699 | 200.8466 | 265.1767 | 128.6966 | 195.9312 | 124.505 | 26.5766 | 46.048 | -6.3188 | 28.1315 | 13.5778 | 54.7472 | 72.883 | 29.5975 | 53.0085 | 25.6361 | 21.631 | 74.6045 | -68.587 | 17.259 | 36.353 | 54.2149 | 75.8743 | -33.4612 | 44.8487 | 46.096 | 51.697 | 95.1783 | -13.6757 | 44.9731 | 48.8676
CZ13 | 265.9995 | 392.9085 | 198.441 | 266.8032 | 193.8076 | 318.9538 | 418.0813 | 245.417 | 322.5164 | 216.9688 | 359.7986 | 441.5978 | 299.2587 | 359.6235 | 237.3728 | 311.6599 | 479.5558 | 148.3787 | 309.841 | 256.1279 | 368.9713 | 477.3225 | 209.3638 | 360.2741 | 213.7855 | 392.3969 | 505.857 | 247.0305 | 371.9545 | 214.214 | 52.9543 | 95.1325 | -22.9838 | 55.7132 | 21.5323 | 106.8152 | 134.4184 | 44.0895 | 105.8974 | 40.5013 | 45.6604 | 156.607 | -120.0221 | 43.0378 | 57.9374 | 102.9718 | 154.3738 | -59.037 | 93.4709 | 69.8668 | 126.3974 | 182.9082 | -21.3703 | 105.1513 | 75.0049
CZ14 | 210.6669 | 291.1036 | 154.4899 | 196.6922 | 147.9335 | 252.8395 | 331.0313 | 210.7462 | 254.204 | 154.3284 | 306.6458 | 359.5663 | 231.2461 | 297.0843 | 160.6371 | 305.7431 | 400.2262 | 180.5499 | 306.9282 | 166.8612 | 340.389 | 429.1275 | 278.6776 | 324.6126 | 120.6871 | 378.405 | 458.6601 | 288.693 | 356.818 | 136.8585 | 17.2895 | 105.3745 | -61.8157 | 34.5409 | 5.1879 | 95.9789 | 157.7603 | -12.5413 | 100.3921 | 10.3059 | 95.0762 | 198.4202 | -63.2375 | 110.236 | 15.3553 | 129.7221 | 227.3215 | 34.8902 | 127.9204 | 21.5017 | 142.8551 | 233.0033 | 16.1311 | 137.1549 | 21.4711
CZ15 | 492.3809 | 787.9201 | 286.5772 | 467.1942 | 333.3449 | 580.6491 | 867.152 | 407.3619 | 579.834 | 349.8027 | 661.6505 | 861.7861 | 497.4542 | 667.9786 | 363.9958 | 586.5762 | 964.1473 | 254.0767 | 587.357 | 377.9993 | 684.6993 | 946.1009 | 356.4004 | 660.5702 | 305.8223 | 733.8144 | 1002.5855 | 438.3458 | 706.1232 | 302.0633 | 88.2682 | 278.9025 | -78.8859 | 112.6398 | 14.9335 | 201.4076 | 312.1315 | 44.9874 | 231.366 | 27.8121 | 94.1953 | 375.8978 | -232.1711 | 120.1627 | 40.5186 | 192.3184 | 357.8513 | -129.8474 | 193.376 | 48.9307 | 233.7397 | 405.192 | -55.8862 | 231.3589 | 52.8649
CZ16 | 58.58 | 75.3079 | 48.9442 | 57.3177 | 52.476 | 65.1182 | 77.3295 | 59.7514 | 66.8895 | 63.7553 | 83.9382 | 94.0875 | 73.6342 | 81.7679 | 73.5707 | 77.1497 | 87.6536 | 41.1099 | 68.3854 | 82.4177 | 83.6691 | 101.0217 | 64.1393 | 79.1629 | 69.2447 | 82.5474 | 98.2079 | 71.1574 | 76.8171 | 72.4159 | 6.4391 | 20.393 | -7.7837 | 9.4727 | 10.9111 | 25.3582 | 37.2474 | 6.2222 | 24.4502 | 20.4063 | 18.4707 | 30.7171 | -26.4252 | 10.9687 | 28.9644 | 25.0891 | 44.1817 | -3.2727 | 21.8453 | 35.4613 | 23.8684 | 41.2714 | 3.6223 | 19.4004 | 37.8834
| Med: | savings determined by comparing the actual median performing unit at each SEER level
| Max/Min: | minimum and maximum savings determined by comparing best and worse perfoming units at each SEER level
| MU: | savings determined by comparing the chosen "median unit" at each SEER level
| ACM: | savings determined by applying a ratio of temperature (climate zone) corrected SEER values to the base energy use
Detailed Results
- including Minimum, Median and Maximum Savings by Vintage and Climate Zone
- all values in kWh/year per ton of installed cooling capacity
| SEER 10 to SEER 13 Med: SEER 10 to SEER 13; SEER 10 to SEER 17 Med: SEER 10 to SEER 14; SEER 13 to SEER 16 Med: SEER 10 to SEER 15 | [5 empty] | SEER 10 to SEER 16 | [19 empty] | SEER 10 to SEER 17 | [19 empty] | SEER 10 to SEER 18 | [19 empty] | SEER 13 to SEER 14 | [19 empty] | SEER 13 to SEER 15 | [19 empty] | SEER 13 to SEER 16 | [19 empty] | SEER 13 to SEER 17 | [19 empty] | SEER 13 to SEER 18
| SEER 10 to SEER 13 Med: Pre-1978; SEER 10 to SEER 14 Med: 1978-1992; SEER 10 to SEER 15 Med: 1992-1998; SEER 10 to SEER 16 Med: Post-1998; SEER 10 to SEER 17 Med: Pre-1978; SEER 10 to SEER 18 Med: 1978-1992; SEER 13 to SEER 14 Med: 1992-1998; SEER 13 to SEER 15 Med: Post-1998; SEER 13 to SEER 16 Med: Pre-1978; SEER 13 to SEER 17 Med: 1978-1992; SEER 13 to SEER 18 Med: 1992-1998 | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998 |  |  |  |  | Pre-1978 |  |  |  |  | 1978-1992 |  |  |  |  | 1992-1998 |  |  |  |  | Post-1998
| Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM | Med | Max | Min | MU | ACM
CZ01* | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CZ02 | 92.51 | 121.0544 | 79.9776 | 93.047 | 86.0807 | 66.4581 | 86.2549 | 57.201 | 68.8489 | 61.3033 | 112.9912 | 155.5025 | 96.7546 | 113.4902 | 107.4862 | 110.9786 | 151.5815 | 98.4821 | 111.5218 | 104.5948 | 108.2617 | 129.2941 | 93.6788 | 109.4346 | 104.1085 | 78.0345 | 93.5387 | 66.0573 | 80.197 | 74.142 | 131.3909 | 161.1934 | 113.885 | 133.3854 | 129.9971 | 128.4922 | 157.4195 | 114.6432 | 130.9182 | 126.5001 | 132.7395 | 156.1338 | 116.6793 | 131.2464 | 119.8316 | 95.0768 | 111.2451 | 81.3957 | 95.1487 | 85.3394 | 164.0054 | 192.3897 | 145.3708 | 160.8543 | 149.63 | 160.3755 | 188.4108 | 145.3889 | 156.9568 | 145.6049 | 118.4095 | 159.0327 | 64.7889 | 118.4095 | 134.0417 | 90.4937 | 116.2112 | 39.5008 | 85.3973 | 95.4593 | 170.5713 | 214.918 | 124.1085 | 166.0797 | 167.3737 | 166.6207 | 209.2531 | 123.7159 | 161.5207 | 162.8712 | 138.5512 | 166.2501 | 92.5219 | 135.0321 | 113.7854 | 102.9303 | 119.0765 | 63.329 | 98.2433 | 80.8303 | 190.5938 | 234.2644 | 165.327 | 185.6763 | 142.9701 | 186.6125 | 227.5946 | 164.6327 | 180.8795 | 138.7619 | 137.7208 | 172.4002 | 103.3914 | 130.3893 | 116.6029 | 92.578 | 123.7153 | 68.9295 | 88.9822 | 82.6849 | 201.2777 | 230.5844 | 168.1869 | 190.0321 | 147.0393 | 196.0111 | 224.2812 | 167.0613 | 184.5021 | 142.8423 | 15.7518 | 25.5005 | -3.5596 | 16.3875 | 17.6756 | 11.5763 | 18.5207 | -2.3807 | 11.3481 | 12.5563 | 18.3998 | 33.5102 | -10.6888 | 19.8951 | 22.2093 | 17.5136 | 32.4196 | -10.4204 | 19.3964 | 21.5556 | 40.2296 | 52.3402 | 19.4408 | 38.1994 | 33.0916 | 28.6186 | 36.2272 | 12.9577 | 26.2999 | 23.5074 | 51.0142 | 64.7065 | 20.797 | 47.3641 | 41.5792 | 49.3969 | 63.4108 | 20.3253 | 45.435 | 40.3554 | 25.8995 | 55.2392 | -32.4495 | 25.3624 | 47.024 | 24.0356 | 41.1932 | -28.9372 | 16.5484 | 33.4047 | 57.5801 | 87.2348 | -0.46528 | 52.5895 | 59.0851 | 55.6421 | 84.2532 | -1.3477 | 49.9989 | 57.346 | 46.0413 | 62.4565 | -4.7165 | 41.9851 | 56.2634 | 36.4722 | 44.0586 | -5.109 | 29.3944 | 39.8972 | 77.6027 | 106.5812 | 40.7532 | 72.186 | 70.9495 | 75.6338 | 102.5946 | 39.5692 | 69.3577 | 68.9244 | 45.2108 | 68.6066 | 6.153 | 37.3423 | 61.4961 | 26.1198 | 48.6973 | 0.49144 | 20.1333 | 43.6765 | 88.2865 | 102.9012 | 43.6131 | 76.5419 | 77.1677 | 85.0325 | 99.2812 | 41.9978 | 72.9803 | 74.9216
CZ03 | 21.8823 | 27.0097 | 15.137 | 22.4491 | 19.7035 | 12.3671 | 14.7421 | 8.5253 | 12.9564 | 10.354 | 37.4504 | 49.9908 | 27.6425 | 38.1598 | 33.4909 | 32.4349 | 43.0822 | 23.3469 | 32.4349 | 32.9392 | 27.3864 | 31.4106 | 19.5705 | 28.6026 | 23.9478 | 14.2569 | 16.3571 | 10.217 | 15.1732 | 12.5843 | 44.1166 | 52.0142 | 33.7718 | 45.4074 | 40.7049 | 38.3294 | 45.0233 | 28.8999 | 38.5245 | 40.0344 | 30.3297 | 34.5662 | 25.6021 | 30.7959 | 27.7275 | 16.0637 | 18.1769 | 13.5316 | 16.5801 | 14.5706 | 53.9524 | 62.4335 | 46.5516 | 54.7165 | 47.1295 | 46.6014 | 53.8357 | 40.0754 | 47.0228 | 46.3532 | 27.2999 | 31.2224 | 16.9405 | 25.7046 | 31.0305 | 14.3824 | 16.4565 | 7.5277 | 13.9178 | 16.3062 | 55.4473 | 64.5569 | 42.8361 | 51.1722 | 52.7437 | 47.4413 | 54.808 | 36.7084 | 43.7808 | 51.8749 | 31.2469 | 38.2869 | 20.2928 | 29.9176 | 23.7673 | 16.085 | 19.3921 | 10.807 | 16.2438 | 13.3377 | 62.5891 | 79.1996 | 49.3075 | 59.1327 | 44.0738 | 54.8368 | 68.4397 | 41.3494 | 49.9747 | 37.6722 | 31.7776 | 36.0104 | 26.4528 | 31.9519 | 25.8402 | 16.9521 | 19.8675 | 13.868 | 16.8919 | 13.6317 | 66.0748 | 76.4443 | 56.0994 | 66.7842 | 44.8794 | 56.4481 | 63.8044 | 47.7848 | 56.4481 | 38.2834 | 3.9762 | 7.6424 | -1.7508 | 4.5861 | 3.7667 | 1.8898 | 4.2409 | -0.93413 | 2.2168 | 2.1138 | 6.6662 | 13.4409 | -5.2881 | 7.2475 | 6.9849 | 5.8945 | 11.431 | -3.9369 | 6.0896 | 5.9703 | 8.4473 | 12.3493 | 5.6723 | 8.3468 | 7.1211 | 4.2776 | 6.6299 | 2.9043 | 4.2324 | 3.9962 | 16.502 | 23.8602 | 7.4917 | 16.5567 | 13.2054 | 14.1665 | 20.2434 | 7.2386 | 14.5879 | 11.2873 | 5.4176 | 9.0054 | -2.9893 | 3.2555 | 10.0525 | 2.5964 | 4.9095 | -3.0995 | 1.5701 | 5.6412 | 17.9969 | 25.9836 | 3.7761 | 13.0124 | 18.6411 | 15.0064 | 21.2157 | 3.8716 | 11.3459 | 15.9336 | 9.3646 | 16.07 | 0.36304 | 7.4685 | 12.7779 | 4.299 | 7.8452 | 0.17973 | 3.8961 | 6.7408 | 25.1387 | 40.6263 | 10.2476 | 20.9729 | 22.1926 | 22.4019 | 34.8474 | 8.5126 | 17.5398 | 18.9309 | 9.8953 | 13.7935 | 6.5231 | 9.5028 | 13.065 | 4.585 | 7.7512 | 2.7168 | 3.9354 | 7.0427 | 28.6244 | 37.871 | 17.0395 | 28.6244 | 24.0344 | 24.0132 | 30.2122 | 14.948 | 24.0132 | 20.5293
CZ04 | 92.8169 | 108.0145 | 65.1718 | 96.8845 | 76.812 | 62.7685 | 72.1637 | 45.4413 | 66.7745 | 51.7785 | 118.7736 | 143.9575 | 79.3928 | 118.7736 | 101.3825 | 103.4827 | 123.5141 | 63.6824 | 103.4827 | 99.8641 | 111.0099 | 123.7036 | 79.9622 | 116.8001 | 93.3576 | 74.5922 | 83.1898 | 54.8095 | 80.3059 | 62.9317 | 141.5678 | 159.6617 | 99.2495 | 143.3054 | 123.2206 | 141.1249 | 157.4264 | 97.6441 | 142.9419 | 121.3751 | 120.3232 | 132.3263 | 96.8014 | 120.7131 | 108.0926 | 85.4573 | 95.5769 | 72.0794 | 88.5803 | 72.8644 | 167.2051 | 186.2579 | 132.6195 | 163.9159 | 142.669 | 143.6669 | 156.4942 | 110.1103 | 142.1709 | 140.5322 | 95.9397 | 118.5872 | 44.6677 | 95.21 | 120.9688 | 64.8002 | 81.6436 | 29.5354 | 63.8099 | 81.5442 | 152.2991 | 173.7593 | 97.5414 | 137.1502 | 159.664 | 131.0063 | 149.0174 | 82.4006 | 117.7367 | 157.2726 | 107.2162 | 120.4027 | 55.5498 | 106.1867 | 98.5554 | 75.2231 | 91.4417 | 44.1443 | 76.8294 | 66.362 | 176.801 | 198.6513 | 122.312 | 160.5007 | 131.4446 | 152.7248 | 170.7511 | 101.4206 | 138.4119 | 112.3332 | 118.7684 | 135.6062 | 87.0748 | 117.5596 | 99.0631 | 76.4899 | 90.7354 | 58.9419 | 77.9284 | 66.8718 | 176.5547 | 198.2922 | 143.1073 | 176.5547 | 132.7005 | 175.1322 | 191.2523 | 139.9818 | 175.1322 | 130.0526 | 18.193 | 27.838 | 2.6415 | 19.9156 | 15.6192 | 11.8237 | 19.229 | 1.1653 | 13.5314 | 10.5171 | 22.7942 | 36.7669 | -1.206 | 24.5317 | 20.8315 | 22.4241 | 41.6543 | -1.3093 | 24.2411 | 17.8027 | 33.5639 | 42.7172 | 24.5271 | 30.1517 | 29.5291 | 22.6888 | 31.6162 | 18.4352 | 21.8057 | 19.8833 | 48.4315 | 63.3631 | 32.1639 | 45.1423 | 39.3833 | 40.1842 | 55.5647 | 23.8432 | 38.6881 | 33.6572 | 3.1228 | 22.7215 | -32.653 | -1.6745 | 41.6843 | 2.0317 | 17.6828 | -24.1088 | -2.9646 | 28.068 | 33.5255 | 50.8645 | -2.9141 | 18.3766 | 55.595 | 27.5236 | 48.0879 | -3.8664 | 14.254 | 47.5117 | 20.4569 | 30.7936 | -16.7245 | 15.6253 | 48.9863 | 12.4546 | 27.4809 | -9.4999 | 10.0549 | 33.0678 | 58.0274 | 75.7565 | 21.8565 | 41.7271 | 65.6198 | 49.2421 | 69.8216 | 15.1535 | 34.9292 | 64.3104 | 25.9515 | 39.7405 | 9.7542 | 20.6751 | 50.4511 | 13.7214 | 26.7747 | 5.2977 | 11.1539 | 36.6866 | 57.7811 | 75.3974 | 42.6518 | 57.7811 | 71.8604 | 56.4315 | 75.4803 | 41.0284 | 56.4315 | 61.6904
CZ05 | 17.9431 | 23.1966 | 12.7298 | 19.255 | 17.5401 | 9.5132 | 12.0313 | 6.8621 | 10.0722 | 8.638 | 35.8967 | 47.6129 | 26.6806 | 36.0511 | 33.6908 | 30.0777 | 40.3292 | 22.329 | 29.6434 | 32.6911 | 22.1364 | 26.7208 | 16.7169 | 24.0517 | 21.6073 | 10.9248 | 12.7898 | 8.2435 | 11.8446 | 10.6409 | 41.6379 | 48.9404 | 32.79 | 42.5223 | 41.5029 | 35.2529 | 41.8193 | 27.4891 | 35.1937 | 40.2714 | 25.2729 | 29.7339 | 22.3624 | 26.5501 | 25.1263 | 12.6991 | 14.4768 | 11.064 | 13.3205 | 12.3739 | 51.8987 | 59.5116 | 46.2679 | 52.4334 | 48.2622 | 43.6715 | 50.6668 | 37.9777 | 44.2912 | 46.8302 | 22.9342 | 27.8914 | 17.7943 | 23.4304 | 28.2648 | 11.4915 | 13.1696 | 8.2777 | 11.2471 | 13.9196 | 55.202 | 63.8267 | 45.3443 | 51.9476 | 54.2906 | 44.5697 | 52.9224 | 35.6238 | 41.541 | 52.6796 | 27.3213 | 35.3472 | 20.487 | 26.7223 | 21.8719 | 13.5735 | 16.5777 | 10.4243 | 13.3578 | 11.4995 | 62.0847 | 79.5561 | 50.5014 | 58.0401 | 45.3315 | 51.142 | 66.5538 | 40.4566 | 47.1374 | 38.4616 | 28.4048 | 31.6884 | 24.8509 | 29.2672 | 23.9821 | 14.6056 | 15.8114 | 12.7646 | 14.661 | 11.8005 | 66.832 | 74.5108 | 57.5438 | 67.1992 | 46.4421 | 54.7041 | 61.5894 | 46.2431 | 54.6187 | 39.2736 | 2.9405 | 7.6034 | -2.6005 | 3.4522 | 3.6978 | 1.4115 | 3.7428 | -1.603 | 1.7724 | 1.9442 | 5.7412 | 13.9841 | -6.5473 | 6.4712 | 7.664 | 5.1752 | 11.1182 | -4.468 | 5.5503 | 6.5025 | 7.3299 | 11.8642 | 4.3057 | 7.2951 | 6.8972 | 3.6329 | 5.8548 | 1.6802 | 3.7216 | 3.6263 | 16.0021 | 24.5554 | 6.9306 | 16.3823 | 14.2952 | 13.5938 | 19.9657 | 6.0205 | 14.6479 | 12.1288 | 4.9912 | 10.0217 | -0.26239 | 4.1753 | 9.7507 | 2.4252 | 4.5477 | -1.1061 | 1.6481 | 5.1266 | 19.3053 | 28.8705 | 6.007 | 15.8965 | 20.2092 | 14.4919 | 22.2213 | 3.6666 | 11.8976 | 17.1465 | 9.3782 | 17.4775 | 2.4303 | 7.4673 | 12.4602 | 4.5073 | 7.9557 | 1.0405 | 3.7588 | 6.1311 | 26.188 | 44.5999 | 11.1641 | 21.989 | 24.1297 | 21.0643 | 35.8527 | 8.4995 | 17.494 | 20.4052 | 10.4618 | 13.8187 | 6.7942 | 10.0122 | 12.5531 | 5.0924 | 6.7644 | 2.9182 | 4.5888 | 6.3004 | 30.9353 | 39.5546 | 18.2065 | 31.1481 | 25.8045 | 24.6264 | 30.8883 | 14.2859 | 24.9754 | 21.8894
CZ06 | 60.4 | 75.6883 | 44.3007 | 65.8217 | 56.385 | 43.0865 | 54.7374 | 32.5377 | 46.4001 | 45.1388 | 92.9962 | 129.0189 | 73.4344 | 95.379 | 92.7856 | 82.3883 | 108.7157 | 66.112 | 85.7275 | 80.5782 | 70.7369 | 84.3926 | 54.0409 | 77.524 | 69.7691 | 57.0925 | 67.7039 | 44.1951 | 61.6412 | 55.8534 | 113.0537 | 134.744 | 91.21 | 115.5065 | 114.8102 | 99.3765 | 116.116 | 81.1157 | 101.6049 | 99.705 | 86.0226 | 99.1679 | 75.3038 | 89.4569 | 81.3926 | 61.3347 | 70.0587 | 54.1883 | 63.9175 | 65.1586 | 120.6657 | 142.244 | 104.9266 | 122.2535 | 133.9375 | 120.7238 | 139.2758 | 106.4832 | 122.8217 | 116.3158 | 71.4384 | 84.6326 | 58.4018 | 74.4358 | 91.5815 | 52.1783 | 61.8059 | 43.7458 | 53.6186 | 73.3152 | 117.5155 | 138.1267 | 98.2811 | 113.9875 | 150.704 | 118.3209 | 138.5672 | 95.8141 | 113.2828 | 130.8764 | 84.5003 | 110.3942 | 63.7552 | 86.8464 | 75.8733 | 61.6415 | 78.87 | 48.526 | 62.1483 | 54.357 | 133.1492 | 172.3196 | 110.6681 | 129.9152 | 127.463 | 133.8521 | 173.0987 | 108.4418 | 130.2687 | 110.0297 | 92.9385 | 105.992 | 79.2911 | 97.8427 | 77.3804 | 75.5976 | 86.6828 | 64.9592 | 79.3041 | 61.7422 | 174.3284 | 199.6652 | 146.8913 | 176.7111 | 128.8096 | 151.296 | 171.0987 | 125.6133 | 154.6353 | 111.3356 | 10.3368 | 23.021 | -4.5765 | 11.7023 | 13.1014 | 8.8959 | 17.4249 | -3.1519 | 9.738 | 9.3861 | 20.0575 | 32.767 | -9.2662 | 20.1275 | 22.0097 | 16.9882 | 26.89 | -4.486 | 15.8774 | 18.9994 | 25.6226 | 37.7962 | 16.6864 | 23.6353 | 24.4795 | 18.2482 | 25.1106 | 11.8613 | 17.5175 | 17.5375 | 39.294 | 53.0141 | 17.0098 | 38.7969 | 41.1242 | 38.3355 | 50.0498 | 20.8815 | 37.0942 | 35.4995 | 11.0384 | 23.261 | -0.21557 | 8.6141 | 34.4531 | 9.0918 | 16.8578 | 1.4188 | 7.2186 | 24.6829 | 36.1438 | 48.8968 | 10.3643 | 30.5309 | 57.8794 | 35.9327 | 49.3412 | 10.2124 | 27.5553 | 49.9631 | 24.1002 | 49.0226 | 5.1378 | 21.0248 | 40.784 | 18.555 | 33.9219 | 6.199 | 15.7483 | 32.5417 | 51.7775 | 83.0897 | 22.7514 | 46.4587 | 67.8901 | 51.4638 | 83.8727 | 22.8401 | 44.5412 | 58.6803 | 32.5384 | 44.6204 | 20.6738 | 32.021 | 44.0103 | 27.4009 | 36.4038 | 17.6122 | 27.4009 | 31.5595 | 81.3321 | 97.6881 | 46.415 | 81.3321 | 64.2461 | 68.9077 | 81.8727 | 40.0116 | 68.9077 | 63.4996
CZ07 | 84.7287 | 103.0353 | 63.435 | 90.3565 | 76.8614 | 75.191 | 91.6909 | 56.0217 | 79.4072 | 68.0358 | 117.6135 | 153.7568 | 92.3862 | 118.9444 | 113.4216 | 103.4688 | 132.2369 | 75.2427 | 106.4533 | 98.3935 | 100.2746 | 115.4443 | 76.6559 | 107.1801 | 94.8275 | 89.3531 | 102.0062 | 68.3967 | 94.8229 | 83.939 | 142.7853 | 163.8298 | 114.276 | 143.346 | 139.9335 | 126.5905 | 143.7502 | 91.5578 | 127.1079 | 121.3927 | 119.8145 | 134.7237 | 101.909 | 121.894 | 110.4974 | 94.7494 | 104.791 | 80.4531 | 96.0867 | 97.8096 | 150.3222 | 170.3708 | 129.3992 | 149.8673 | 163.0571 | 149.5777 | 170.4187 | 121.9477 | 149.732 | 141.4524 | 93.5176 | 111.7205 | 67.8302 | 98.96 | 124.285 | 77.9678 | 91.15 | 58.1334 | 79.1257 | 110.014 | 140.3152 | 160.3798 | 116.0482 | 135.5818 | 183.4029 | 142.5139 | 159.3504 | 106.9777 | 135.4042 | 159.1024 | 112.5347 | 137.5584 | 78.4939 | 115.3361 | 102.4038 | 91.8061 | 110.9376 | 68.8487 | 92.1388 | 90.5687 | 160.6362 | 193.819 | 130.9152 | 155.7487 | 154.0888 | 161.0608 | 198.5521 | 121.0713 | 156.5749 | 133.0953 | 120.14 | 135.8879 | 105.1816 | 125.7678 | 103.8733 | 109.9592 | 123.8854 | 95.0258 | 114.1754 | 91.6895 | 203.794 | 230.9544 | 173.6343 | 205.9315 | 155.529 | 176.1291 | 199.5757 | 142.1659 | 179.1136 | 133.7417 | 15.5458 | 27.9282 | -2.2983 | 16.8236 | 17.429 | 14.162 | 24.2909 | -1.6006 | 15.4157 | 15.4147 | 25.1717 | 37.7495 | -5.7868 | 24.4016 | 26.2257 | 23.1217 | 29.7193 | -1.8909 | 20.6545 | 22.6527 | 35.0858 | 47.2075 | 22.9548 | 31.5375 | 32.6305 | 27.5306 | 35.3156 | 17.8773 | 25.0987 | 28.8593 | 47.4104 | 60.0506 | 24.3442 | 45.791 | 49.0997 | 46.1089 | 56.3878 | 28.4989 | 43.2787 | 42.4102 | 8.7889 | 24.2044 | -11.124 | 8.6035 | 46.0059 | 10.749 | 21.6746 | -4.4424 | 8.1377 | 40.6889 | 37.4033 | 50.0596 | 10.9932 | 31.5054 | 69.2259 | 39.0451 | 45.3195 | 13.5289 | 28.9508 | 59.7944 | 27.806 | 50.0423 | -0.46029 | 24.9796 | 54.2304 | 24.5873 | 41.4622 | 6.2729 | 21.1509 | 47.8695 | 57.7244 | 83.4988 | 25.8603 | 51.6723 | 81.1989 | 57.592 | 84.5212 | 27.6225 | 50.1216 | 69.8242 | 35.4113 | 48.3718 | 26.2273 | 35.4113 | 58.9545 | 34.7682 | 46.1701 | 25.0284 | 34.7682 | 46.6689 | 86.1805 | 104.8741 | 53.5715 | 86.9871 | 77.2957 | 72.6602 | 85.5449 | 48.7171 | 72.6602 | 76.4879
CZ08 | 142.7183 | 170.0585 | 91.3869 | 143.3286 | 112.6706 | 133.5636 | 165.5156 | 89.9342 | 135.3256 | 107.8191 | 176.1111 | 233.6128 | 129.5782 | 175.5828 | 151.3658 | 150.891 | 198.4679 | 101.547 | 150.891 | 147.0394 | 173.4119 | 188.7665 | 112.5878 | 174.299 | 135.4997 | 164.2003 | 181.8916 | 109.8029 | 167.2264 | 129.6652 | 215.243 | 249.9666 | 157.753 | 215.3966 | 182.0352 | 211.1502 | 242.2416 | 152.7156 | 211.0057 | 176.8323 | 198.8485 | 220.2716 | 149.7136 | 193.896 | 155.8039 | 189.4157 | 210.3818 | 145.4273 | 184.3329 | 149.0951 | 255.306 | 292.8147 | 210.1553 | 248.475 | 209.3127 | 215.2065 | 245.4206 | 173.1919 | 212.7992 | 203.3301 | 145.9382 | 187.381 | 68.7493 | 146.7321 | 173.9739 | 146.0631 | 186.6202 | 80.8596 | 144.5581 | 166.4828 | 225.5416 | 275.4397 | 165.3075 | 217.1369 | 233.7229 | 193.9734 | 233.0001 | 138.4326 | 184.3309 | 227.0426 | 179.2206 | 208.5456 | 92.2458 | 174.9341 | 141.8952 | 177.515 | 204.1187 | 105.7312 | 172.5253 | 136.8118 | 261.0299 | 313.4634 | 203.2746 | 251.9111 | 195.9558 | 225.2031 | 266.3473 | 166.3313 | 214.4708 | 166.1518 | 191.843 | 215.6369 | 127.5275 | 186.5262 | 141.6076 | 187.0055 | 210.9622 | 133.7893 | 185.8916 | 136.1513 | 283.67 | 330.3396 | 233.2663 | 283.67 | 196.7551 | 275.1228 | 308.989 | 222.4073 | 275.1228 | 190.3746 | 30.6937 | 40.4894 | -0.58049 | 30.9704 | 21.2912 | 30.6367 | 39.193 | -2.9484 | 31.9008 | 20.5285 | 39.1319 | 51.1137 | -6.5851 | 39.8137 | 29.403 | 38.7033 | 58.0764 | -5.9934 | 38.5588 | 24.9309 | 56.1302 | 71.9945 | 36.5454 | 50.5674 | 40.2277 | 55.852 | 67.6833 | 32.6761 | 49.0073 | 38.7865 | 79.1948 | 93.9619 | 45.8172 | 72.8921 | 55.554 | 64.3154 | 84.2761 | 34.3215 | 61.9082 | 47.1045 | 3.2199 | 39.1039 | -44.4189 | 3.4035 | 57.1737 | 12.4995 | 43.9217 | -31.8916 | 9.2325 | 55.1254 | 49.4304 | 76.5869 | 0.96943 | 41.5541 | 78.9562 | 43.0824 | 71.8556 | -0.43778 | 33.4399 | 66.9474 | 36.5024 | 60.2685 | -20.9225 | 31.6055 | 67.2963 | 43.9513 | 61.4201 | -7.0201 | 37.1997 | 64.7033 | 84.9188 | 114.6105 | 38.9365 | 76.3283 | 93.5041 | 74.312 | 105.2028 | 27.4609 | 63.5797 | 90.4719 | 49.1248 | 67.3599 | 14.3592 | 43.1976 | 74.7654 | 53.4419 | 68.2636 | 21.0381 | 50.566 | 71.727 | 107.5589 | 131.4867 | 68.9282 | 108.0872 | 102.9013 | 102.6759 | 124.8238 | 63.6982 | 102.6759 | 87.8394
CZ09 | 150.5976 | 184.9672 | 88.5957 | 146.178 | 107.5897 | 159.1212 | 201.1741 | 99.1351 | 155.2532 | 116.7124 | 143.0204 | 193.8976 | 99.1532 | 143.6236 | 130.4069 | 140.3997 | 186.7027 | 94.6249 | 139.8412 | 121.5269 | 178.2221 | 201.6863 | 108.6335 | 182.0265 | 126.294 | 189.0053 | 215.8255 | 121.4788 | 193.2747 | 137.0027 | 191.8561 | 241.9822 | 145.2064 | 195.1458 | 153.0779 | 181.5463 | 222.9444 | 133.3384 | 186.1704 | 142.6541 | 202.6154 | 226.979 | 149.4958 | 202.2744 | 142.879 | 203.096 | 232.0951 | 153.0721 | 202.4591 | 154.9939 | 200.9119 | 240.5212 | 166.42 | 201.909 | 173.1802 | 193.8235 | 231.8678 | 160.1657 | 196.0669 | 161.3875 | 141.8978 | 199.5978 | 32.5444 | 141.8978 | 157.9758 | 169.3963 | 229.8084 | 63.9318 | 160.9622 | 171.3708 | 190.9339 | 251.7964 | 113.9553 | 173.2134 | 191.4786 | 187.4005 | 242.5586 | 101.286 | 169.5016 | 178.4399 | 181.5743 | 209.7291 | 62.7916 | 170.9738 | 127.3282 | 207.1766 | 244.282 | 95.8613 | 192.5943 | 139.3686 | 212.9039 | 267.5282 | 151.6267 | 201.343 | 140.5664 | 207.5817 | 259.171 | 145.3593 | 197.1113 | 135.3119 | 180 | 221.2591 | 94.0903 | 171.7029 | 127.831 | 207.1578 | 249.5323 | 126.0712 | 197.4425 | 140.0298 | 245.7678 | 306.3197 | 186.5077 | 242.5029 | 162.5313 | 230.3663 | 283.6902 | 172.941 | 219.2786 | 150.5985 | 27.6244 | 47.9433 | -11.1864 | 35.8485 | 17.0198 | 29.8841 | 49.3733 | -12.3781 | 38.0214 | 18.6292 | 28.9718 | 58.0487 | -4.6124 | 31.5745 | 18.7893 | 27.4491 | 53.4615 | -5.9529 | 32.6861 | 18.087 | 52.0178 | 73.236 | 29.6759 | 56.0963 | 32.1112 | 53.4366 | 75.5407 | 27.1747 | 56.4378 | 35.1477 | 57.8914 | 79.0187 | 34.8718 | 58.2853 | 35.4498 | 53.4238 | 77.4501 | 33.2558 | 56.2256 | 34.1246 | -8.6998 | 45.8548 | -87.2755 | -4.2802 | 45.8484 | 10.2751 | 63.3562 | -69.9251 | 5.709 | 50.1839 | 47.9135 | 90.2939 | -17.593 | 29.5898 | 50.6152 | 47.0008 | 88.1409 | -25.6239 | 29.6603 | 48.7232 | 30.9767 | 55.9861 | -57.0283 | 24.7958 | 54.4196 | 48.0554 | 77.8298 | -37.9957 | 37.341 | 59.6128 | 69.8835 | 106.0257 | 20.0785 | 57.7193 | 69.192 | 67.182 | 104.7532 | 18.4494 | 57.2701 | 64.112 | 29.4024 | 67.5161 | -25.7297 | 25.5249 | 61.0599 | 48.0366 | 83.0801 | -7.7857 | 42.1893 | 62.878 | 82.8834 | 122.3863 | 36.6889 | 78.9316 | 67.334 | 76.2691 | 114.2073 | 33.6496 | 65.7943 | 65.1846
CZ10 | 174.0924 | 236.5432 | 132.8922 | 174.0924 | 129.1954 | 181.6784 | 251.5378 | 134.8493 | 181.6784 | 136.4492 | 162.9959 | 235.6379 | 135.811 | 167.3786 | 148.1243 | 155.6166 | 224.318 | 131.8649 | 162.0963 | 136.1721 | 210.9254 | 257.1504 | 154.0858 | 209.28 | 147.4923 | 215.948 | 271.0019 | 157.3887 | 218.2649 | 155.7735 | 222.9017 | 281.2097 | 187.5154 | 224.9559 | 169.102 | 203.9887 | 259.8635 | 171.1448 | 205.4849 | 155.4572 | 245.8626 | 292.1503 | 199.6251 | 244.2778 | 164.2542 | 256.7609 | 306.1731 | 205.5728 | 255.4642 | 173.4764 | 236.1717 | 285.0784 | 208.2198 | 235.2918 | 188.3197 | 225.9322 | 277.5379 | 198.5206 | 227.1128 | 173.1242 | 184.8083 | 283.6171 | 60.4115 | 184.8083 | 179.6446 | 215.48 | 314.2192 | 88.7451 | 208.3461 | 189.731 | 264.0454 | 366.0482 | 169.8149 | 251.3316 | 205.9651 | 226.3701 | 311.3915 | 140.2679 | 212.584 | 189.3457 | 230.1107 | 279.8231 | 109.5049 | 217.7122 | 149.2568 | 261.1534 | 313.2349 | 146.0204 | 242.4507 | 158.1912 | 265.2348 | 327.6975 | 206.6745 | 250.46 | 153.3613 | 253.9159 | 317.0667 | 198.602 | 241.5043 | 146.2622 | 226.6327 | 298.98 | 130.3159 | 214.4881 | 149.07 | 256.1605 | 328.9947 | 158.2294 | 242.4922 | 159.2796 | 299.6758 | 378.1644 | 232.2995 | 293.3242 | 176.017 | 274.8143 | 351.1336 | 214.8062 | 267.127 | 162.0642 | 36.833 | 55.0614 | -13.2605 | 35.1877 | 17.0018 | 34.2697 | 56.6132 | -14.6098 | 36.5866 | 18.0196 | 37.2675 | 58.7879 | -13.1016 | 34.3303 | 17.4694 | 33.19 | 51.5847 | -11.5089 | 27.5742 | 16.6607 | 71.7702 | 90.0613 | 32.2788 | 70.1855 | 32.5772 | 75.0825 | 91.7843 | 33.5743 | 73.7858 | 34.5273 | 73.1758 | 89.7812 | 32.0682 | 67.9132 | 33.4731 | 70.3156 | 87.7728 | 32.1029 | 65.0164 | 31.9236 | 10.716 | 81.528 | -106.9348 | 10.716 | 46.8783 | 33.8017 | 99.8305 | -83.2533 | 26.6678 | 49.6845 | 78.4112 | 143.6263 | -30.8022 | 60.7061 | 48.1675 | 70.7535 | 121.6264 | -26.1498 | 50.4877 | 45.9378 | 56.0183 | 77.7341 | -57.8414 | 43.6199 | 55.8823 | 79.475 | 98.8462 | -25.9781 | 60.7723 | 59.7096 | 102.2388 | 132.4003 | 30.5229 | 83.0815 | 65.984 | 98.2993 | 127.3016 | 32.1843 | 79.408 | 60.7535 | 52.5403 | 96.891 | -37.0304 | 40.3958 | 62.6558 | 74.4821 | 114.606 | -13.769 | 60.8138 | 66.5255 | 114.0415 | 155.7425 | 31.6824 | 102.6986 | 64.4476 | 104.0155 | 142.8548 | 32.1526 | 89.2164 | 61.4005
CZ11 | 186.2352 | 257.5333 | 152.7285 | 180.8973 | 140.8805 | 178.4062 | 256.7504 | 148.1332 | 178.4062 | 157.0354 | 161.109 | 218.6356 | 136.6472 | 161.7262 | 120.5846 | 142.5958 | 191.4575 | 121.3611 | 144.0527 | 115.226 | 218.2572 | 272.5499 | 180.7469 | 216.5236 | 158.9727 | 242.4514 | 304.4855 | 199.8946 | 240.4292 | 177.2022 | 185.8481 | 231.3814 | 159.3255 | 187.2545 | 136.0703 | 175.0656 | 220.5427 | 153.1525 | 180.4971 | 130.0236 | 267.7052 | 325.6892 | 230.4834 | 262.9406 | 174.9823 | 260.3995 | 315.227 | 227.4398 | 259.4533 | 195.0477 | 229.458 | 273.6903 | 197.9146 | 227.0082 | 149.7735 | 200.5961 | 238.8704 | 173.0903 | 201.2137 | 143.1179 | 230.0931 | 338.7515 | 113.0172 | 230.0931 | 190.2829 | 269.7529 | 385.6761 | 158.9645 | 269.7529 | 212.1028 | 235.4671 | 317.6973 | 150.4541 | 230.3701 | 162.8698 | 227.4505 | 304.3173 | 141.8051 | 220.9399 | 155.6322 | 266.2723 | 333.2574 | 175.9267 | 259.6706 | 160.4121 | 310.5439 | 387.2859 | 212.5329 | 302.8976 | 160.3278 | 269.4867 | 323.442 | 217.3879 | 256.3925 | 136.9002 | 252.7155 | 308.1017 | 203.4221 | 246.3872 | 120.3002 | 270.1887 | 353.0598 | 185.9467 | 252.1611 | 162.1659 | 307.2342 | 404.8266 | 236.6494 | 302.9629 | 180.9703 | 260.6051 | 323.093 | 210.1034 | 246.5107 | 139.0454 | 241.306 | 309.1632 | 196.647 | 234.8135 | 133.4985 | 32.022 | 61.6303 | -18.5952 | 35.6263 | 16.9604 | 41.6892 | 69.5006 | -20.74 | 39.667 | 16.9514 | 24.7391 | 53.3994 | -17.9754 | 25.5283 | 14.4744 | 20.2473 | 49.1432 | -15.0797 | 24.097 | 12.7193 | 81.4701 | 114.7695 | 31.1413 | 82.0433 | 31.9685 | 81.9933 | 106.4091 | 31.3741 | 81.0471 | 31.9517 | 68.349 | 95.7083 | 20.6137 | 65.282 | 27.2828 | 58.0003 | 81.0025 | 18.1396 | 57.1611 | 23.9746 | 43.8579 | 127.8318 | -86.3249 | 49.1959 | 46.3118 | 68.9907 | 150.6912 | -61.6701 | 68.9907 | 46.2875 | 74.3581 | 139.7153 | -26.8468 | 68.6439 | 39.5238 | 72.6323 | 132.9178 | -26.4271 | 64.5399 | 34.7313 | 80.0371 | 122.3378 | -23.4154 | 78.7733 | 56.7126 | 109.7816 | 152.301 | -8.1017 | 102.1354 | 63.2889 | 108.3777 | 145.46 | 40.0871 | 94.6663 | 48.6269 | 97.8973 | 136.7023 | 35.19 | 89.9871 | 46.687 | 83.9535 | 142.1402 | -13.3955 | 71.2639 | 62.6546 | 106.472 | 169.8417 | 16.0148 | 102.2007 | 62.5624 | 99.4962 | 145.111 | 32.8026 | 84.7845 | 53.5948 | 86.4877 | 137.7637 | 28.4149 | 78.4134 | 47.312
CZ12 | 149.2408 | 200.0534 | 111.3513 | 149.6345 | 106.5499 | 148.4579 | 201.8251 | 106.0365 | 148.7904 | 120.691 | 119.9038 | 165.3151 | 96.5807 | 127.4932 | 91.5362 | 105.9802 | 142.6756 | 84.29 | 112.1943 | 86.5638 | 175.2945 | 214.511 | 133.2502 | 177.9589 | 121.8255 | 195.637 | 242.455 | 150.8442 | 200.0513 | 137.994 | 145.7922 | 178.1164 | 117.9964 | 147.9174 | 104.6594 | 137.1095 | 167.0489 | 113.577 | 141.1046 | 98.9741 | 205.4842 | 245.5466 | 171.0603 | 204.6774 | 135.3917 | 203.6729 | 243.9962 | 171.0466 | 204.6012 | 153.3607 | 174.0852 | 206.5992 | 147.8634 | 173.4934 | 116.314 | 152.7719 | 179.4613 | 131.4648 | 153.6294 | 109.9956 | 157.8126 | 234.6208 | 52.5071 | 157.8126 | 147.4487 | 189.709 | 273.9017 | 88.9387 | 188.9011 | 167.0178 | 168.9106 | 222.1675 | 91.8121 | 157.9078 | 126.6721 | 149.711 | 193.6541 | 80.8331 | 138.4463 | 119.791 | 193.0832 | 236.7064 | 87.2769 | 187.8119 | 121.2702 | 207.6406 | 249.214 | 104.6586 | 197.7248 | 122.5095 | 192.4438 | 230.0674 | 134.3448 | 182.0375 | 106.2576 | 165.7889 | 202.7132 | 115.1952 | 159.7476 | 92.1673 | 191.6917 | 255.0018 | 114.2737 | 182.9263 | 122.1711 | 224.2551 | 298.1739 | 141.4739 | 224.2551 | 139.1626 | 185.9591 | 234.2728 | 140.1212 | 177.6368 | 106.2333 | 170.0221 | 221.4279 | 130.9289 | 167.7826 | 100.6654 | 26.0538 | 42.8939 | -6.5374 | 28.3244 | 14.0409 | 28.5759 | 54.7945 | -7.9349 | 32.6159 | 14.1844 | 25.8884 | 37.7268 | -3.5098 | 20.4242 | 12.3027 | 22.0453 | 36.6977 | -2.4917 | 19.2936 | 10.6713 | 56.2434 | 73.9296 | 31.2727 | 55.0429 | 26.5106 | 55.215 | 77.2328 | 29.9485 | 55.8108 | 26.7816 | 54.1814 | 66.2095 | 26.3572 | 46.0003 | 23.2287 | 46.7917 | 59.4009 | 24.5595 | 41.4351 | 20.1485 | 8.5718 | 63.0037 | -87.2805 | 8.1782 | 37.593 | 22.6479 | 86.2411 | -69.8403 | 21.4657 | 37.9772 | 49.0068 | 81.7778 | -29.6941 | 30.4147 | 32.9392 | 43.7308 | 73.5938 | -26.0722 | 26.252 | 28.5713 | 43.8424 | 65.0894 | -52.5107 | 38.1774 | 45.2319 | 59.1827 | 82.4506 | -36.4395 | 48.9344 | 51.5228 | 72.54 | 89.6777 | 12.8386 | 54.5444 | 39.3312 | 59.8088 | 82.6529 | 8.2899 | 47.5532 | 37.2698 | 42.4509 | 83.3848 | -25.5139 | 33.2918 | 50.5783 | 57.194 | 110.5134 | -17.3052 | 56.8198 | 51.2842 | 66.0553 | 93.8831 | 18.6151 | 50.1436 | 43.7395 | 54.958 | 91.0767 | 14.8603 | 45.9716 | 37.9636
CZ13 | 270.9274 | 402.1276 | 202.487 | 270.488 | 196.5047 | 291.1384 | 439.131 | 207.8971 | 291.1384 | 213.9155 | 229.7891 | 321.9259 | 179.51 | 230.8643 | 164.9164 | 216.2905 | 310.2717 | 181.4427 | 225.3975 | 159.4054 | 328.3645 | 428.0894 | 246.2628 | 331 | 219.9882 | 348.5933 | 465.7995 | 266.6069 | 355.6385 | 239.4798 | 269.753 | 346.5007 | 215.8687 | 268.3987 | 184.6249 | 258.3794 | 326.9441 | 216.0808 | 261.9741 | 178.4553 | 387.0296 | 475.3921 | 318.975 | 385.9816 | 240.6762 | 368.8426 | 453.0213 | 306.8674 | 369.9321 | 262.0007 | 319.9617 | 393.3181 | 268.8651 | 319.2127 | 201.9872 | 286.7373 | 347.5968 | 245.2324 | 286.346 | 195.2374 | 296.4711 | 467.674 | 116.2228 | 296.4711 | 259.6923 | 339.3839 | 525.7247 | 168.0657 | 339.3839 | 282.7017 | 299.1961 | 439.4745 | 168.0365 | 292.5067 | 217.9465 | 289.1763 | 424.2223 | 165.8274 | 282.1182 | 210.6634 | 348.2704 | 462.9888 | 186.0856 | 347.4235 | 216.4859 | 402.2546 | 527.3462 | 212.1266 | 395.7641 | 236.517 | 359.0275 | 434.7373 | 242.3766 | 334.5262 | 181.1449 | 342.1188 | 422.0263 | 229.9342 | 323.328 | 176.3953 | 382.4745 | 498.7369 | 220.4745 | 361.2028 | 216.0134 | 441.4839 | 559.4851 | 276.7303 | 417.1227 | 237.2596 | 348.7108 | 449.309 | 246.0098 | 330.9456 | 182.6738 | 323.8601 | 433.4528 | 242.0107 | 317.8149 | 177.1301 | 57.437 | 95.7346 | -25.9971 | 60.5119 | 21.8043 | 57.4549 | 113.599 | -28.2206 | 64.5001 | 23.8218 | 39.9639 | 73.2714 | -12.3379 | 37.5344 | 18.2448 | 42.089 | 61.8047 | -10.4943 | 36.5765 | 17.7664 | 116.1022 | 143.0373 | 46.7152 | 115.4935 | 41.0129 | 110.1242 | 140.0403 | 44.8707 | 111.2137 | 44.8078 | 90.1726 | 120.0888 | 40.6585 | 88.3484 | 34.3176 | 87.5224 | 103.3895 | 36.5448 | 78.743 | 33.4178 | 25.5437 | 135.3192 | -156.0371 | 25.9831 | 58.6693 | 48.2455 | 173.5242 | -126.7618 | 48.2455 | 64.0979 | 69.407 | 166.2452 | -60.1701 | 61.6424 | 49.0916 | 72.8859 | 159.0829 | -60.7477 | 56.7207 | 47.8044 | 77.343 | 130.6341 | -86.1743 | 76.9354 | 70.4537 | 111.1162 | 175.1457 | -82.7008 | 104.6257 | 77.3832 | 129.2384 | 161.508 | 14.17 | 103.6619 | 59.5798 | 125.8283 | 156.8869 | 3.3591 | 97.9305 | 57.7717 | 111.5471 | 166.3822 | -51.7854 | 90.7148 | 79.6901 | 150.3455 | 207.2845 | -18.0971 | 125.9843 | 77.6119 | 118.9217 | 176.0797 | 17.8033 | 100.0813 | 67.3346 | 107.5697 | 168.3134 | 15.4356 | 92.4173 | 59.7697
CZ14 | 228.9539 | 311.5038 | 169.9717 | 208.5226 | 160.8784 | 213.1964 | 294.989 | 156.033 | 196.5169 | 151.8351 | 189.2586 | 261.9391 | 138.862 | 192.4793 | 119.509 | 184.4202 | 257.3719 | 136.2933 | 185.2469 | 129.4392 | 273.851 | 351.7974 | 230.4978 | 280.6453 | 167.8329 | 259.3011 | 341.0719 | 216.2681 | 257.3551 | 158.3986 | 206.8963 | 265.7833 | 169.3952 | 221.0114 | 124.6751 | 219.6114 | 288.3154 | 184.7208 | 233.5854 | 135.0346 | 329.6542 | 390.0535 | 261.8562 | 321.8117 | 174.6936 | 309.6777 | 364.4527 | 233.2637 | 298.6814 | 164.8737 | 280.2416 | 320.0206 | 203.6791 | 277.0824 | 129.7716 | 274.9467 | 314.7065 | 205.3574 | 269.5719 | 140.5546 | 306.6468 | 413.0476 | 192.8658 | 317.2569 | 181.4623 | 305.7233 | 403.6522 | 176.6441 | 305.7233 | 171.262 | 307.0657 | 378.3573 | 190.8253 | 308.6899 | 134.7998 | 299.7352 | 370.5951 | 196.4766 | 300.6478 | 146.0006 | 344.4776 | 441.9227 | 279.6641 | 334.6198 | 132.0894 | 341.2592 | 432.0707 | 278.7661 | 323.2801 | 121.833 | 336.0186 | 409.3938 | 276.8112 | 327.4542 | 109.164 | 327.072 | 402.4199 | 280.5025 | 318.2094 | 107.1388 | 394.7703 | 479.8469 | 292.1552 | 374.6691 | 149.0163 | 384.2558 | 470.6062 | 291.4722 | 362.2807 | 140.5018 | 334.704 | 381.1773 | 267.5096 | 313.7301 | 110.1305 | 361.4396 | 415.829 | 292.3648 | 342.1105 | 120.0134 | 19.1226 | 106.828 | -60.2103 | 48.6482 | 5.6781 | 17.0898 | 108.957 | -64.0208 | 34.0932 | 5.2372 | 17.6377 | 85.4291 | -51.0517 | 28.5321 | 4.6926 | 15.7786 | 93.7816 | -55.8489 | 28.8388 | 4.6055 | 100.7003 | 169.8711 | 0.56305 | 113.2891 | 11.2796 | 96.4813 | 160.1432 | -13.4489 | 102.1645 | 10.4038 | 90.983 | 139.6665 | -16.7678 | 84.6031 | 9.3219 | 90.5265 | 138.6997 | -12.301 | 84.325 | 9.149 | 77.693 | 192.8653 | -68.4274 | 108.7343 | 16.806 | 92.5269 | 199.3427 | -70.0684 | 109.2063 | 15.5011 | 117.8071 | 198.0032 | -29.6216 | 116.2106 | 13.8892 | 115.315 | 194.5882 | -21.1818 | 115.4009 | 13.6315 | 115.5237 | 221.7403 | 18.3709 | 126.0972 | 23.4118 | 128.0628 | 227.7613 | 32.0535 | 126.7632 | 22.0741 | 146.76 | 229.0396 | 56.3643 | 134.9749 | 17.3025 | 142.6518 | 226.413 | 62.8442 | 132.9625 | 18.8552 | 140.0419 | 234.8776 | 1.447 | 142.6721 | 23.6393 | 142.0445 | 238.4913 | 11.1832 | 139.0188 | 21.6881 | 145.4454 | 200.8232 | 47.0626 | 121.2508 | 19.2871 | 157.6067 | 221.2951 | 51.795 | 137.3639 | 18.8897
CZ15 | 516.5008 | 832.0627 | 225.7705 | 480.1357 | 342.9326 | 512.7335 | 825.8994 | 326.1543 | 485.0086 | 341.7274 | 394.3076 | 603.597 | 274.212 | 387.9647 | 298.8327 | 412.9273 | 650.6869 | 318.3281 | 435.7734 | 282.8055 | 611.4722 | 920.71 | 353.77 | 609.2268 | 359.8638 | 602.889 | 916.9916 | 451.0491 | 605.3398 | 358.5991 | 464.0817 | 637.5128 | 370.7199 | 450.6781 | 313.5866 | 493.0585 | 677.2381 | 421.0628 | 508.1873 | 296.7681 | 740.2318 | 976.9757 | 491.7915 | 745.255 | 374.4651 | 649.4729 | 836.0678 | 516.4817 | 656.4019 | 373.1491 | 564.9874 | 743.7384 | 454.1115 | 568.2506 | 326.3103 | 552.9744 | 712.9974 | 466.2991 | 572.619 | 308.8093 | 577.122 | 959.7498 | 154.5542 | 577.122 | 388.8714 | 609.0733 | 1002.9895 | 295.8317 | 609.0733 | 387.5047 | 536.0012 | 857.3349 | 298.6659 | 536.0012 | 338.8639 | 568.0311 | 910.628 | 351.9631 | 586.5429 | 320.6897 | 682.987 | 990.1064 | 257.5672 | 652.4394 | 319.2308 | 709.3071 | 960.5762 | 387.4988 | 685.7571 | 318.4182 | 613.7258 | 822.1057 | 430.6339 | 595.4857 | 245.8992 | 654.2324 | 877.1061 | 471.6587 | 650.831 | 265.3214 | 765.8666 | 998.6215 | 360.415 | 704.4155 | 314.8424 | 730.1387 | 1027.6073 | 477.5648 | 728.8316 | 314.7911 | 700.5543 | 957.5835 | 464.0677 | 649.848 | 243.0733 | 652.8952 | 893.9633 | 470.1505 | 646.9725 | 261.4776 | 94.9714 | 308.0189 | -91.3722 | 129.091 | 15.5883 | 90.1555 | 301.6375 | -85.6505 | 120.3312 | 15.5486 | 69.7741 | 168.8891 | -38.4654 | 62.7134 | 12.0074 | 80.1312 | 175.504 | -46.2181 | 72.4139 | 12.9558 | 223.7309 | 364.2846 | 46.6493 | 265.1193 | 29.0315 | 198.1607 | 294.4282 | 44.0743 | 229.4934 | 28.9576 | 170.6798 | 275.1146 | 44.9262 | 180.2859 | 22.3626 | 179.3735 | 259.0476 | 43.5211 | 178.3478 | 24.1289 | 60.6211 | 347.0587 | -290.588 | 96.9863 | 42.2951 | 96.3398 | 387.6354 | -240.8679 | 124.0647 | 42.1875 | 141.6936 | 388.7112 | -110.5194 | 148.0365 | 32.5794 | 155.1037 | 408.894 | -115.3179 | 150.7696 | 35.1526 | 166.4862 | 377.4153 | -187.575 | 172.3037 | 51.0008 | 196.5736 | 345.2221 | -149.2008 | 200.7485 | 50.9925 | 219.4182 | 353.482 | 21.4486 | 207.521 | 39.375 | 241.3051 | 375.372 | 4.3778 | 215.0576 | 42.3563 | 249.3658 | 385.9304 | -84.7272 | 224.2797 | 59.0829 | 217.4052 | 412.2532 | -59.1349 | 243.8229 | 51.8157 | 253.6723 | 426.4766 | 0.3243 | 210.1547 | 45.5654 | 239.9679 | 392.2292 | 2.8696 | 211.1991 | 44.0614
CZ16 | 62.7875 | 80.4594 | 52.9353 | 61.183 | 56.2329 | 42.8331 | 54.0663 | 35.308 | 42.8331 | 38.2075 | 86.0666 | 114.5225 | 71 | 82.4262 | 76.7116 | 71.1953 | 97.9294 | 59.9151 | 71.1953 | 74.7421 | 69.5533 | 82.6771 | 64.5935 | 71.3635 | 68.3197 | 47.9388 | 56.454 | 42.7104 | 49.5954 | 46.4199 | 94.6169 | 113.3817 | 87.1115 | 96.5364 | 93.2001 | 93.3333 | 111.6491 | 84.1102 | 95.3234 | 90.8073 | 89.9208 | 101.2498 | 79.4109 | 87.611 | 78.8379 | 61.5248 | 68.263 | 52.5831 | 60.4235 | 53.5665 | 122.9282 | 137.866 | 109.391 | 118.1157 | 107.5488 | 103.7663 | 114.5944 | 93.0868 | 101.2369 | 104.7876 | 80.3005 | 90.624 | 40.5709 | 71.3278 | 88.3182 | 54.529 | 65.2703 | 23.2511 | 47.3497 | 60.0079 | 128.4889 | 139.1257 | 95.6992 | 116.0492 | 120.4816 | 125.5631 | 136.3247 | 92.0968 | 113.5977 | 117.3883 | 88.1317 | 104.272 | 65.4165 | 82.9598 | 74.3645 | 58.389 | 73.9009 | 42.9147 | 56.0276 | 50.4657 | 138.1038 | 166.7029 | 121.3313 | 130.3152 | 101.2986 | 117.4491 | 142.1198 | 102.6862 | 111.2657 | 86.7269 | 86.7612 | 103.7645 | 73.358 | 80.0837 | 77.6878 | 54.9456 | 69.5589 | 46.6682 | 51.5232 | 52.5226 | 143.4615 | 155.9836 | 132.3871 | 135.4027 | 106.0826 | 140.2461 | 152.595 | 128.3617 | 132.1773 | 102.9172 | 6.7658 | 21.3391 | -7.4632 | 10.1805 | 11.7179 | 5.1057 | 14.8357 | -5.0455 | 6.7623 | 7.9521 | 8.5504 | 32.1589 | -17.1882 | 14.1102 | 15.962 | 11.6682 | 32.1086 | -17.4062 | 13.6582 | 13.6659 | 27.1333 | 39.9117 | 7.3542 | 26.428 | 21.915 | 18.6918 | 26.6447 | 4.8272 | 17.5904 | 14.8721 | 36.8616 | 56.6432 | 5.0913 | 35.6895 | 29.8525 | 32.571 | 45.2514 | 4.5853 | 30.0416 | 25.5582 | 17.513 | 29.286 | -31.4858 | 10.1448 | 31.106 | 11.696 | 23.6519 | -24.5048 | 4.5166 | 21.1093 | 42.4223 | 57.9029 | -8.6005 | 33.623 | 42.3723 | 43.898 | 56.7842 | -9.4196 | 31.9326 | 36.277 | 25.3442 | 42.9339 | -6.6401 | 21.7768 | 38.0429 | 15.5559 | 32.2825 | -4.8412 | 13.1945 | 25.7198 | 52.0373 | 85.4801 | 17.0316 | 47.889 | 51.9475 | 46.2538 | 72.7768 | 14.1847 | 40.0705 | 50.3974 | 23.9737 | 42.4264 | 1.3014 | 18.9007 | 40.7069 | 12.1125 | 27.9405 | -1.0877 | 8.6901 | 27.5622 | 57.3949 | 74.7608 | 28.0874 | 52.9765 | 55.4729 | 58.581 | 73.0546 | 26.8453 | 50.5122 | 47.2656
|  | Graph Scenario: | 1 |  |  |  | Vintage: | 5 |  |  | calibration: | 3
from SEER 10 to SEER 13 | 1978-1992 ACM: DEER 2001
from SEER 10 to SEER 14 | 1978-1992 ACM: RASS T-Stat
from SEER 10 to SEER 15 | 1978-1992 ACM: None
from SEER 10 to SEER 16 | 1978-1992 Max: Improvement from SEER 10 to SEER 13
from SEER 10 to SEER 17
from SEER 10 to SEER 18
from SEER 13 to SEER 14
from SEER 13 to SEER 15
from SEER 13 to SEER 16
from SEER 13 to SEER 17
from SEER 13 to SEER 18

## HP Savings
Residential Heating + Cooling Electricity Savings due to HP equipment SEER improvement
- A comparison of savings based on simulations using detailed performance characteristics
| SEER Increment |  |  |  |  | House Vintage |  |  |  | Calibration Source
|  |  | Median | Min/Max | Min | MedUnit
|  | CZ01* | 123.7269 | 328.126 | -101.4896 | 122.1959 |  | 1
|  | CZ02 | 190.2753 | 447.7688 | -100.5684 | 202.2989 |  | 1
|  | CZ03 | 107.0091 | 258.4417 | -50.7065 | 114.9013 |  | 1
|  | CZ04 | 185.9285 | 352.8172 | -23.7873 | 193.1441 |  | 1
|  | CZ05 | 95.5079 | 222.0377 | -55.5611 | 95.2017 |  | 1
|  | CZ06 | 108.5332 | 169.3223 | 36.7045 | 115.1286 |  | 1
|  | CZ07 | 119.9105 | 163.4311 | 65.3465 | 128.6632 |  | 1
|  | CZ08 | 174.3974 | 234.1558 | 107.4631 | 185.9967 |  | 1
|  | CZ09 | 165.9574 | 230.3376 | 96.7124 | 180.41 |  | 1
|  | CZ10 | 197.311 | 272.1783 | 126.3797 | 209.0359 |  | 1
|  | CZ11 | 273.174 | 462.7849 | 38.4594 | 281.7155 |  | 1
|  | CZ12 | 241.4265 | 415.9456 | 24.4151 | 241.9775 |  | 1
|  | CZ13 | 322.3281 | 496.276 | 161.3919 | 337.704 |  | 1
|  | CZ14 | 294.6727 | 437.293 | 28.3195 | 295.932 |  | 1
|  | CZ15 | 455.4528 | 666.2927 | 285.7379 | 487.981 |  | 1
|  | CZ16 | 271.7081 | 1023.9207 | -600.6422 | 267.668 |  | 1
* For the DEER 2001 Update, climate zone CZ01 was prescribed to have no residential cooling load
| Median: | savings determined by comparing the actual median performing unit at each SEER level
| Min/Max: | minimum and maximum savings determined by comparing best and worse perfoming units at each SEER level
| Med Unit: | savings determined by comparing the chosen "median unit" at each SEER level
Summary Results - Electricity savings per year per ton of cooling equipment installed
- Vintage results weighted based on RASS data for homes with central heating
Residential HP Energy Savings by Climate Zone and SEER Improvement Level - kWh/yr per ton
| SEER 10 to SEER 13 |  |  |  | SEER 10 to SEER 14 |  |  |  | SEER 10 to SEER 15 |  |  |  | SEER 10 to SEER 16 |  |  |  | SEER 10 to SEER 17 |  |  |  | SEER 10 to SEER 18 |  |  |  | SEER 13 to SEER 14 |  |  |  | SEER 13 to SEER 15 |  |  |  | SEER 13 to SEER 16 |  |  |  | SEER 13 to SEER 17 |  |  |  | SEER 13 to SEER 18
| Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU
CZ01* | 123.7269 | 328.126 | -101.4896 | 122.1959 | 149.8851 | 235.8426 | -38.3924 | 172.3292 | 155.8559 | 358.6986 | -108.2375 | 185.1317 | 12.7555 | 217.6269 | -235.2917 | 13.2431 | -39.8605 | 190.71 | -215.1742 | -138.6025 | -37.2572 | 165.2782 | -208.2128 | -64.7269 | 26.1582 | 201.5263 | -230.7125 | 50.1333 | 32.4942 | 324.6148 | -300.0248 | 63.2582 | -104.1416 | 184.8879 | -417.1041 | -102.3066 | -156.7576 | 157.9709 | -396.9865 | -254.1523 | -160.6189 | 131.1944 | -400.0001 | -186.6004
CZ02 | 190.2753 | 447.7688 | -100.5684 | 202.2989 | 200.6002 | 293.8353 | -41.7157 | 219.209 | 188.8456 | 476.3045 | -90.9235 | 216.8056 | -24.6244 | 194.9266 | -364.3614 | -35.4178 | -109.9535 | 179.5592 | -333.7982 | -278.7987 | -120.7197 | 128.1131 | -343.2683 | -158.1241 | 10.325 | 286.2519 | -381.3326 | 16.91 | -1.4297 | 468.721 | -430.5404 | 14.5067 | -214.8996 | 187.3432 | -703.9783 | -237.7167 | -300.2288 | 171.9758 | -673.4151 | -481.0976 | -310.9949 | 120.5297 | -682.8852 | -360.423
CZ03 | 107.0091 | 258.4417 | -50.7065 | 114.9013 | 135.0924 | 211.1975 | 0.41696 | 158.4884 | 149.9716 | 301.7376 | -51.202 | 176.6348 | 35.6172 | 215.0241 | -150.7675 | 40.7983 | 6.0656 | 186.0532 | -123.8288 | -56.9634 | 14.1304 | 164.5287 | -101.8923 | 0.04081 | 28.0834 | 150.6351 | -146.7558 | 43.587 | 42.9626 | 241.1752 | -198.3748 | 61.7335 | -69.9107 | 155.7227 | -296.0487 | -72.5376 | -99.4623 | 126.7518 | -269.11 | -170.2993 | -92.8787 | 103.9663 | -249.065 | -114.8605
CZ04 | 185.9285 | 352.8172 | -23.7873 | 193.1441 | 205.867 | 276.2784 | 35.0912 | 226.5879 | 219.0391 | 401.1289 | -14.3045 | 247.7093 | 47.6281 | 228.2546 | -192.6549 | 46.2764 | 10.6519 | 199.0698 | -150.1655 | -93.7697 | 4.8724 | 180.5415 | -140.017 | -17.7992 | 19.9384 | 208.8085 | -226.4687 | 33.4438 | 33.1105 | 333.6589 | -275.8644 | 54.5652 | -128.5539 | 163.5226 | -440.2103 | -136.7077 | -165.5301 | 134.3378 | -397.7209 | -276.7538 | -182.133 | 112.2175 | -402.8359 | -212.0442
CZ05 | 95.5079 | 222.0377 | -55.5611 | 95.2017 | 112.3614 | 162.8694 | -9.0877 | 122.2099 | 115.7332 | 248.2185 | -50.497 | 131.3546 | 3.6551 | 140.0894 | -161.9942 | -3.2997 | -31.4716 | 128.2873 | -151.2665 | -109.351 | -30.3784 | 98.7854 | -142.7295 | -51.9298 | 16.8535 | 140.4936 | -153.1885 | 27.0081 | 20.2254 | 225.8427 | -194.5978 | 36.1529 | -89.7845 | 119.2051 | -303.3027 | -96.4333 | -124.9112 | 107.403 | -292.5751 | -202.4846 | -125.8862 | 76.4096 | -286.8303 | -147.1315
CZ06 | 108.5332 | 169.3223 | 36.7045 | 115.1286 | 131.0138 | 173.379 | 75.6386 | 143.0744 | 155.0015 | 218.3122 | 55.5161 | 168.1316 | 95.4117 | 192.314 | 18.9733 | 98.7061 | 105.8815 | 176.8299 | 47.9852 | 86.6799 | 117.4633 | 185.7966 | 75.2601 | 113.9529 | 22.4806 | 74.8716 | -31.8808 | 27.9458 | 48.3601 | 121.4591 | -50.1968 | 54.9318 | -10.0491 | 96.5751 | -85.5319 | -13.2555 | 0.42074 | 81.091 | -56.5201 | -25.2817 | 8.9301 | 87.2892 | -32.2593 | -1.1757
CZ07 | 119.9105 | 163.4311 | 65.3465 | 128.6632 | 142.4285 | 174.1095 | 103.9076 | 154.1603 | 172.8855 | 217.3455 | 94.0479 | 187.0857 | 111.5829 | 180.9945 | 43.1122 | 115.2559 | 123.8099 | 173.9533 | 77.4922 | 108.6067 | 140.3709 | 189.7625 | 106.7063 | 140.9497 | 22.518 | 66.2248 | -16.9854 | 25.4971 | 52.975 | 109.4608 | -26.845 | 58.4225 | -2.4211 | 78.5117 | -71.8142 | -7.0398 | 9.8059 | 71.4705 | -37.4342 | -13.689 | 20.4605 | 81.8778 | -14.1867 | 12.2865
CZ08 | 174.3974 | 234.1558 | 107.4631 | 185.9967 | 202.4864 | 244.0064 | 158.2351 | 216.757 | 252.1592 | 303.6056 | 143.7984 | 273.154 | 164.4642 | 249.2642 | 35.1417 | 169.716 | 169.2653 | 234.0671 | 103.2837 | 139.6329 | 185.1315 | 243.1744 | 134.1905 | 185.4225 | 28.089 | 96.1015 | -35.4789 | 30.7604 | 77.7618 | 155.7007 | -49.9155 | 87.1574 | -9.9332 | 101.3593 | -158.5722 | -16.2806 | -5.1321 | 86.1622 | -90.4303 | -46.3638 | 9.4911 | 94.0904 | -60.7748 | -1.878
CZ09 | 165.9574 | 230.3376 | 96.7124 | 180.41 | 198.2261 | 252.8384 | 153.995 | 209.6096 | 250.4554 | 301.9883 | 150.8425 | 277.7371 | 156.89 | 261.8771 | 15.2269 | 165.3654 | 154.5699 | 240.5744 | 87.4579 | 122.8698 | 184.0586 | 246.1864 | 109.0883 | 187.974 | 32.2687 | 111.445 | -31.6615 | 29.1996 | 84.498 | 160.5949 | -34.8141 | 97.3271 | -9.0674 | 120.4837 | -170.4297 | -15.0446 | -11.3874 | 99.181 | -98.1987 | -57.5401 | 16.5056 | 103.3616 | -78.2126 | 6.003
CZ10 | 197.311 | 272.1783 | 126.3797 | 209.0359 | 236.7899 | 291.7852 | 184.4175 | 251.2068 | 296.4753 | 354.1831 | 201.3991 | 319.4248 | 197.4306 | 291.0534 | 20.3615 | 206.5285 | 183.0574 | 288.5359 | 105.7239 | 138.7783 | 226.3452 | 295.9359 | 113.0728 | 228.4701 | 39.4789 | 125.3952 | -47.7506 | 42.1709 | 99.1643 | 187.7932 | -30.769 | 110.3889 | 0.1196 | 124.6634 | -211.8066 | -2.5074 | -14.2536 | 122.1459 | -126.4441 | -70.2576 | 17.381 | 120.0259 | -133.0194 | 7.3276
CZ11 | 273.174 | 462.7849 | 38.4594 | 281.7155 | 312.4186 | 382.9893 | 132.0868 | 341.7175 | 353.7971 | 554.3606 | 112.8175 | 382.477 | 152.4522 | 335.0171 | -183.509 | 143.0176 | 90.5572 | 311.8482 | -115.8572 | -58.76 | 107.8503 | 297.1158 | -130.0391 | 82.07 | 39.2446 | 269.9358 | -256.104 | 60.002 | 80.6231 | 441.3071 | -275.3733 | 100.7614 | -120.7218 | 221.9636 | -571.6998 | -138.6979 | -182.6168 | 198.7947 | -504.048 | -340.4756 | -183.5922 | 173.7841 | -542.9909 | -218.1333
CZ12 | 241.4265 | 415.9456 | 24.4151 | 241.9775 | 264.8066 | 336.1576 | 99.7226 | 282.9982 | 302.4306 | 475.9776 | 62.0259 | 325.9465 | 110.5085 | 285.7249 | -214.7194 | 99.2167 | 49.0786 | 249.0614 | -143.2297 | -92.6195 | 66.1713 | 244.7909 | -143.0097 | 32.852 | 23.3801 | 240.3531 | -244.8336 | 41.0208 | 61.0041 | 380.1731 | -282.5303 | 83.969 | -130.918 | 189.9203 | -559.2756 | -142.7608 | -192.3479 | 153.2569 | -487.7859 | -334.597 | -187.6143 | 141.8093 | -504.5458 | -221.4586
CZ13 | 322.3281 | 496.276 | 161.3919 | 337.704 | 367.0092 | 474.7349 | 248.749 | 398.3633 | 431.0652 | 579.5102 | 235.3742 | 462.304 | 234.2464 | 412.4876 | -97.5858 | 245.0484 | 199.5556 | 389.0716 | 33.8111 | 89.9855 | 232.9021 | 390.756 | 34.2313 | 219.0221 | 44.681 | 239.4817 | -173.6657 | 60.6592 | 120.8677 | 355.2147 | -171.5522 | 137.5282 | -89.4914 | 175.9972 | -521.6581 | -94.1543 | -124.1822 | 152.5812 | -390.2612 | -249.2173 | -93.9991 | 151.4999 | -393.6117 | -123.3705
CZ14 | 294.6727 | 437.293 | 28.3195 | 295.932 | 328.8613 | 393.0717 | 139.2696 | 344.9605 | 364.2416 | 572.7576 | 186.0671 | 374.2817 | 201.9998 | 357.9166 | -130.0077 | 182.4472 | 145.7472 | 399.684 | -89.9352 | -27.0883 | 154.0758 | 346.0763 | -128.317 | 127.2647 | 34.1886 | 263.1616 | -196.4328 | 49.0284 | 69.5689 | 442.8475 | -149.6353 | 78.3496 | -92.6729 | 228.0064 | -465.7102 | -113.4849 | -148.9255 | 269.7739 | -425.6377 | -323.0204 | -179.0725 | 199.0216 | -507.7885 | -207.3036
CZ15 | 455.4528 | 666.2927 | 285.7379 | 487.981 | 588.4572 | 757.1943 | 403.8839 | 614.2883 | 669.994 | 780.4831 | 551.3734 | 717.2709 | 578.6991 | 744.0743 | 250.2214 | 643.5466 | 592.7216 | 815.5732 | 444.3742 | 601.9676 | 745.9117 | 861.3235 | 546.5131 | 798.6603 | 133.0044 | 298.2242 | -89.1765 | 126.3074 | 244.5467 | 352.6926 | 90.3229 | 261.2674 | 123.2463 | 285.1042 | -242.8391 | 155.5656 | 137.2688 | 356.6031 | -48.6863 | 113.9867 | 264.5331 | 377.2268 | 24.8736 | 282.7342
CZ16 | 271.7081 | 1023.9207 | -600.6422 | 267.668 | 222.2234 | 476.292 | -573.9201 | 111.2676 | 75.6091 | 898.7222 | -555.4457 | -29.4917 | -233.8581 | 239.1448 | -1150.4302 | -392.7198 | -402.5241 | 286.133 | -1137.1627 | -1008.668 | -548.6962 | 66.1377 | -1189.723 | -763.2997 | -49.4847 | 671.2977 | -1192.2043 | -156.4004 | -195.7192 | 1093.7837 | -1173.043 | -296.8614 | -505.1864 | 434.2063 | -1768.0274 | -660.0894 | -673.8524 | 481.1945 | -1754.76 | -1276.0377 | -820.4043 | 261.1434 | -1808.0072 | -1030.9678
Detailed Results
- including Median, Maximum, Minimum and "Median Unit" Savings by Vintage and Climate Zone
- all values in kWh/year per ton of installed cooling capacity
| SEER 10 to SEER 13 Med: SEER 10 to SEER 13; SEER 10 to SEER 17 Med: SEER 10 to SEER 14; SEER 13 to SEER 16 Med: SEER 10 to SEER 15 |  |  |  |  | SEER 10 to SEER 16 | [15 empty] | SEER 10 to SEER 17 | [15 empty] | SEER 10 to SEER 18 | [15 empty] | SEER 13 to SEER 14 | [15 empty] | SEER 13 to SEER 15 | [15 empty] | SEER 13 to SEER 16 | [15 empty] | SEER 13 to SEER 17 | [15 empty] | SEER 13 to SEER 18
| SEER 10 to SEER 13 Med: Pre-1978; SEER 10 to SEER 14 Med: 1978-1992; SEER 10 to SEER 15 Med: 1992-1998; SEER 10 to SEER 16 Med: Post-1998; SEER 10 to SEER 17 Med: Pre-1978; SEER 10 to SEER 18 Med: 1978-1992; SEER 13 to SEER 14 Med: 1992-1998; SEER 13 to SEER 15 Med: Post-1998; SEER 13 to SEER 16 Med: Pre-1978; SEER 13 to SEER 17 Med: 1978-1992; SEER 13 to SEER 18 Med: 1992-1998 | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998 |  |  |  | Pre-1978 |  |  |  | 1978-1992 |  |  |  | 1992-1998 |  |  |  | Post-1998
| Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU | Med | Max | Min | MU
CZ01* | 151.3741 | 412.0463 | -164.3292 | 151.8074 | 99.6568 | 273.3828 | -54.767 | 106.064 | 100.5214 | 235.745 | -25.0769 | 88.7107 | 87.5 | 210.6973 | -22.5539 | 78.0814 | 182.6941 | 278.2096 | -91.7889 | 207.4727 | 132.4145 | 214.4777 | -0.44726 | 154.2435 | 114.0992 | 187.3831 | 29.2025 | 133.9676 | 99.9935 | 171.315 | 29.1322 | 118.2902 | 172.4685 | 450.7105 | -170.0197 | 201.9537 | 147.6689 | 304.4843 | -66.2124 | 179.0694 | 140.7083 | 244.4366 | -31.1831 | 166.975 | 128.5487 | 230.4224 | -27.7339 | 156.6431 | -21.4179 | 233.4283 | -345.041 | -25.8307 | 19.6398 | 200.6173 | -208.3886 | 25.97 | 76.6127 | 219.5958 | -70.9125 | 79.5248 | 63.1775 | 192.8942 | -58.8044 | 69.3494 | -98.9018 | 195.9397 | -309.9727 | -214.5576 | -36.3645 | 188.3421 | -203.2968 | -135.6233 | 66.1443 | 200.465 | -66.633 | -13.5821 | 57.4663 | 175.0511 | -54.7685 | -6.5556 | -106.711 | 156.765 | -314.2147 | -145.8776 | -20.1296 | 161.3079 | -187.7101 | -40.3925 | 74.6048 | 187.6899 | -44.2819 | 58.7917 | 70.6309 | 180.3004 | -34.8559 | 60.5169 | 31.32 | 269.7582 | -331.0546 | 55.6653 | 32.7577 | 157.8102 | -162.3956 | 48.1795 | 13.5778 | 123.3872 | -117.4697 | 45.257 | 12.4936 | 106.7081 | -94.4044 | 40.2087 | 21.0945 | 442.2592 | -409.2854 | 50.1463 | 48.0121 | 247.8167 | -228.1607 | 73.0055 | 44.0531 | 182.9021 | -172.2141 | 81.6763 | 41.0487 | 165.8156 | -151.2705 | 78.5617 | -162.9589 | 225.5259 | -568.7643 | -167.7768 | -80.017 | 143.9498 | -370.3369 | -80.0939 | -20.0425 | 158.0612 | -211.9435 | -5.7739 | -17.1166 | 133.608 | -172.1675 | -2.3018 | -240.4428 | 188.0374 | -533.696 | -356.5038 | -136.0213 | 131.6746 | -365.2452 | -241.6872 | -30.5108 | 138.9304 | -207.664 | -98.8808 | -22.8278 | 115.7649 | -168.1315 | -78.2068 | -258.0851 | 148.3136 | -553.4804 | -297.685 | -119.7863 | 104.6404 | -349.6585 | -146.4565 | -22.0504 | 126.1554 | -185.313 | -26.507 | -16.8691 | 115.6935 | -158.3925 | -17.5645 | 1
CZ02 | 206.0204 | 533.8546 | -181.3922 | 225.5436 | 161.8321 | 326.3737 | -3.6618 | 163.2601 | 195.4187 | 317.8705 | 103.7679 | 195.4187 | 186.2342 | 295.9912 | 102.149 | 186.2342 | 205.342 | 319.6895 | -123.9219 | 228.5093 | 185.9782 | 250.8689 | 55.234 | 197.6576 | 231.6119 | 286.2145 | 174.2129 | 245.583 | 220.4227 | 271.2363 | 169.7369 | 233.0099 | 170.0369 | 554.3327 | -174.205 | 199.3684 | 200.2052 | 362.3074 | 4.3556 | 227.0847 | 290.1461 | 376.512 | 137.7517 | 312.9976 | 275.8805 | 354.3856 | 139.6415 | 296.8965 | -85.6399 | 201.067 | -466.393 | -99.8694 | 27.5796 | 157.938 | -272.7627 | 21.9623 | 221.5257 | 311.9244 | 20.5949 | 214.4638 | 215.2888 | 298.7325 | 29.922 | 209.1866 | -170.742 | 165.3575 | -427.8231 | -355.76 | -71.434 | 173.9066 | -257.8436 | -226.4766 | 191.4438 | 318.5403 | 57.5217 | 83.6599 | 189.2093 | 304.1565 | 65.3261 | 90.1796 | -202.2433 | 97.3588 | -438.2388 | -245.2694 | -51.9489 | 142.1347 | -269.7003 | -83.605 | 209.0027 | 308.204 | 65.4555 | 189.0854 | 208.7425 | 297.0346 | 73.4206 | 191.0614 | -0.67837 | 355.8206 | -512.5154 | 2.9657 | 24.1461 | 195.9132 | -212.522 | 34.3975 | 36.1933 | 145.4193 | -106.6303 | 50.1643 | 34.1885 | 133.9329 | -91.0998 | 46.7757 | -35.9835 | 590.4638 | -562.7985 | -26.1752 | 38.3731 | 307.3516 | -263.4005 | 63.8246 | 94.7274 | 235.7167 | -143.0915 | 117.579 | 89.6463 | 217.0822 | -121.1953 | 110.6623 | -291.6603 | 237.1981 | -854.9865 | -325.4131 | -134.2525 | 102.9823 | -540.5188 | -141.2978 | 26.1071 | 171.1291 | -260.2482 | 19.0452 | 29.0546 | 161.4291 | -230.9148 | 22.9525 | -376.7624 | 201.4887 | -816.4166 | -581.3036 | -233.2661 | 118.9508 | -525.5997 | -389.7367 | -3.9749 | 177.7451 | -223.3215 | -111.7588 | 2.9751 | 166.8531 | -195.5106 | -96.0546 | -408.2637 | 133.4899 | -826.8324 | -470.8131 | -213.781 | 87.179 | -537.4564 | -246.8651 | 13.584 | 167.4088 | -215.3877 | -6.3333 | 22.5084 | 159.7311 | -187.4162 | 4.8273 | 2
CZ03 | 118.6585 | 291.8252 | -66.9642 | 128.0653 | 72.4652 | 177.4316 | -22.7674 | 76.6281 | 88.7913 | 171.5486 | 17.0673 | 93.8064 | 72.6537 | 131.515 | 18.1136 | 71.5559 | 148.9267 | 233.9856 | -11.7664 | 176.3169 | 96.1599 | 152.1297 | 16.9632 | 109.9336 | 110.0993 | 160.7958 | 61.4556 | 123.8348 | 88.6583 | 124.8505 | 52.7972 | 93.7408 | 161.8681 | 339.5822 | -69.2301 | 191.6015 | 111.911 | 207.3662 | -22.1429 | 131.3167 | 138.9614 | 208.8131 | 27.9634 | 158.3146 | 111.6145 | 159.4822 | 27.1129 | 122.6575 | 30.0881 | 235.5934 | -190.0727 | 35.917 | 33.6032 | 155.3229 | -86.575 | 37.7477 | 81.7479 | 178.4578 | 19.2267 | 84.9143 | 74.2667 | 158.9049 | 22.0643 | 73.7006 | -9.1065 | 202.1879 | -155.5008 | -78.3602 | 18.5775 | 138.1174 | -80.1281 | -34.8862 | 95.6479 | 160.2397 | 27.9593 | 60.854 | 91.1706 | 141.2396 | 30.4791 | 55.933 | -1.4183 | 171.3216 | -131.7298 | -17.503 | 27.6495 | 134.4408 | -68.7283 | 16.8156 | 107.0624 | 178.93 | 58.3 | 102.1029 | 91.71 | 140.0642 | 50.099 | 84.6832 | 30.2682 | 174.5734 | -177.2152 | 48.2517 | 23.6946 | 95.3547 | -80.926 | 33.3055 | 21.308 | 80.8995 | -47.264 | 30.0284 | 16.0046 | 62.1056 | -34.0864 | 22.1849 | 43.2096 | 280.1701 | -234.679 | 63.5363 | 39.4458 | 150.5911 | -120.0321 | 54.6886 | 50.1701 | 128.9168 | -80.7561 | 64.5083 | 38.9608 | 96.7372 | -59.7708 | 51.1017 | -88.5704 | 176.1812 | -355.5215 | -92.1482 | -35.4574 | 101.2153 | -179.865 | -35.2802 | 4.3401 | 108.8046 | -75.5544 | 3.1344 | 1.613 | 96.16 | -64.8193 | 2.1447 | -127.765 | 142.7757 | -320.9496 | -206.4255 | -50.4831 | 84.0098 | -173.4181 | -107.9141 | 18.2401 | 90.5865 | -66.8218 | -20.9259 | 18.5169 | 78.4947 | -56.4045 | -15.6229 | -120.0768 | 111.9095 | -297.1786 | -145.5683 | -44.8158 | 77.6657 | -166.6175 | -59.8125 | 18.2711 | 99.0336 | -50.4195 | 8.2966 | 19.0562 | 77.3192 | -36.7847 | 13.1274 | 3
CZ04 | 202.9764 | 397.9914 | -49.3202 | 211.5872 | 131.4883 | 232.3168 | 28.6311 | 134.9402 | 172.5015 | 240.8193 | 103.0375 | 175.318 | 143.2293 | 200.0037 | 81.0423 | 146.4321 | 221.185 | 301.3079 | 12.2775 | 246.078 | 157.2503 | 203.2389 | 78.0056 | 168.4254 | 199.7425 | 237.0065 | 166.1849 | 207.3421 | 162.9084 | 200.5439 | 132.2453 | 165.5029 | 227.0832 | 448.8731 | -44.0898 | 259.5852 | 182.9503 | 270.9453 | 42.8831 | 203.4349 | 255.8392 | 296.0858 | 138.7568 | 270.6954 | 210.5189 | 241.8355 | 119.1163 | 221.5048 | 28.4506 | 237.1845 | -242.0155 | 26.6569 | 71.1939 | 181.5608 | -111.0309 | 71.811 | 188.0525 | 279.0982 | 73.9354 | 185.5273 | 156.1137 | 236.5869 | 67.8025 | 154.7783 | -14.4244 | 199.6453 | -192.7821 | -128.8133 | 37.9309 | 174.8692 | -91.5514 | -51.5659 | 197.4688 | 271.6753 | 112.4449 | 140.6845 | 163.2537 | 234.2971 | 97.882 | 120.6664 | -28.217 | 176.2686 | -186.6567 | -54.2376 | 49.0628 | 163.2695 | -78.671 | 32.8862 | 208.9221 | 263.3036 | 142.8868 | 200.3121 | 202.1008 | 254.7454 | 144.1291 | 196.0652 | 18.2086 | 244.2876 | -279.3734 | 34.4908 | 25.7619 | 118.2108 | -97.9142 | 33.4852 | 27.241 | 99.5657 | -40.2311 | 32.0241 | 19.6791 | 86.9506 | -35.2074 | 19.0708 | 24.1068 | 391.8528 | -335.7407 | 47.998 | 51.462 | 185.9172 | -133.0366 | 68.4947 | 83.3377 | 158.645 | -67.6593 | 95.3774 | 67.2896 | 128.2422 | -48.3363 | 75.0727 | -161.2787 | 183.8856 | -514.632 | -171.1212 | -60.2944 | 96.5326 | -286.9507 | -63.1291 | 15.551 | 141.6574 | -132.4806 | 10.2093 | 12.8844 | 122.9936 | -99.6502 | 8.3462 | -204.1537 | 146.3464 | -465.3986 | -326.5915 | -93.5574 | 89.8411 | -267.4711 | -186.506 | 24.9673 | 134.2346 | -93.9711 | -34.6335 | 20.0244 | 120.7037 | -69.5707 | -25.7657 | -231.1934 | 119.2483 | -478.3075 | -265.8248 | -82.4255 | 78.2414 | -254.5908 | -102.054 | 36.4206 | 125.8629 | -63.5292 | 24.9941 | 37.8084 | 124.4471 | -47.949 | 28.0989 | 4
CZ05 | 112.5791 | 276.4292 | -95.7667 | 112.5791 | 63.7548 | 149.305 | -12.9355 | 63.7548 | 79.8637 | 137.621 | 25.4353 | 79.8552 | 65.7916 | 104.643 | 25.2694 | 59.4314 | 129.7594 | 191.8391 | -39.5095 | 143.1563 | 81.6797 | 119.5703 | 17.5222 | 87.8027 | 95.9073 | 125.7092 | 60.8749 | 100.2325 | 76.2411 | 97.3612 | 51.2505 | 74.0248 | 125.3574 | 305.396 | -92.7689 | 144.2566 | 91.0186 | 167.5497 | -9.8776 | 104.1237 | 118.3478 | 165.6221 | 40.0548 | 128.3223 | 95.1722 | 125.1644 | 36.9877 | 97.2084 | -25.4294 | 156.4461 | -238.3715 | -35.9222 | 23.9985 | 101.6761 | -105.4507 | 23.4348 | 75.2586 | 134.6762 | 17.3166 | 73.7405 | 69.7565 | 118.4003 | 23.5701 | 63.347 | -72.5842 | 138.0838 | -223.8489 | -169.1501 | -12.1688 | 103.5958 | -102.9068 | -74.7064 | 78.6801 | 128.4088 | 25.5477 | 43.4702 | 77.0254 | 112.7816 | 29.7245 | 41.4843 | -78.9699 | 88.4783 | -214.1844 | -106.8413 | 1.1881 | 95.8916 | -105.5799 | -13.8006 | 92.5263 | 142.9017 | 44.6744 | 84.4698 | 81.0143 | 111.3233 | 41.9821 | 70.5301 | 17.1803 | 186.6079 | -214.9407 | 30.5772 | 17.9249 | 80.4641 | -79.7411 | 24.0479 | 16.0437 | 64.3699 | -40.8421 | 20.3773 | 10.4495 | 47.1904 | -28.4912 | 14.5933 | 12.7783 | 300.1647 | -268.2001 | 31.6776 | 27.2638 | 128.4435 | -107.141 | 40.3689 | 38.4841 | 104.2829 | -61.6623 | 48.4671 | 29.3806 | 74.9937 | -42.754 | 37.7769 | -138.0085 | 151.2148 | -413.8028 | -148.5013 | -36.7609 | 64.4072 | -198.1443 | -37.3246 | 5.6339 | 81.2009 | -71.3598 | 4.1231 | 3.9649 | 68.2296 | -56.1716 | 3.9156 | -185.1633 | 132.8525 | -399.2801 | -281.7291 | -72.9282 | 66.327 | -195.6004 | -135.4659 | 9.0554 | 74.9336 | -63.1287 | -26.1472 | 11.2338 | 62.6108 | -50.0172 | -17.9472 | -191.549 | 83.247 | -389.6157 | -219.4203 | -62.5667 | 56.7854 | -202.8432 | -77.5554 | 12.6626 | 81.5625 | -57.0426 | 4.6146 | 15.2227 | 61.1526 | -37.7596 | 11.0987 | 5
CZ06 | 113.8798 | 190.6021 | 25.1395 | 122.393 | 91.3103 | 138.4714 | 28.5572 | 93.0921 | 119.1779 | 139.2615 | 95.1305 | 124.9975 | 99.5285 | 116.261 | 81.7684 | 103.9248 | 139.4467 | 193.1152 | 68.2201 | 155.9306 | 108.6408 | 141.8928 | 62.8559 | 117.3118 | 137.3856 | 152.1131 | 127.2325 | 139.4946 | 115.6376 | 124.5617 | 108.3344 | 113.5219 | 166.6812 | 249.3021 | 42.799 | 184.1152 | 118.1318 | 159.4354 | 35.5233 | 127.6625 | 168.4701 | 190.756 | 133.0475 | 171.5923 | 141.9776 | 156.2822 | 116.7485 | 142.2098 | 92.3365 | 213.8378 | -7.9688 | 98.3601 | 73.0995 | 147.7576 | 18.7134 | 76.3033 | 135.1672 | 168.8048 | 118.0817 | 129.7541 | 128.7466 | 160.4754 | 116.2737 | 121.3102 | 97.9618 | 193.4593 | 26.2148 | 74.7647 | 86.5852 | 130.5632 | 33.4224 | 63.4712 | 157.0974 | 171.5216 | 147.1058 | 157.4351 | 155.7133 | 165.9418 | 140.3262 | 154.8924 | 107.8824 | 192.9993 | 56.1867 | 105.226 | 103.2629 | 151.0311 | 62.3223 | 95.9349 | 185.0259 | 215.067 | 172.7943 | 181.7779 | 154.1369 | 185.0587 | 147.563 | 152.5995 | 25.5669 | 89.9857 | -44.392 | 33.5376 | 17.3306 | 62.0504 | -24.3303 | 24.2197 | 18.2078 | 39.639 | 5.3146 | 14.4971 | 16.1091 | 30.026 | 4.8407 | 9.5972 | 52.8014 | 146.1727 | -69.8132 | 61.7222 | 36.5028 | 88.0584 | -42.4188 | 44.4407 | 49.2923 | 78.2819 | 11.1296 | 46.5949 | 42.449 | 61.7465 | 13.2547 | 38.285 | -21.5433 | 110.7084 | -120.581 | -24.0329 | -8.5295 | 76.3806 | -59.2288 | -6.9186 | 30.8866 | 70.3899 | 11.4035 | 20.3813 | 29.218 | 65.9397 | 12.7799 | 17.3854 | -15.918 | 90.3299 | -86.3973 | -47.6284 | 4.9562 | 59.1862 | -44.5197 | -19.7507 | 52.8168 | 73.1068 | 40.4276 | 48.0623 | 56.1848 | 71.4061 | 36.8324 | 50.9677 | -5.9974 | 89.8699 | -56.4254 | -17.167 | 11.9526 | 71.1887 | -24.8639 | 2.8428 | 65.8481 | 102.5929 | 50.8764 | 56.7805 | 54.6084 | 90.523 | 44.0692 | 48.6748 | 6
CZ07 | 129.1748 | 189.4507 | 54.2846 | 139.2059 | 106.1307 | 137.4781 | 59.3506 | 112.8832 | 129.5206 | 157.2916 | 111.2464 | 143.5893 | 111.6552 | 129.4754 | 95.9907 | 112.3215 | 154.4325 | 197.8804 | 98.3716 | 170.9445 | 124.5305 | 149.2311 | 94.1169 | 135.5773 | 154.5354 | 170.5521 | 145.1734 | 159.9574 | 132.6306 | 145.9301 | 123.7569 | 124.4492 | 186.3321 | 250.5408 | 79.7569 | 204.5352 | 151.2458 | 184.1538 | 82.4975 | 165.5973 | 190.7669 | 209.7173 | 161.211 | 198.5869 | 162.9044 | 174.1061 | 140.6596 | 158.3342 | 111.2486 | 207.5995 | 11.6708 | 117.9891 | 93.8292 | 147.2024 | 41.4699 | 96.6871 | 148.894 | 181.63 | 126.6812 | 149.9979 | 145.7065 | 174.8951 | 130.1431 | 135.9696 | 117.1404 | 195.1556 | 52.9441 | 95.3152 | 107.7588 | 138.4914 | 67.7296 | 92.7066 | 173.3184 | 191.3375 | 162.6709 | 178.4367 | 172.5384 | 186.2746 | 156.5747 | 167.6889 | 130.4869 | 199.2796 | 82.348 | 130.5951 | 126.0824 | 159.9296 | 98.8237 | 126.7629 | 204.1969 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7
CZ08 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 8
CZ09 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 9
CZ10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 10
CZ11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 11
CZ12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 12
CZ13 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 13
CZ14 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 14
CZ15 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 15
CZ16 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 16
| 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 11 | 12 | 13 | 14 | 16 | 17 | 18 | 19 | 21 | 22 | 23 | 24 | 26 | 27 | 28 | 29 | 31 | 32 | 33 | 34 | 36 | 37 | 38 | 39 | 41 | 42 | 43 | 44 | 46 | 47 | 48 | 49 | 51 | 52 | 53 | 54 | 56 | 57 | 58 | 59 | 61 | 62 | 63 | 64 | 66 | 67 | 68 | 69 | 71 | 72 | 73 | 74 | 76 | 77 | 78 | 79 | 81 | 82 | 83 | 84 | 86 | 87 | 88 | 89 | 91 | 92 | 93 | 94 | 96 | 97 | 98 | 99 | 101 | 102 | 103 | 104 | 106 | 107 | 108 | 109 | 111 | 112 | 113 | 114 | 116 | 117 | 118 | 119 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 11 | 12 | 13 | 14 | 16 | 17 | 18 | 19 | 21 | 22 | 23 | 24 | 26 | 27 | 28 | 29 | 31 | 32 | 33 | 34 | 36 | 37 | 38 | 39 | 41 | 42 | 43 | 44 | 46 | 47 | 48 | 49 | 51 | 52 | 53 | 54 | 56 | 57 | 58 | 59 | 61 | 62 | 63 | 64 | 66 | 67 | 68 | 69 | 71 | 72 | 73 | 74 | 76 | 77 | 78 | 79 | 81 | 82 | 83 | 84 | 86 | 87 | 88 | 89 | 91 | 92 | 93 | 94 | 96 | 97 | 98 | 99
Graph Data:
|  | Graph Scenario: | 1 |  |  |  | Vintage: | 5 |  |  | calibration: | 3
from SEER 10 to SEER 13 | 1992-1998 Max: DEER 2001
from SEER 10 to SEER 14 | 1992-1998 Max: RASS T-Stat
from SEER 10 to SEER 15 | 1992-1998 Max: None
from SEER 10 to SEER 16
from SEER 10 to SEER 17 | 1978-1992 Min: Improvement from SEER 10 to SEER 13
from SEER 10 to SEER 18
from SEER 13 to SEER 14
from SEER 13 to SEER 15
from SEER 13 to SEER 16
from SEER 13 to SEER 17
from SEER 13 to SEER 18

## Calibration Tables
Tables used to adjust simulated cooling and heating energy use.
Table 1. DEER 2001 UEC-based Calibration factors (translated from forecasting CZs) | [10 empty] | Table 4. Average Household Size by Vintage and Region
| Cooling Calibration Factor |  |  |  |  | Heating Calibration Factor | [5 empty] | Average Floor Area per Household
T24-CZ | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | weighted | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | weighted | Region | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998
CZ01 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.84694 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.82038 | North Coast | 1591 | 1904 | 2164 | 2295.6102
CZ02 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85769 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.87023 | South Coast | 1528 | 2064 | 2270 | 2392.9091
CZ03 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.81885 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.85181 | South Inland | 1636 | 1811 | 2118 | 2422.9286
CZ04 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.8293 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.85471 | Central Valley | 1528 | 1704 | 2056 | 1948.7812
CZ05 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.88389 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.83949 | Desert | 1555 | 1741 | 1643 | 2160.9167
CZ06 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 0.97234 | 1 | 0.975 | 0.975 | 0.975 | 0.99077
CZ07 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 0.96204 | 1 | 0.975 | 0.975 | 0.975 | 0.98661
CZ08 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 0.98346 | 1 | 0.975 | 0.975 | 0.975 | 0.99136 | Table 5. Average number of Stories by Vintage and Region
CZ09 | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 0.80484 | 1 | 1 | 1 | 1 | 1 |  | Average number of Stories
CZ10 | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 0.74347 | 1 | 1 | 1 | 1 | 1 | Region | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998
CZ11 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.60612 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | North Coast | 1.4844 | 1.307 | 1.7 | 1.7
CZ12 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.61136 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | South Coast | 1.5494 | 1.6219 | 1.8 | 1.8
CZ13 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.60388 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | South Inland | 1.3259 | 1.4231 | 1.8 | 1.8
CZ14 | 0.61506 | 0.59885 | 0.5 | 0.5 | 0.58475 | 1 | 1 | 1 | 1 | 1 | Central Valley | 1.2562 | 1.2296 | 1.4 | 1.4
CZ15 | 0.61506 | 0.59885 | 0.5 | 0.5 | 0.58532 | 1 | 1 | 1 | 1 | 1 | Desert | 1.0811 | 1.1188 | 1.2 | 1.2
CZ16 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.86407 | 0.85 | 0.95 | 0.68333 | 0.68333 | 0.8736
Table 6. Average Cooling Capacity by Vintage and Region
Table 2. Calibration Factors derived from RASS Thermostat Data | [11 empty] | Cooling Tons per Household
| Cooling Calibration Factor |  |  |  |  | Heating Calibration Factor |  |  |  |  | Region | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998
T24-CZ | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | weighted | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | weighted | North Coast | 3.711 | 3.2676 | 3.9 | 3.9
CZ01 | 1 | 1 | 1 | 1 | 1 | 0.55203 | 0.55339 | 0.5428 | 0.54982 | 0.55098 | South Coast | 3.0988 | 2.9329 | 3.2 | 3.2
CZ02 | 1.1318 | 1.3142 | 1.1158 | 1.1326 | 1.2075 | 0.54941 | 0.55579 | 0.54717 | 0.5545 | 0.55159 | South Inland | 3.9888 | 3.5578 | 4.5 | 4.6
CZ03 | 1.8759 | 2 | 1.68 | 1.7299 | 1.8622 | 0.5262 | 0.53431 | 0.52944 | 0.54186 | 0.52826 | Central Valley | 3.8843 | 3.4592 | 4.1 | 3.8
CZ04 | 1.279 | 1.5847 | 1.2176 | 1.2361 | 1.336 | 0.53002 | 0.53705 | 0.53027 | 0.54124 | 0.53189 | Desert | 5 | 4.1188 | 3.8 | 4.6
CZ05 | 1.9746 | 2 | 1.6473 | 1.6845 | 1.9632 | 0.50881 | 0.51364 | 0.51267 | 0.53234 | 0.5115
CZ06 | 1.3536 | 1.7591 | 1.277 | 1.3106 | 1.4646 | 0.56477 | 0.66265 | 0.78452 | 0.91184 | 0.63411
CZ07 | 1.2131 | 1.4791 | 1.1802 | 1.2081 | 1.2845 | 0.57929 | 0.73122 | 0.89723 | 1.065 | 0.70084
CZ08 | 1.024 | 1.168 | 1.0122 | 1.0398 | 1.0667 | 0.56809 | 0.66413 | 0.72883 | 0.80906 | 0.61361
CZ09 | 1.0644 | 1.0563 | 1.0221 | 1.0322 | 1.0581 | 0.78922 | 0.93042 | 1.0694 | 1.217 | 0.8448
CZ10 | 0.99904 | 0.99969 | 0.98249 | 0.9944 | 0.9968 | 0.76668 | 0.85217 | 0.93362 | 1.0353 | 0.85717
CZ11 | 1.0359 | 1.0274 | 1.0659 | 1.0766 | 1.0417 | 0.75343 | 0.76253 | 0.79082 | 0.79673 | 0.76696
CZ12 | 1.0892 | 1.0813 | 1.1367 | 1.1547 | 1.0979 | 0.75476 | 0.76291 | 0.79121 | 0.79815 | 0.76456
CZ13 | 0.98795 | 0.98059 | 1.0054 | 1.0142 | 0.99074 | 0.76125 | 0.77388 | 0.80518 | 0.81401 | 0.77578
CZ14 | 0.99682 | 1.0178 | 1.0396 | 1.0382 | 1.0193 | 0.76729 | 0.78064 | 0.81016 | 0.83188 | 0.78282
CZ15 | 0.93239 | 0.93914 | 0.95304 | 0.95128 | 0.93956 | 0.83138 | 1.1153 | 2 | 2 | 1.1949
CZ16 | 1.2041 | 1.4412 | 1.1813 | 1.2031 | 1.2824 | 0.56846 | 0.58946 | 0.56483 | 0.58457 | 0.57712
Table 3. Vintage Weighting values from the RASS Thermostat study:
| Cooling Weights |  |  |  | Heating Weights
Wth File | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998
1 | 1 | 0 | 0 | 0 | 0.51086 | 0.19466 | 0.094461 | 0.20002
2 | 0.38461 | 0.4232 | 0.097699 | 0.094488 | 0.59165 | 0.3311 | 0.045098 | 0.032153
3 | 0.36992 | 0.33195 | 0.22729 | 0.070842 | 0.72089 | 0.18123 | 0.075913 | 0.021966
4 | 0.58528 | 0.21826 | 0.068364 | 0.1281 | 0.73575 | 0.18282 | 0.0303 | 0.051126
5 | 0.53336 | 0.3973 | 0.035865 | 0.033477 | 0.60192 | 0.2094 | 0.14074 | 0.047944
6 | 0.44529 | 0.30764 | 0.093307 | 0.15377 | 0.63085 | 0.19542 | 0.079246 | 0.094485
7 | 0.38433 | 0.30005 | 0.24363 | 0.07199 | 0.46432 | 0.35655 | 0.117 | 0.062122
8 | 0.53419 | 0.29756 | 0.10397 | 0.064275 | 0.65445 | 0.22229 | 0.068943 | 0.054316
9 | 0.63321 | 0.26133 | 0.075547 | 0.029914 | 0.70909 | 0.20698 | 0.064666 | 0.019257
10 | 0.24895 | 0.4903 | 0.1135 | 0.14725 | 0.31515 | 0.45209 | 0.10507 | 0.12769
11 | 0.38987 | 0.35714 | 0.13547 | 0.11752 | 0.36057 | 0.39051 | 0.136 | 0.11292
12 | 0.42772 | 0.3637 | 0.11492 | 0.093659 | 0.48841 | 0.33266 | 0.097051 | 0.081877
13 | 0.37598 | 0.35679 | 0.18238 | 0.084856 | 0.45759 | 0.31842 | 0.14806 | 0.07593
14 | 0.09011 | 0.75248 | 0.11994 | 0.037469 | 0.17004 | 0.7053 | 0.089048 | 0.03561
15 | 0.31525 | 0.49623 | 0.14634 | 0.042177 | 0.31169 | 0.49832 | 0.14857 | 0.041411
16 | 0.54164 | 0.34087 | 0.10803 | 0.00946 | 0.46631 | 0.42205 | 0.10173 | 0.009914

## AC-HP Unit Data
Detailed AC and HP Unit Performance Data
The performance of all the units examined were distilled down to 99 units, identified by the slope of the EER curve and the value of the
cycling degradation coefficient or the manufacturer. The table below (starting at row 52) contains the data used to simulate the units
examined in this study.
Data Key:
Columns B through H are unit descriptors and are not uses as DOE-2 input fields.
| Column(s) | Usage
| B. | Evaporator configuration. Split-R indicates split-system residential units.
| C. | Type of cooling unit -- AC is air conditioner and HP is heat pump.
| D. | Nominal SEER rating
| E. | Sensitivity of units' EER to temperature. Values are Low, Median, and High.
| F. | Unit cycling degradation coefficient description. Values are Low, Median, and High.
| G. | Unit's rated EER.
| H. | Actual unit total capacity. Value is for reference only and not used in simulations.
Colums I through BK are used as DOE-2 simulation inputs. Fields are used as follows:
| I. | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load.
COOL-SH-CAP = COOLING-CAPACITY * Sen/Total
| J. | Value is DOE-2 keyword COOLING-EIR
| K. | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity.
| L. | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords:
SUPPLY-KW = (Fan W/cfm)/1,000
SUPPLY-DELTA-T = (Fan W/cfm)* 3.160
| M. | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF
| N. | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor load.
| O. | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
| P thru U | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT
| V thru AA | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT
| AB Thru AG | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT
| AH thru AM | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT
| AN thru AQ | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in temperate climate zones
| AR thru AU | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in moderate climate zones
| AV thru AY | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in hot climate zones
| AZ thru BB | The coefficients for the quadratic equation of the C-LOSS curve for houses in temperate climate zones
| BC thru BE | The coefficients for the quadratic equation of the C-LOSS curve for houses in moderate climate zones
| BF thru BH | The coefficients for the quadratic equation of the C-LOSS curve for houses in hot climate zones
| BI | Number of compressor speeds (1 or 2). This is used as a flag to notify simulation when 2-speed equipment is to be simulated
| BJ | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO
| BK | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES
Columns BL through CA are for heat pumps only. Colums BL and BN are descriptive only and not used in simulations
| BL | For heat pumps only - rated HSPF
| BM | For heat pumps only - rated COP at 47 outdoor temperature. Keyword HEATING-EIR = 1/(COP at 47 ODB)
| BN | For heat pumps only - Actual unit rated heating capacity. Value is for reference only and not used in simulations.
| BO | Heating EIR from manufacturers expanded ratings chart. Used only as a check with the rated COP at 47 ODB.
| BP thru BU | For heat pumps only - the coefficients of the bi-quadratic heating capacity off-design curve set by keyword HEAT-CAP-FT
| BV thru CA | For heat pumps only - the coefficients of the bi-quadratic heating EIR off-design curve set by keyword HEAT-EIR-FT
Columns CB through CE are needed for two-speed units only
| CB & CC | The coefficients C0 and C1 of the linear curve-fit command assigned to keyword COIL-BF-FFLOW
| CD thru CE | The min and max values used in the same curve-fit command referenced above.
ID | Evap Config | Cool Type | SEER | EER Slope | CD or Man | EER | Tot Cap | Sen/Total | EIR | cfm/Btuh | Fan W/cfm | Coil-BF | Crnk/Tot kW | Crnk Off | Total Capacity Curve Fit Coefficients | [5 empty] | Sensible Capacity Curve Fit Coefficients | [5 empty] | EIR Curve Fit Coefficients | [5 empty] | Coil-BF Curve Fit Coefficients | [5 empty] | Temperate EIR_PLR Curve Fit Coefficients |  |  |  | Moderate EIR_PLR Curve Fit Coefficients |  |  |  | Hot EIR_PLR Curve Fit Coefficients |  |  |  | Temp C-Loss Curve Fit Coefficients |  |  | Mod C-Loss Curve Fit Coefficients |  |  | Hot C-Loss Curve Fit Coefficients |  |  | Cmp Spd | Low Speed Ratios |  | HSPF | COP47 | Heat Cap | H-EIR | Total Capacity Curve Fit Coefficients | [5 empty] | HIR Curve Fit Coefficients | [5 empty] | BF-FFLOW Curve Coeffients
SA-10-LL | Split-R | AC | 10 | Low | Low | 8.87 | 23397 | 0.735 | 0.32576 | 0.03419 | 0.365 | 0.2127 | 0 | 100 | 2.1366 | -0.049513 | 0.00060311 | 0.0051714 | -6.3929e-06 | -0.00015086 | -1.6066 | 0.14422 | -0.001486 | -0.017898 | -2.381e-08 | 0.00020662 | -0.20834 | 0.029968 | -0.00027444 | -0.00042858 | 6.7994e-05 | -2.2073e-05 | 45.2564 | -1.2384 | 0.0076048 | -0.047037 | -0.00058972 | 0.0022607 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-LM | Split-R | AC | 10 | Low | Median | 9.29 | 30000 | 0.7667 | 0.30336 | 0.0375 | 0.365 | 0.2206 | 0 | 100 | 1.1609 | -0.028145 | 0.0004005 | 0.0095336 | -4.7167e-05 | -8.69e-05 | 0.5179 | 0.055771 | -0.000739 | -0.0031257 | -3.9833e-05 | 0.000113 | 0.44422 | 0.00787 | -4e-05 | 0.0012025 | 9.3333e-05 | -0.0001176 | 2.3345 | -0.084691 | 0 | 0.055522 | 0 | -1.9029e-05 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-LH | Split-R | AC | 10 | Low | High | 9.51 | 24120 | 0.7803 | 0.2959 | 0.03731 | 0.365 | 0.1888 | 0 | 100 | 1.1473 | -0.028911 | 0.000414 | 0.010872 | -5.1667e-05 | -9.98e-05 | 0.36475 | 0.061711 | -0.000849 | -0.0046315 | -6.65e-05 | 0.0002124 | 0.83534 | 0.0017305 | -9.5e-06 | -0.002555 | 0.000111 | -0.0001049 | 1.4085 | -0.10207 | 0 | 0.093466 | 0 | -0.00019531 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-ML | Split-R | AC | 10 | Median | Low | 8.77 | 17947 | 0.7103 | 0.3311 | 0.03343 | 0.365 | 0.2537 | 0 | 100 | 1.8143 | -0.040224 | 0.00054456 | 0.0049525 | -4.5833e-06 | -0.000156 | -0.41194 | 0.10962 | -0.0012322 | -0.01885 | -1.1548e-06 | 0.00021991 | -0.055224 | 0.024173 | -0.00023156 | 0.00045781 | 7.3988e-05 | -3.7102e-05 | 42.2422 | -0.83363 | 0.0045517 | -0.29513 | 0.00078486 | 0.0023815 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-MM | Split-R | AC | 10 | Median | Median | 9.08 | 35495 | 0.7662 | 0.31786 | 0.03381 | 0.365 | 0.1319 | 0 | 100 | -0.58806 | 0.032113 | 3.0888e-06 | 0.0044513 | 4.5818e-07 | -0.0001578 | 5.3907 | -0.061339 | -8.2689e-07 | -0.017483 | -9.6288e-06 | 0.00023103 | 0.6212 | 0.00017973 | -9.9627e-06 | 0.0021263 | 7.9472e-05 | -7.9771e-05 | 23.4123 | -1.2782 | 0.011002 | 0.44797 | -0.0010572 | -0.0028415 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-MH | Split-R | AC | 10 | Median | High | 9.83 | 18840 | 0.7612 | 0.2869 | 0.03583 | 0.365 | 0.1961 | 0 | 100 | 1.2756 | -0.034465 | 0.0004505 | 0.010942 | -5.7583e-05 | -7.99e-05 | 0.65755 | 0.047882 | -0.000663 | -0.00048887 | -4.65e-05 | 9.06e-05 | 0.34873 | 0.010851 | -6.45e-05 | 0.0025882 | 9.85e-05 | -0.0001447 | 2.4424 | -0.09701 | 0 | 0.065452 | 0 | -3.339e-05 | 0.00021601 | 1.2854 | -0.39389 | 0.10824 | 0.00031399 | 1.3209 | -0.45319 | 0.13194 | 0.00042614 | 1.3532 | -0.5084 | 0.15482 | 0.76597 | 0.28782 | -0.054621 | 0.74134 | 0.32421 | -0.06666 | 0.71951 | 0.3574 | -0.078308 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-HL | Split-R | AC | 10 | High | Low | 8.46 | 47993 | 0.7229 | 0.34522 | 0.03334 | 0.365 | 0.2213 | 0 | 100 | 1.8334 | -0.040389 | 0.00050267 | 0.0045755 | -8.1905e-06 | -0.00011698 | -1.1685 | 0.12379 | -0.0013098 | -0.013198 | -6.5238e-06 | 0.00016766 | -0.59695 | 0.038944 | -0.00029044 | -0.0024521 | 0.0001425 | -0.00011966 | 43.1842 | -1.1029 | 0.0062778 | -0.1057 | -0.00049098 | 0.0028219 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-HM | Split-R | AC | 10 | High | Median | 8.79 | 48893 | 0.7239 | 0.33153 | 0.03272 | 0.365 | 0.2154 | 0 | 100 | 1.8967 | -0.043158 | 0.00052567 | 0.0048137 | -8.5833e-06 | -0.000117 | -1.2607 | 0.12654 | -0.0013233 | -0.013335 | -2.25e-06 | 0.00015866 | -0.36023 | 0.034808 | -0.00027133 | -0.0029425 | 0.00012808 | -9.9029e-05 | 40.0949 | -1.4017 | 0.0051578 | 0.22572 | -0.0048275 | 0.0083024 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-10-HH | Split-R | AC | 10 | High | High | 9.17 | 59742.341 | 0.6703 | 0.32083 | 0.03013 | 0.365 | 0.2947 | 0 | 100 | 0.03889 | 0.0099102 | 0.00013398 | 0.0066983 | -1.2104e-05 | -0.00013062 | 2.4229 | 0.0064884 | -0.00036504 | -0.0016293 | -1.1562e-06 | -8.4375e-06 | 1.1153 | -0.0028376 | -1.6602e-05 | -0.0081661 | 0.0001327 | -4.2813e-05 | 18.0124 | -0.40743 | 0.0048155 | -0.10279 | 0.001541 | -0.0024198 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-LL | Split-R | AC | 13 | Low | Low | 11.36 | 43994.894 | 0.7022 | 0.2562 | 0.02728 | 0.365 | 0.1226 | 0 | 55 | 1.1675 | -0.024899 | 0.00035684 | 0.0054285 | -2.4052e-05 | -6.2812e-05 | 0.33332 | 0.066177 | -0.00080937 | -0.002306 | -4.6667e-06 | 2e-05 | -0.10321 | 0.026928 | -0.00018477 | -0.0007664 | 0.00013867 | -0.000165 | 57.5279 | -1.2249 | 0.0091779 | -0.44581 | 0.003236 | -0.00013194 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-LM | Split-R | AC | 13 | Low | Median | 12.04 | 49930 | 0.7416 | 0.23394 | 0.03104 | 0.365 | 0.1211 | 0 | 55 | 1.058 | -0.022649 | 0.000341 | 0.0058047 | -3.5e-05 | -4.82e-05 | 2.2518 | -0.0066825 | -0.0002025 | 0.0041301 | -3.375e-05 | 2.7e-06 | 0.97322 | -0.0023395 | 0.0001155 | -0.001479 | 0.00018517 | -0.0002931 | 2.976 | -0.12205 | 0 | 0.10297 | 0 | -0.00037985 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-LH | Split-R | AC | 13 | Low | High | 12.5 | 26120 | 0.7703 | 0.2184 | 0.03445 | 0.365 | 0.1437 | 0 | 55 | 2.0708 | -0.064319 | 0.000671 | 0.012967 | -5.4417e-05 | -8.08e-05 | 1.1698 | 0.013783 | -0.0003475 | 0.011487 | -6.2083e-05 | -1.01e-05 | -0.75939 | 0.051959 | -0.000331 | -0.0021968 | 0.00016525 | -0.0002386 | 2.0091 | -0.10624 | 0 | 0.098615 | 0 | -0.0003321 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-ML | Split-R | AC | 13 | Median | Low | 11.09 | 44700 | 0.75 | 0.25674 | 0.03132 | 0.364 | 0.1148 | 0 | 55 | 1.1914 | -0.01965 | 0.00031563 | 0.0030587 | -9.3333e-06 | -7.825e-05 | 2.9212 | -0.0010016 | -0.00032734 | -0.0068234 | 1.6417e-05 | 1.8125e-05 | -0.068189 | 0.022284 | -0.00011719 | 0.0010593 | 0.00014817 | -0.00021 | -39.997 | 0.31043 | 0.0012794 | 0.76281 | -0.0019955 | -0.0063058 | 1.5738e-06 | 1.0607 | -0.067322 | 0.006596 | 5.2912e-06 | 1.0891 | -0.10267 | 0.013563 | 1.2001e-05 | 1.1153 | -0.13713 | 0.021822 | 0.94256 | 0.060678 | -0.0032424 | 0.91762 | 0.088968 | -0.0066159 | 0.89551 | 0.11501 | -0.01057 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-MM | Split-R | AC | 13 | Median | Median | 11.3 | 43544.043 | 0.729 | 0.25 | 0.03215 | 0.365 | 0.1888 | 0 | 55 | 3.5009 | -0.090336 | 0.00087051 | 0.0029382 | 3.6458e-07 | -0.00010031 | 0.48245 | 0.069346 | -0.00084785 | -0.0073919 | 1.451e-05 | 3.9062e-05 | -2.9365 | 0.10373 | -0.00079922 | 0.0030636 | 0.00010629 | -0.00010625 | 63.2163 | -1.3448 | 0.0055112 | -0.4917 | 0.00056485 | 0.0072514 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-MH | Split-R | AC | 13 | Median | High | 11.72 | 30545.745 | 0.7381 | 0.2386 | 0.03274 | 0.365 | 0.1815 | 0 | 55 | 3.0075 | -0.070888 | 0.00070215 | -0.00081068 | 6.0937e-06 | -6.0937e-05 | -2.6484 | 0.16813 | -0.0016205 | -0.010065 | 1.8948e-05 | 6.9687e-05 | -3.0666 | 0.087898 | -0.00057734 | 0.019142 | 8.1646e-05 | -0.00028062 | 57.1344 | -0.80664 | 0.0083139 | -0.78771 | 0.0071905 | -0.0041815 | 6.0394e-05 | 1.1914 | -0.24571 | 0.054241 | 0.00010034 | 1.2244 | -0.29617 | 0.071638 | 0.00014998 | 1.2546 | -0.34377 | 0.089044 | 0.83477 | 0.19221 | -0.027284 | 0.80995 | 0.22567 | -0.036074 | 0.78794 | 0.25632 | -0.044885 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-HL | Split-R | AC | 13 | High | Low | 10.74 | 43400 | 0.77 | 0.2752 | 0.03283 | 0.288 | 0.1087 | 0 | 55 | 1.3186 | -0.025167 | 0.00037734 | 0.0061013 | -1.725e-05 | -0.00011788 | 3.0045 | 0.0047656 | -0.00047969 | -0.012061 | -9e-06 | 0.000166 | 0.35078 | 0.025947 | -0.00016406 | -0.012954 | 0.00021875 | -0.00017225 | -9.1849 | -0.24568 | 0.0079909 | 0.46534 | 0.0017032 | -0.0107 | 7.1792e-07 | 1.0473 | -0.051396 | 0.0040952 | 3.0792e-06 | 1.0751 | -0.084968 | 0.0098542 | 7.8289e-06 | 1.1008 | -0.11786 | 0.017048 | 0.95473 | 0.047315 | -0.0020505 | 0.92975 | 0.075168 | -0.0049383 | 0.90755 | 0.10094 | -0.0085501 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-HM | Split-R | AC | 13 | High | Median | 10.98 | 62102 | 0.7693 | 0.2634 | 0.0322 | 0.329 | 0.0813 | 0 | 100 | 2.389 | -0.060045 | 0.000656 | 0.0091894 | -2.7101e-05 | -0.00014756 | -1.546 | 0.13361 | -0.0013876 | -0.013416 | -1.8685e-05 | 0.00019886 | -1.242 | 0.07635 | -0.00060556 | -0.015157 | 0.00019547 | -7.5314e-05 | 96.0292 | -3.5738 | 0.0161 | 0.62464 | -0.0089535 | 0.014827 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-13-HH | Split-R | AC | 13 | High | High | 11.35 | 41570 | 0.7643 | 0.2515 | 0.03368 | 0.329 | 0.1329 | 0 | 100 | 1.8327 | -0.044845 | 0.00050533 | 0.0093478 | -4.3107e-05 | -9.3559e-05 | -4.1057 | 0.213 | -0.002043 | -0.013024 | -3.1304e-05 | 0.00023969 | -1.2152 | 0.079179 | -0.00057567 | -0.017619 | 0.00023964 | -0.00015625 | 43.9436 | -2.4671 | 0.018721 | 0.94478 | -0.004946 | -0.0010474 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-ML | Split-R | AC | 14 | Median | Low | 12.15 | 36500 | 0.78 | 0.22932 | 0.03288 | 0.383 | 0.0866 | 0 | 100 | 1.631 | -0.03418 | 0.00042734 | 0.003849 | -1.15e-05 | -8.1875e-05 | 1.0575 | 0.055406 | -0.00080938 | -0.0077255 | -7.5e-06 | 0.0001045 | -0.67296 | 0.044013 | -0.000275 | 0.00034433 | 0.00016317 | -0.000243 | -56.2904 | 0.38216 | 0.0057104 | 1.1079 | -0.00016624 | -0.015208 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-MM | Split-R | AC | 14 | Median | Median | 13.08 | 37680 | 0.7478 | 0.22503 | 0.03185 | 0.263 | 0.1282 | 0 | 100 | 0.70697 | -0.007713 | 0.000132 | 0.0030629 | -6.4167e-05 | 7.94e-05 | 1.0885 | 0.027737 | -0.000533 | 0.0039964 | -6.8e-05 | 0.0001068 | 0.79053 | -0.0097785 | 0.0002915 | 0.0078246 | 0.00020042 | -0.0004707 | 1.1154 | -0.091274 | 0 | 0.11423 | 0 | -0.00058558 | 4.9876e-05 | 1.1803 | -0.22911 | 0.048793 | 8.486e-05 | 1.2129 | -0.27841 | 0.065382 | 0.00012897 | 1.2428 | -0.32502 | 0.082084 | 0.84333 | 0.18094 | -0.024534 | 0.81849 | 0.21402 | -0.032911 | 0.79646 | 0.24434 | -0.04136 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-MH | Split-R | AC | 14 | Median | High | 13.22 | 41520 | 0.711 | 0.22709 | 0.0301 | 0.24 | 0.1744 | 0 | 100 | 0.80636 | -0.018401 | 0.000349 | 0.0074827 | -2.8e-05 | -9.4e-05 | 1.8938 | -0.0014855 | -0.0001855 | 0.0064776 | -2.8167e-05 | -5.07e-05 | 1.1105 | -0.006073 | 0.000117 | -0.00062367 | 0.00017233 | -0.000271 | 1.983 | -0.084043 | 0 | 0.073734 | 0 | -0.00023337 | 7.2478e-05 | 1.2027 | -0.26271 | 0.059969 | 0.00011782 | 1.236 | -0.31431 | 0.078168 | 0.00017345 | 1.2665 | -0.3629 | 0.096274 | 0.82622 | 0.20361 | -0.030176 | 0.80141 | 0.23745 | -0.039377 | 0.77942 | 0.26843 | -0.048548 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-HL | Split-R | AC | 14 | High | Low | 11.7 | 31167.925 | 0.7722 | 0.25992 | 0.03208 | 0.225 | 0.0826 | 0 | 100 | 2.9298 | -0.073729 | 0.0007663 | 0.0041592 | -1.8617e-06 | -0.00012698 | -4.2897 | 0.21439 | -0.0020881 | -0.0057032 | -4.9151e-05 | 0.00020182 | -1.7975 | 0.087146 | -0.00078912 | -0.0078009 | 0.00012471 | 1.8319e-05 | 90.3078 | -1.963 | 0.029663 | -0.65674 | 0.015862 | -0.026105 | 1.5758e-06 | 1.0607 | -0.067351 | 0.006601 | 5.2959e-06 | 1.0891 | -0.10271 | 0.01357 | 1.2009e-05 | 1.1153 | -0.13716 | 0.021831 | 0.94251 | 0.06078 | -0.0033065 | 0.91754 | 0.089226 | -0.0068034 | 0.89536 | 0.11552 | -0.010954 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-HM | Split-R | AC | 14 | High | Median | 11.84 | 29100 | 0.79 | 0.23689 | 0.03436 | 0.345 | 0.104 | 0 | 100 | 1.8979 | -0.041081 | 0.00050938 | 0.0029553 | 2.8333e-06 | -0.000116 | 0.52066 | 0.072658 | -0.00094453 | -0.0094176 | -5.4167e-06 | 0.00012487 | -0.7592 | 0.037092 | -0.00026797 | 0.0073089 | 0.00011458 | -0.00019663 | 13.4021 | -0.59777 | 0.013199 | 0.19292 | 0.0053696 | -0.015187 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-14-HH | Split-R | AC | 14 | High | High | 12.17 | 25300 | 0.75 | 0.24507 | 0.03162 | 0.306 | 0.1232 | 0 | 100 | 1.3696 | -0.02588 | 0.00040234 | 0.0026539 | 3.25e-06 | -0.00011363 | 1.7984 | 0.022356 | -0.00047188 | -0.0010312 | -3.5833e-06 | -7.5e-06 | -1.1928 | 0.048469 | -0.00035313 | 0.009335 | 0.00010933 | -0.000211 | -10.0124 | -0.12326 | 0.0012043 | 0.37445 | -0.0018415 | -0.00080331 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-ML | Split-R | AC | 15 | Median | Low | 12.72 | 45047.791 | 0.7025 | 0.2389 | 0.02664 | 0.256 | 0.1007 | 0 | 55 | 1.612 | -0.034129 | 0.00044551 | 0.0027867 | -2.1146e-06 | -8.9687e-05 | 0.42252 | 0.073602 | -0.00089453 | -0.0084029 | 1.6146e-05 | 4.9375e-05 | -0.68032 | 0.034102 | -0.0002502 | 0.0055919 | 0.00010461 | -0.00015031 | 97.5679 | -1.803 | 0.012457 | -1.0113 | 0.006252 | 0.0017172 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-MM | Split-R | AC | 15 | Median | Median | 12.99 | 36100 | 0.78 | 0.2297 | 0.03324 | 0.233 | 0.0966 | 0 | 100 | 1.7038 | -0.037103 | 0.00045469 | 0.0041866 | -1.1583e-05 | -8.675e-05 | 2.7021 | -0.0057594 | -0.00031094 | -0.00016333 | -2.825e-05 | 5.5e-05 | -0.85172 | 0.049228 | -0.00030469 | 0.0008295 | 0.00016767 | -0.0002625 | 17.3372 | 0.10011 | 0.0058611 | -0.47841 | 0.0080575 | -0.011689 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-MH | Split-R | AC | 15 | Median | High | 13.11 | 29600 | 0.79 | 0.23488 | 0.03378 | 0.19 | 0.0886 | 0 | 100 | 1.5132 | -0.028142 | 0.00042109 | 0.0019705 | 1.1167e-05 | -0.00012663 | 2.1808 | 0.020644 | -0.0005625 | -0.0073817 | -1.9e-05 | 0.000131 | -0.46971 | 0.021738 | -0.00014063 | 0.011561 | 9.7833e-05 | -0.00021 | 14.3529 | 0.16281 | 0.0027522 | -0.45449 | 0.006411 | -0.0077029 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-HL | Split-R | AC | 15 | High | Low | 12.39 | 51934.1453 | 0.7766 | 0.2328 | 0.03081 | 0.318 | 0.0336 | 0 | 55 | 3.7471 | -0.099512 | 0.00095195 | 0.005716 | -9.8125e-06 | -0.00012687 | -6.1903 | 0.27495 | -0.0025369 | -0.0085626 | -3.4656e-05 | 0.00020156 | -3.6661 | 0.12222 | -0.00089687 | 0.0045344 | 0.00013588 | -0.00018125 | 301.6633 | -5.0926 | 0.079056 | -3.5078 | 0.054289 | -0.071113 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-HM | Split-R | AC | 15 | High | Median | 13.01 | 30874 | 0.7636 | 0.2267 | 0.03239 | 0.256 | 0.1001 | 0 | 100 | 1.8768 | -0.038132 | 0.00048922 | 0.0067273 | -8.8869e-06 | -0.0001692 | -2.6365 | 0.17652 | -0.0017579 | -0.016188 | -7.0536e-06 | 0.00020456 | -0.55408 | 0.059005 | -0.00051111 | -0.018903 | 0.00019695 | -1.3608e-05 | 39.0509 | -3.5216 | 0.023336 | 1.9039 | -0.012782 | 0.0042222 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.9561e-05 | 1.1799 | -0.22858 | 0.048622 | 7.9822e-05 | 1.2089 | -0.27221 | 0.063229 | 0.86849 | 0.14864 | -0.017294 | 0.84361 | 0.18058 | -0.024448 | 0.82153 | 0.20992 | -0.031823 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-15-HH | Split-R | AC | 15 | High | High | 12.85 | 23967 | 0.7819 | 0.2288 | 0.03338 | 0.255 | 0.0847 | 0 | 100 | 2.9829 | -0.076834 | 0.00078589 | 0.007719 | -2.2036e-05 | -0.00014098 | -2.137 | 0.15234 | -0.0015286 | -0.014449 | -1.5113e-05 | 0.00020436 | -2.2648 | 0.10387 | -0.00080911 | -0.014056 | 0.00021446 | -0.00010408 | 84.3049 | -3.6612 | 0.018089 | 0.97877 | -0.010325 | 0.012794 | 6.0394e-05 | 1.1914 | -0.24571 | 0.054241 | 0.00010034 | 1.2244 | -0.29617 | 0.071638 | 0.00014998 | 1.2546 | -0.34377 | 0.089044 | 0.83477 | 0.19221 | -0.027284 | 0.80995 | 0.22567 | -0.036074 | 0.78794 | 0.25632 | -0.044885 | 1 | 1 | 1 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 1 | 0 | 0 | 1
SA-16-CL | Split-TS | AC | 16 | Low | Carrier | 11.74 | 36720.291 | 0.7718 | 0.2539 | 0.03268 | 0.256 | 0.0886 | 0 | 125 | 4.052 | -0.10535 | 0.0010484 | 0.0062599 | -8.2649e-06 | -0.00019164 | -3.7388 | 0.20718 | -0.0019624 | -0.01929 | -1.2872e-05 | 0.00025384 | -2.6536 | 0.11873 | -0.00099967 | -0.013031 | 0.00015455 | 4.5918e-06 | 75.8019 | -3.3222 | 0.016741 | 0.90512 | -0.0090922 | 0.010898 | 0.018637 | 1.2239 | -1.1229 | 0.88034 | 0.018664 | 1.2489 | -1.1555 | 0.88798 | 0.018695 | 1.2717 | -1.1865 | 0.8962 | 0.94183 | 0.058167 | 1e-08 | 0.94487 | 0.055126 | 1e-08 | 0.93106 | 0.068939 | 1e-08 | 2 | 0.66667 | 0.50993 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 10.9813 | -9.9813 | 1 | 4.3271
SA-16-CM | Split-TS | AC | 16 | Median | Carrier | 11.86 | 37095.791 | 0.7717 | 0.2513 | 0.03235 | 0.256 | 0.0795 | 0 | 125 | 4.2699 | -0.11178 | 0.0011223 | 0.0058889 | 1.7143e-06 | -0.00021892 | -3.7353 | 0.20707 | -0.0019615 | -0.019293 | -1.2842e-05 | 0.00025383 | -2.7579 | 0.1217 | -0.0010342 | -0.01279 | 0.00014946 | 1.7651e-05 | 94.4335 | -3.676 | 0.019772 | 0.73261 | -0.0075505 | 0.01004 | 0.012855 | 1.1827 | -0.82527 | 0.62975 | 0.012883 | 1.2089 | -0.85952 | 0.63776 | 0.012916 | 1.2329 | -0.89216 | 0.64639 | 0.94361 | 0.056389 | 1e-08 | 0.94733 | 0.052675 | 1e-08 | 0.93405 | 0.065954 | 1e-08 | 2 | 0.66667 | 0.48479 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 13.3848 | -12.3848 | 1 | 5.1283
SA-16-CH | Split-TS | AC | 16 | High | Carrier | 12.08 | 35996.6667 | 0.7465 | 0.2483 | 0.02977 | 0.255 | 0.0654 | 0 | 125 | 3.7971 | -0.097888 | 0.0010122 | 0.004213 | 5.247e-06 | -0.00019326 | -2.6239 | 0.17499 | -0.0016976 | -0.020663 | 3.7024e-06 | 0.00022776 | -2.5692 | 0.10472 | -0.00088628 | -0.0013036 | 8.9101e-05 | -2.3386e-05 | 120.72 | -4.04 | 0.02471 | 0.3686 | -0.0034633 | 0.0061033 | 0.012 | 1.166 | -0.75679 | 0.57876 | 0.020393 | 0.99141 | -0.10366 | 0.014744 | 0.012033 | 1.2162 | -0.82239 | 0.59422 | 0.93922 | 0.06078 | 1e-08 | 0.95114 | 0.048857 | 1e-08 | 0.93785 | 0.062152 | 1e-08 | 2 | 0.6 | 0.49441 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 14.3705 | -13.3705 | 1 | 6.3482
SA-16-LL | Split-TS | AC | 16 | Low | Lennox | 11.61 | 37000 | 0.81 | 0.2527 | 0.03405 | 0.274 | 0.0515 | 0.02 | 55 | -0.060238 | 0.015541 | 9.3437e-05 | 0.0072195 | -1.3738e-05 | -0.00015119 | 1.386 | 0.045014 | -0.00073969 | -0.0092408 | -2.6845e-05 | 0.00016319 | 0.78016 | -0.0048631 | 4.5625e-05 | -0.00042783 | 0.00013845 | -0.00013638 | -2.0538 | -0.69966 | -0.0086129 | 0.69353 | -0.010774 | 0.019042 | -0.0016823 | 1.1464 | -0.36946 | 0.22473 | -0.002039 | 1.1958 | -0.48121 | 0.28746 | -0.0023076 | 1.2396 | -0.58135 | 0.34406 | 0.8967 | 0.1033 | 1e-08 | 0.86176 | 0.13824 | 1e-08 | 0.83071 | 0.16929 | 1e-08 | 2 | 0.71429 | 0.71892 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.5812 | 0.4188 | 0.88034 | 1
SA-16-LM | Split-TS | AC | 16 | Median | Lennox | 12.17 | 50500 | 0.78 | 0.24415 | 0.03228 | 0.258 | 0.0696 | 0.02 | 55 | 0.29802 | 0.0068147 | 0.00011344 | 0.0045177 | -2.1821e-05 | -7.7938e-05 | 2.4124 | -0.00026594 | -0.00029969 | 0.00049472 | -2.2786e-05 | 1.7188e-05 | 1.0729 | -0.0117 | 8.7187e-05 | 3.7057e-05 | 0.00013221 | -0.00013781 | 22.9056 | 0.0046457 | -0.018062 | -0.55313 | -0.0069756 | 0.027567 | -0.00064101 | 1.1385 | -0.22982 | 0.091947 | -0.0010546 | 1.1899 | -0.34688 | 0.15807 | -0.0013697 | 1.2354 | -0.45174 | 0.2177 | 0.90391 | 0.096094 | 1e-08 | 0.86823 | 0.13177 | 1e-08 | 0.83651 | 0.16349 | 1e-08 | 2 | 0.69939 | 0.70891 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.39451 | 0.60549 | 0.81798 | 1
SA-16-LH | Split-TS | AC | 16 | High | Lennox | 12.23 | 37600 | 0.76 | 0.2287 | 0.03191 | 0.367 | 0.1071 | 0.02 | 55 | 0.42903 | -0.00016781 | 0.00021219 | 0.007257 | -1.6964e-05 | -0.00014244 | 3.6373 | -0.035357 | -2.9688e-05 | 0.0015161 | -1.8988e-05 | -1.6937e-05 | 0.69825 | -0.0033959 | 3.7187e-05 | 0.00073416 | 0.00013861 | -0.00015056 | 17.1948 | -0.33141 | -0.012571 | -0.13824 | -0.0085894 | 0.023968 | -0.00091799 | 1.31 | -0.52982 | 0.22074 | -0.0010756 | 1.3585 | -0.64376 | 0.28636 | -0.0011415 | 1.4012 | -0.74524 | 0.34516 | 0.78926 | 0.21074 | 1e-08 | 0.75601 | 0.24399 | 1e-08 | 0.72646 | 0.27354 | 1e-08 | 2 | 0.75 | 0.71277 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.10429 | 0.89571 | 0.77607 | 1
SA-16-NM | Split-TS | AC | 16 | Median | Nordyne | 12.42 | 36910 | 0.7047 | 0.2433 | 0.02844 | 0.255 | 0.1442 | 0 | 55 | 0.90944 | -0.01415 | 0.0003153 | 0.0058039 | -1.6057e-05 | -0.00012305 | 4.9807 | -0.084755 | 0.00035784 | 0.0086154 | -3.5136e-05 | -6.4395e-05 | 0.77771 | -0.00035923 | 3.4419e-05 | -0.0045689 | 0.00013645 | -0.00011085 | 177.8475 | -2.6885 | 0 | -2.2187 | 0 | 0.033727 | 0.022889 | 1.2353 | -1.3378 | 1.0795 | 0.022895 | 1.2587 | -1.3674 | 1.0858 | 0.022905 | 1.2803 | -1.3963 | 1.0931 | 0.95311 | 0.046888 | 1e-08 | 0.93375 | 0.066253 | 1e-08 | 0.91458 | 0.085423 | 1e-08 | 2 | 0.69048 | 0.68976 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.72213 | 0.27787 | 0.91399 | 1
SA-16-TL | Split-TS | AC | 16 | Low | Trane | 11.15 | 47892.848 | 0.7557 | 0.25984 | 0.0355 | 0.292 | 0.2065 | 0 | 55 | 3.2298 | -0.088433 | 0.00090792 | 0.00933 | -1.0265e-05 | -0.00018448 | -1.1615 | 0.14133 | -0.0015565 | -0.020803 | 2.6436e-06 | 0.00025643 | -6.2332 | 0.16851 | -0.0012055 | 0.027828 | 1.0494e-05 | -0.00021743 | 129.054 | -0.52389 | -0.00012299 | -2.9187 | 0.016883 | 0.006165 | -0.0020891 | 0.97845 | -0.32897 | 0.35261 | -0.0020545 | 1.0158 | -0.4315 | 0.41771 | -0.0018548 | 1.0479 | -0.52071 | 0.47468 | 0.85618 | 0.14382 | 1e-08 | 0.8032 | 0.1968 | 1e-08 | 0.75613 | 0.24387 | 1e-08 | 2 | 0.47059 | 0.51276 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.42407 | 0.57593 | 0.71204 | 1
SA-16-TH | Split-TS | AC | 16 | High | Trane | 11.33 | 35847.791 | 0.7657 | 0.2632 | 0.03347 | 0.256 | 0.1356 | 0 | 55 | 1.2932 | -0.031085 | 0.00047896 | 0.0093448 | -1.548e-05 | -0.00017417 | -5.5606 | 0.27693 | -0.0025829 | -0.024284 | 7.7034e-06 | 0.00028882 | -5.4091 | 0.11493 | -0.00057687 | 0.05069 | 3.021e-05 | -0.00059542 | 130.9113 | -0.28421 | 0.0053636 | -3.2022 | 0.024429 | -0.0065512 | -0.00017093 | 1.0169 | -0.48282 | 0.46604 | 0.00050831 | 1.0438 | -0.56209 | 0.51777 | 0.0012805 | 1.0665 | -0.63038 | 0.56264 | 0.72359 | 0.27641 | 1e-08 | 0.6738 | 0.3262 | 1e-08 | 0.62957 | 0.37043 | 1e-08 | 2 | 0.5 | 0.49055 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.53207 | 0.46793 | 0.76604 | 1
SA-17-CL | Split-TS | AC | 17 | Low | Carrier | 12.4 | 35751.184 | 0.7363 | 0.24257 | 0.02937 | 0.255 | 0.08 | 0 | 125 | 3.2655 | -0.085987 | 0.0009245 | 0.0080508 | -1.1327e-05 | -0.00020692 | -2.0277 | 0.15738 | -0.0015827 | -0.020037 | -5.9315e-06 | 0.00024274 | -1.9706 | 0.098556 | -0.00084772 | -0.012219 | 0.00015414 | -9.0388e-06 | 90.2891 | -3.0706 | 0.015173 | 0.32347 | -0.0051004 | 0.010279 | 0.018832 | 1.2102 | -1.1156 | 0.88654 | 0.018822 | 1.2345 | -1.1459 | 0.89262 | 0.03183 | 0.94669 | -0.11644 | 0.018538 | 0.93472 | 0.06528 | 1e-08 | 0.95474 | 0.04526 | 1e-08 | 0.94135 | 0.058652 | 1e-08 | 2 | 0.66667 | 0.50778 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 13.4906 | -12.4906 | 1 | 5.1635
SA-17-CM | Split-TS | AC | 17 | Median | Carrier | 12.47 | 36479.053 | 0.7479 | 0.2402 | 0.03015 | 0.255 | 0.0737 | 0 | 125 | 3.3948 | -0.089412 | 0.00094844 | 0.0078907 | -1.1158e-05 | -0.00020592 | -2.2544 | 0.16477 | -0.0016427 | -0.020343 | -5.9107e-06 | 0.00024744 | -2.0993 | 0.10288 | -0.00088022 | -0.012621 | 0.00015604 | -8.0939e-06 | 100.2521 | -3.5536 | 0.019424 | 0.47605 | -0.0054908 | 0.009086 | 0.015242 | 1.184 | -0.92878 | 0.72954 | 0.015237 | 1.209 | -0.96003 | 0.73582 | 0.025893 | 0.97747 | -0.1202 | 0.019128 | 0.93552 | 0.064483 | 1e-08 | 0.95571 | 0.044287 | 1e-08 | 0.94258 | 0.057424 | 1e-08 | 2 | 0.6 | 0.49589 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 13.5106 | -12.5106 | 1 | 6.0043
SA-17-CH | Split-TS | AC | 17 | High | Carrier | 12.68 | 36117.884 | 0.7362 | 0.23708 | 0.02907 | 0.255 | 0.0707 | 0 | 125 | 3.2671 | -0.086035 | 0.00092483 | 0.0080501 | -1.1354e-05 | -0.00020685 | -2.0267 | 0.15737 | -0.0015828 | -0.02004 | -5.9702e-06 | 0.00024288 | -1.9807 | 0.09881 | -0.0008495 | -0.012199 | 0.0001542 | -9.2592e-06 | 104.2769 | -3.4136 | 0.019183 | 0.25316 | -0.0034905 | 0.0077248 | 0.015301 | 1.1822 | -0.91873 | 0.72126 | 0.015295 | 1.2072 | -0.95005 | 0.72756 | 0.025866 | 0.97836 | -0.12033 | 0.019158 | 0.93486 | 0.065144 | 1e-08 | 0.95475 | 0.045246 | 1e-08 | 0.94137 | 0.058634 | 1e-08 | 2 | 0.66667 | 0.50761 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 15.2831 | -14.2831 | 1 | 5.761
SA-17-LL | Split-TS | AC | 17 | Low | Lennox | 12.28 | 38000 | 0.8 | 0.247 | 0.03513 | 0.202 | 0.102 | 0.02 | 55 | -0.12969 | 0.021743 | 6.25e-06 | 0.0045865 | -1.6488e-05 | -0.00010088 | 2.4465 | 0.01062 | -0.00046281 | -0.006325 | -2.4988e-05 | 0.00011719 | 0.64502 | -0.0066291 | 7.5938e-05 | 0.0032945 | 0.00012519 | -0.00015469 | -1.9512 | 0.048314 | -0.006893 | 0.040911 | -0.0036033 | 0.0094114 | 0.31934 | 0.83931 | 0.81734 | -0.97599 | -0.0021621 | 1.1415 | -0.40846 | 0.26915 | -0.0025171 | 1.187 | -0.51219 | 0.32772 | 0.93459 | 0.06541 | 1e-08 | 0.89757 | 0.10243 | 1e-08 | 0.86467 | 0.13533 | 1e-08 | 2 | 0.67416 | 0.71053 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | -1.1368 | 2.1368 | 0.30374 | 1
SA-17-LM | Split-TS | AC | 17 | Median | Lennox | 12.47 | 37600 | 0.78 | 0.25105 | 0.03205 | 0.162 | 0.0629 | 0.02 | 55 | 0.0034759 | 0.012093 | 0.00010844 | 0.0080883 | -2.3095e-05 | -0.00013519 | 3.1085 | -0.01284 | -0.00026312 | -0.002867 | -2.5036e-05 | 6.775e-05 | 0.61285 | -0.0028816 | 3.8437e-05 | 0.001551 | 0.0001323 | -0.00014669 | 4.4061 | -1.2171 | -0.0037503 | 0.92703 | -0.013112 | 0.019538 | -0.0023212 | 1.0984 | -0.37565 | 0.27953 | -0.002737 | 1.1473 | -0.48589 | 0.3413 | -0.0030633 | 1.1908 | -0.5848 | 0.39711 | 0.92815 | 0.071854 | 1e-08 | 0.89234 | 0.10766 | 1e-08 | 0.86052 | 0.13948 | 1e-08 | 2 | 0.6971 | 0.71277 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | -0.10333 | 1.1033 | 0.6658 | 1
SA-17-LH | Split-TS | AC | 17 | High | Lennox | 12.67 | 36800 | 0.77 | 0.22812 | 0.03261 | 0.292 | 0.1025 | 0.02 | 55 | -0.94099 | 0.045076 | -0.00015063 | 0.0044388 | -1.0881e-05 | -0.00011413 | 2.1508 | 0.01799 | -0.00049594 | -0.0049829 | -1.5048e-05 | 7.5313e-05 | 1.5356 | -0.03418 | 0.00030031 | 0.0046427 | 0.00013373 | -0.00019506 | -16.7867 | 0.15369 | -0.0084188 | 0.31207 | -0.006063 | 0.01103 | -0.0017675 | 1.2285 | -0.50343 | 0.27671 | -0.0020095 | 1.2761 | -0.61269 | 0.33857 | -0.0021679 | 1.3183 | -0.71033 | 0.39421 | 0.84059 | 0.15941 | 1e-08 | 0.80733 | 0.19267 | 1e-08 | 0.77776 | 0.22224 | 1e-08 | 2 | 0.75 | 0.72283 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | -0.36195 | 1.3619 | 0.65951 | 1
SA-17-TL | Split-TS | AC | 17 | Low | Trane | 11.41 | 61342.341 | 0.687 | 0.2517 | 0.02934 | 0.365 | 0.2272 | 0 | 55 | 1.8251 | -0.046541 | 0.00059461 | 0.0091277 | -1.0753e-05 | -0.00018007 | -1.7234 | 0.15727 | -0.0016886 | -0.0199 | -5.6407e-06 | 0.00026832 | -8.1183 | 0.19462 | -0.001363 | 0.049219 | -7.8478e-05 | -0.00027809 | -18.1646 | -1.0769 | -0.0033542 | 1.3631 | -0.016506 | 0.019211 | 0.00093864 | 0.77642 | -0.23604 | 0.45868 | 0.0014606 | 0.79218 | -0.28387 | 0.49023 | 0.0020106 | 0.80555 | -0.32526 | 0.5177 | 0.75329 | 0.24671 | 1e-08 | 0.71255 | 0.28745 | 1e-08 | 0.67634 | 0.32366 | 1e-08 | 2 | 0.61111 | 0.46385 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.78779 | 0.21221 | 0.91747 | 1
SA-17-TM | Split-TS | AC | 17 | Median | Trane | 12.16 | 51504.454 | 0.767 | 0.2333 | 0.03301 | 0.328 | 0.1203 | 0 | 55 | 3.0314 | -0.081031 | 0.00085058 | 0.0080524 | -6.4373e-06 | -0.00017713 | -1.0324 | 0.1385 | -0.0015388 | -0.021496 | 3.9127e-06 | 0.00026193 | -5.6513 | 0.1511 | -0.0010574 | 0.02796 | 1.9731e-05 | -0.00024508 | 157.5024 | -1.3681 | 0.0074867 | -2.9282 | 0.018207 | 0.0035975 | 0.00041969 | 1.0323 | -0.31848 | 0.28572 | 0.0011243 | 1.0651 | -0.41485 | 0.34858 | 0.001985 | 1.0926 | -0.49748 | 0.40294 | 0.80434 | 0.19566 | 1e-08 | 0.74384 | 0.25616 | 1e-08 | 0.69009 | 0.30991 | 1e-08 | 2 | 0.41176 | 0.47194 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.3394 | 0.6606 | 0.61141 | 1
SA-17-TH | Split-TS | AC | 17 | High | Trane | 12.95 | 32559.053 | 0.7789 | 0.2263 | 0.03378 | 0.255 | 0.1137 | 0 | 55 | 1.3083 | -0.030729 | 0.00047802 | 0.009023 | -1.3356e-05 | -0.00017784 | -6.7773 | 0.31446 | -0.0028762 | -0.02487 | 6.0066e-06 | 0.00030295 | -5.7681 | 0.12399 | -0.00064518 | 0.051623 | 2.6164e-05 | -0.00059441 | 165.8828 | 0.047005 | 0.0086536 | -4.3925 | 0.036402 | -0.016503 | -0.0023022 | 1.2196 | -0.64679 | 0.42947 | -0.0021015 | 1.259 | -0.75499 | 0.49805 | -0.0017531 | 1.2929 | -0.84925 | 0.55809 | 0.74664 | 0.25336 | 1e-08 | 0.70097 | 0.29903 | 1e-08 | 0.66039 | 0.33961 | 1e-08 | 2 | 0.54545 | 0.54703 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.38159 | 0.61841 | 0.71891 | 1
SA-18-LL | Split-TS | AC | 18 | Low | Lennox | 12.97 | 37800 | 0.76 | 0.22318 | 0.03228 | 0.287 | 0.117 | 0.02 | 55 | 0.14919 | 0.0090303 | 0.00013469 | 0.0066192 | -1.7179e-05 | -0.00013081 | 4.4315 | -0.064587 | 0.00018906 | 0.0045302 | -3.3345e-05 | -1.2937e-05 | 0.59373 | -0.0030766 | 4.5937e-05 | 0.0025947 | 0.00013455 | -0.00016569 | -34.6228 | 0.77426 | -0.020326 | 0.24359 | -0.010642 | 0.023062 | -0.00080657 | 1.1134 | -0.21443 | 0.1018 | -0.0012548 | 1.1639 | -0.32949 | 0.16684 | -0.0016043 | 1.2087 | -0.4326 | 0.2255 | 0.9203 | 0.079698 | 1e-08 | 0.88469 | 0.11531 | 1e-08 | 0.85304 | 0.14696 | 1e-08 | 2 | 0.70082 | 0.7037 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | -0.46519 | 1.4652 | 0.56164 | 1
SA-18-LH | Split-TS | AC | 18 | High | Lennox | 13.22 | 37600 | 0.77 | 0.22729 | 0.03218 | 0.223 | 0.0906 | 0.02 | 55 | 0.32427 | 0.00443 | 0.00016562 | 0.0062572 | -1.6869e-05 | -0.00012675 | 3.7959 | -0.031583 | -0.00010781 | -0.0047877 | -9.3452e-06 | 5.3938e-05 | 0.46634 | 0.00021 | 1.625e-05 | 0.0029905 | 0.0001305 | -0.0001595 | -16.1082 | 0.99625 | -0.017405 | -0.38778 | -0.0032431 | 0.014975 | -0.0021434 | 1.1673 | -0.43738 | 0.2722 | -0.0025059 | 1.2169 | -0.55128 | 0.33693 | -0.0027705 | 1.2607 | -0.65317 | 0.39521 | 0.87914 | 0.12086 | 1e-08 | 0.84341 | 0.15659 | 1e-08 | 0.81166 | 0.18834 | 1e-08 | 2 | 0.69835 | 0.70745 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | -0.31521 | 1.3152 | 0.60326 | 1
SA-18-TL | Split-TS | AC | 18 | Low | Trane | 12.73 | 37347.791 | 0.7671 | 0.2325 | 0.03213 | 0.256 | 0.0962 | 0 | 55 | 1.7951 | -0.04764 | 0.00061145 | 0.010621 | -1.6781e-05 | -0.0001894 | -5.7065 | 0.27823 | -0.0025744 | -0.022305 | 5.5166e-06 | 0.00026566 | -6.5421 | 0.14759 | -0.0008538 | 0.051393 | 1.0894e-05 | -0.00054898 | 7.6211 | -1.5673 | 0.013074 | 1.0848 | -0.0043853 | -0.003549 | -0.0012671 | 1.0227 | -0.41945 | 0.39806 | -0.00094452 | 1.0519 | -0.50218 | 0.45126 | -0.00051974 | 1.0768 | -0.57402 | 0.49771 | 0.78962 | 0.21038 | 1e-08 | 0.74362 | 0.25638 | 1e-08 | 0.70275 | 0.29725 | 1e-08 | 2 | 0.54167 | 0.5014 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.82514 | 0.17486 | 0.91986 | 1
SA-18-TM | Split-TS | AC | 18 | Median | Trane | 13.37 | 33259.053 | 0.7775 | 0.219 | 0.03307 | 0.255 | 0.0978 | 0 | 55 | 0.9836 | -0.022207 | 0.00042621 | 0.0097194 | -1.2497e-05 | -0.0001916 | -6.8297 | 0.31392 | -0.0028688 | -0.023417 | 6.1541e-07 | 0.00029761 | -5.4569 | 0.11477 | -0.00057356 | 0.051643 | 2.8182e-05 | -0.00059995 | 182.1591 | -0.18963 | 0.012835 | -4.6337 | 0.039881 | -0.020637 | -0.0023654 | 1.1693 | -0.53973 | 0.37281 | -0.0023282 | 1.2091 | -0.64795 | 0.44114 | -0.0021382 | 1.2435 | -0.74244 | 0.50109 | 0.79 | 0.21 | 1e-08 | 0.74431 | 0.25569 | 1e-08 | 0.70371 | 0.29629 | 1e-08 | 2 | 0.54545 | 0.54453 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.32333 | 0.67667 | 0.69242 | 1
SA-18-TH | Split-TS | AC | 18 | High | Trane | 13.75 | 34047.791 | 0.7944 | 0.2098 | 0.03524 | 0.256 | 0.1169 | 0 | 55 | 2.1039 | -0.056594 | 0.00067585 | 0.010745 | -1.846e-05 | -0.00018855 | -6.6409 | 0.30833 | -0.0028165 | -0.023667 | 5.1352e-06 | 0.00028719 | -6.8884 | 0.16007 | -0.00094699 | 0.049483 | 2.0896e-05 | -0.00054592 | -33.0977 | -1.7425 | 0.012613 | 2.3104 | -0.013677 | -0.00057401 | -0.0021401 | 1.2111 | -0.56396 | 0.35503 | -0.0020998 | 1.253 | -0.67753 | 0.42665 | -0.0018975 | 1.2891 | -0.77668 | 0.48949 | 0.78097 | 0.21903 | 1e-08 | 0.73496 | 0.26504 | 1e-08 | 0.69408 | 0.30592 | 1e-08 | 2 | 0.54167 | 0.55 | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | na | 0.46976 | 0.53024 | 0.75697 | 1
SH-10-LL | Split-R | HP | 10 | Low | Low | 9.12 | 24890.1122 | 0.7308 | 0.31389 | 0.03515 | 0.365 | 0.2541 | 0 | 100 | 2.6857 | -0.076584 | 0.00079834 | 0.0097026 | -3.2612e-05 | -0.00012031 | -4.3331 | 0.21581 | -0.0020488 | -0.0046574 | -2.4881e-05 | 0.00011599 | -1.015 | 0.067142 | -0.00059398 | -0.0083138 | 0.0001093 | -2.1647e-06 | 34.7964 | -0.55642 | 0.0097177 | -0.41463 | 0.0065097 | -0.0090728 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | 6.8 | 3.08 | 22300 | 0.32446 | 0.43219 | 0.0024648 | -2.3318e-05 | 0.0082513 | 0.00012628 | -4.779e-05 | 1.1874 | 0.010345 | 3.3597e-05 | -0.020254 | 0.00015209 | -0.00013988 | 1 | 0 | 0 | 1
SH-10-LM | Split-R | HP | 10 | Low | Median | 9.52 | 24596.596 | 0.7276 | 0.3036 | 0.03252 | 0.365 | 0.2016 | 0 | 100 | 2.7788 | -0.075579 | 0.00078796 | 0.0072226 | -1.9665e-05 | -0.00011954 | -3.9429 | 0.20203 | -0.0019456 | -0.0039589 | -3.1427e-05 | 0.00012577 | -1.0983 | 0.06542 | -0.000565 | -0.0055602 | 9.9285e-05 | -1.8295e-05 | 42.4842 | -0.83116 | 0.012332 | -0.37701 | 0.0066037 | -0.0099358 | 7.2478e-05 | 1.2027 | -0.26271 | 0.059969 | 0.00011782 | 1.236 | -0.31431 | 0.078168 | 0.00017345 | 1.2665 | -0.3629 | 0.096274 | 0.82622 | 0.20361 | -0.030176 | 0.80141 | 0.23745 | -0.039377 | 0.77942 | 0.26843 | -0.048548 | 1 | 1 | 1 | 7 | 3.2 | 22600 | 0.31261 | 0.51855 | 0.00010742 | -5.8997e-06 | 0.0080204 | 0.00013588 | -5.2971e-05 | 1.1326 | 0.010803 | 2.6032e-05 | -0.01848 | 0.00011913 | -0.00012491 | 1 | 0 | 0 | 1
SH-10-LH | Split-R | HP | 10 | Low | High | 10.01 | 58800 | 0.7381 | 0.28844 | 0.03146 | 0.365 | 0.1415 | 0.02 | 100 | 0.53344 | -0.0056185 | 0.0001615 | 0.0067088 | -4.675e-05 | -1.53e-05 | 1.7985 | 0.001115 | -0.000265 | 0.007611 | -5e-05 | 7e-06 | 1.0015 | -0.0026135 | 8.65e-05 | -0.0029867 | 0.00015075 | -0.0002029 | 1.7031 | -0.10878 | 0 | 0.11623 | 0 | -0.00050623 | 0.00021601 | 1.2854 | -0.39389 | 0.10824 | 0.00031399 | 1.3209 | -0.45319 | 0.13194 | 0.00042614 | 1.3532 | -0.5084 | 0.15482 | 0.76597 | 0.28782 | -0.054621 | 0.74134 | 0.32421 | -0.06666 | 0.71951 | 0.3574 | -0.078308 | 1 | 1 | 1 | 7.2 | 3.1 | 57000 | 0.32258 | 0.49754 | -0.0035468 | 1.864e-05 | 0.016303 | 4.1388e-08 | -3.2506e-05 | 1.0056 | 0.0076815 | 6.6733e-05 | -0.018148 | 0.00023191 | -0.00016098 | 1 | 0 | 0 | 1
SH-10-ML | Split-R | HP | 10 | Median | Low | 8.78 | 17778.5053 | 0.7413 | 0.32807 | 0.03515 | 0.365 | 0.2307 | 0 | 100 | 3.2147 | -0.081674 | 0.00084926 | 0.0030296 | 5.7672e-06 | -0.00014057 | -3.8556 | 0.20894 | -0.0020275 | -0.009746 | -1.5271e-05 | 0.00016059 | -2.0119 | 0.088143 | -0.00077337 | -0.0011726 | 8.0641e-05 | -6.0427e-06 | 44.4065 | -0.83516 | 0.0099629 | -0.42743 | 0.0054315 | -0.0061085 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 6.9 | 3.22 | 16300 | 0.31199 | 0.39388 | 0.000142 | -3.272e-06 | 0.010095 | 0.00012964 | -4.518e-05 | 1.3969 | 0.013881 | 2.9612e-05 | -0.03592 | 0.00033915 | -0.00017466 | 1 | 0 | 0 | 1
SH-10-MM | Split-R | HP | 10 | Median | Median | 9.01 | 45244.043 | 0.6861 | 0.32561 | 0.03094 | 0.365 | 0.2695 | 0 | 100 | 0.81128 | -0.018719 | 0.00035371 | 0.0090212 | -3.3219e-05 | -0.00011031 | 0.54049 | 0.067781 | -0.00086934 | -0.005392 | -6.0937e-06 | 6.0938e-05 | -0.38566 | 0.032329 | -0.00020957 | 0.0010332 | 0.00011907 | -0.00015906 | 22.5798 | -0.47799 | 0.0062049 | -0.15993 | 0.0026371 | -0.0040095 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 7.2 | 2.98 | 41000 | 0.33547 | 0.48708 | 0.0022175 | -2.2764e-05 | 0.0080465 | 0.00011543 | -4.9826e-05 | 1.0328 | 0.0029551 | 5.9167e-05 | -0.0059182 | -9.9441e-08 | -7.6341e-05 | 1 | 0 | 0 | 1
SH-10-MH | Split-R | HP | 10 | Median | High | 9.54 | 41810 | 0.7512 | 0.29923 | 0.03468 | 0.365 | 0.1918 | 0.02 | 100 | 0.88897 | -0.016558 | 0.0002515 | 0.0072477 | -4.775e-05 | -2.61e-05 | 0.98267 | 0.030796 | -0.000509 | 0.0042383 | -4.5083e-05 | 3.82e-05 | 0.70283 | 0.0076665 | -3.5e-06 | -0.0059112 | 0.00016375 | -0.0001755 | 1.3647 | -0.08062 | 0 | 0.08728 | 0 | -0.00036298 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 7.2 | 3.1 | 39000 | 0.32258 | 0.50135 | -0.0032958 | 1.6026e-05 | 0.017694 | 6.2468e-07 | -5.5371e-05 | 1.1925 | 0.0076525 | 5.5889e-05 | -0.024692 | 0.00026254 | -0.00012809 | 1 | 0 | 0 | 1
SH-10-HL | Split-R | HP | 10 | High | Low | 8.94 | 42244 | 0.7349 | 0.3247 | 0.03314 | 0.365 | 0.1991 | 0 | 100 | 2.5528 | -0.062992 | 0.0006532 | 0.0049664 | -1.631e-05 | -9.2557e-05 | -1.643 | 0.13839 | -0.0014391 | -0.013122 | -1.0762e-05 | 0.0001845 | -1.2598 | 0.069465 | -0.00053187 | -0.0062728 | 0.00014619 | -0.00011474 | -4.394 | -0.093684 | 0.01118 | 0.17745 | 0.0066788 | -0.017809 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | 7.2 | 3 | 42000 | 0.32423 | 0.57143 | 0.00022109 | -1.1905e-05 | 0.0092094 | 5.5461e-05 | -2.551e-05 | 1.0876 | 0.0011147 | 0.00011398 | -0.011862 | 0.00013312 | -0.00014002 | 1 | 0 | 0 | 1
SH-10-HM | Split-R | HP | 10 | High | Median | 9.01 | 37894.894 | 0.7097 | 0.32427 | 0.03167 | 0.365 | 0.225 | 0 | 100 | 1.7413 | -0.040143 | 0.00050117 | 0.005304 | -1.3417e-05 | -0.0001075 | -1.2901 | 0.12608 | -0.0013088 | -0.0068638 | 7.6979e-06 | 4.7187e-05 | -0.58043 | 0.046714 | -0.0003959 | -0.0058191 | 0.00012903 | -6.0312e-05 | 36.5773 | -0.7262 | 0.0096588 | -0.3145 | 0.0047944 | -0.0066798 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 7.3 | 3.04 | 32400 | 0.32866 | 0.53054 | 0.0010371 | -4.1152e-06 | 0.0023607 | 0.00011984 | 1.2566e-05 | -0.46921 | 0.033136 | -1.054e-05 | -0.0026813 | 7.3956e-05 | -0.0002541 | 1 | 0 | 0 | 1
SH-10-HH | Split-R | HP | 10 | High | High | 9.39 | 47993 | 0.7562 | 0.3069 | 0.03334 | 0.365 | 0.154 | 0 | 100 | 2.8361 | -0.069879 | 0.00069173 | 0.0045196 | -1.6857e-05 | -8.43e-05 | -2.6635 | 0.16954 | -0.0016832 | -0.013263 | -1.2452e-05 | 0.00019369 | -1.5182 | 0.078325 | -0.00060147 | -0.0074392 | 0.00014795 | -0.0001034 | -5.8153 | -0.51413 | 0.016022 | 0.5341 | 0.0060075 | -0.020865 | 0.00010194 | 1.2255 | -0.29791 | 0.072258 | 0.00015951 | 1.2595 | -0.35175 | 0.092043 | 0.00022851 | 1.2905 | -0.40227 | 0.11153 | 0.80912 | 0.2268 | -0.036387 | 0.78436 | 0.26139 | -0.046404 | 0.76241 | 0.29301 | -0.056289 | 1 | 1 | 1 | 7.2 | 3.2 | 47000 | 0.31225 | 0.18865 | 0.0091403 | -7.4468e-05 | 0.0080527 | 9.3381e-05 | -1.4691e-05 | 0.94611 | 0.0083744 | 6.12e-05 | -0.015269 | 0.0001579 | -0.00014083 | 1 | 0 | 0 | 1
SH-13-LL | Split-R | HP | 13 | Low | Low | 11.53 | 25598.642 | 0.75 | 0.2555 | 0.03125 | 0.293 | 0.1129 | 0 | 55 | 3.0075 | -0.075226 | 0.0007541 | 0.0033559 | -1.4219e-05 | -8.5312e-05 | -3.6346 | 0.19506 | -0.0017805 | -0.007642 | 2.0042e-05 | 1.625e-05 | -3.2389 | 0.09682 | -0.00061875 | 0.015587 | 8.8104e-05 | -0.00027438 | 52.5801 | -1.3481 | 0.017654 | -0.18922 | 0.0072047 | -0.013335 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 8.3 | 3.5 | 21129.2 | 0.29285 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
SH-13-LM | Split-R | HP | 13 | Low | Median | 11.84 | 48930 | 0.7507 | 0.2374 | 0.03168 | 0.365 | 0.1164 | 0 | 55 | 1.1178 | -0.023581 | 0.0003585 | 0.0053237 | -3.0667e-05 | -5.91e-05 | 2.1597 | -0.000701 | -0.000286 | 0.002418 | -4.3167e-05 | 5.2e-05 | 0.99779 | -0.007208 | 0.000192 | 0.0020622 | 0.00018875 | -0.0003576 | 3.5898 | -0.13858 | 0 | 0.094128 | 0 | -0.00015582 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.9561e-05 | 1.1799 | -0.22858 | 0.048622 | 7.9822e-05 | 1.2089 | -0.27221 | 0.063229 | 0.86849 | 0.14864 | -0.017294 | 0.84361 | 0.18058 | -0.024448 | 0.82153 | 0.20992 | -0.031823 | 1 | 1 | 1 | 8 | 4.09 | 46000 | 0.2445 | 0.52239 | -0.0028874 | 1.3587e-05 | 0.016094 | -1.6915e-07 | -4.3434e-05 | 1.0249 | 0.0035545 | 2.1474e-05 | -0.014943 | 9.3632e-05 | 3.5437e-05 | 1 | 0 | 0 | 1
SH-13-LH | Split-R | HP | 13 | Low | High | 12.5 | 31370 | 0.7737 | 0.2174 | 0.03506 | 0.365 | 0.1511 | 0 | 55 | 1.2306 | -0.028843 | 0.000367 | 0.0073972 | -4.25e-05 | -4.16e-05 | 0.80346 | 0.036358 | -0.0005775 | 0.0039492 | -5.5e-05 | 7.45e-05 | 0.59526 | 0.004412 | 4.7e-05 | 0.0016515 | 0.00015442 | -0.0002596 | 1.7988 | -0.10593 | 0 | 0.097877 | 0 | -0.00028579 | 0.00011963 | 1.2372 | -0.31609 | 0.078814 | 0.00018406 | 1.2715 | -0.37103 | 0.099385 | 0.00026049 | 1.3027 | -0.4225 | 0.11955 | 0.80059 | 0.23859 | -0.039704 | 0.77585 | 0.27354 | -0.050126 | 0.75392 | 0.30548 | -0.060364 | 1 | 1 | 1 | 8 | 3.46 | 28200 | 0.28902 | 0.44887 | -0.00087708 | -2.2163e-06 | 0.018922 | 4.8169e-07 | -8.1163e-05 | 1.5705 | 0.0039751 | 4.7938e-05 | -0.033101 | 0.00027456 | -4.0843e-05 | 1 | 0 | 0 | 1
SH-13-ML | Split-R | HP | 13 | Median | Low | 11.12 | 43600 | 0.74 | 0.26056 | 0.02982 | 0.346 | 0.0963 | 0 | 100 | 0.82741 | -0.00885 | 0.00023438 | 0.0022913 | -9.5e-06 | -6.575e-05 | 1.828 | 0.020088 | -0.00048125 | -0.00068342 | -1.775e-05 | 3.325e-05 | 0.63994 | -0.00017656 | 6.9531e-05 | 0.0029365 | 0.00015458 | -0.00025363 | 31.1798 | -0.92033 | 0.012082 | 0.023305 | 0.0037661 | -0.0090897 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 8.3 | 3.4 | 39400 | 0.29106 | 0.44609 | 0 | 0 | 0.010267 | 3.2312e-05 | 0 | 2.0124 | 0 | 0 | -0.039052 | 0.00037259 | 0 | 1 | 0 | 0 | 1
SH-13-MM | Split-R | HP | 13 | Median | Median | 11.07 | 42695.9152 | 0.726 | 0.2718 | 0.02811 | 0.292 | 0.0806 | 0 | 55 | 2.1469 | -0.053591 | 0.00057676 | 0.005859 | -2.599e-05 | -7.3437e-05 | -1.7062 | 0.13575 | -0.0013857 | -0.0069019 | -2.6146e-06 | 8.0312e-05 | -1.7948 | 0.059853 | -0.00042656 | 0.0098629 | 9.9313e-05 | -0.00017813 | 110.892 | -2.1341 | 0.019265 | -1.0703 | 0.010216 | -0.0061829 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | 8.1 | 3.28 | 39500 | 0.30501 | 0.6623 | -0.0032213 | 1.0127e-05 | 0.012603 | 4.4602e-05 | -5.3888e-05 | 0.85347 | 0.012033 | 3.2884e-05 | -0.015984 | 0.00015301 | -0.00013486 | 1 | 0 | 0 | 1
SH-13-MH | Split-R | HP | 13 | Median | High | 11.96 | 37195.9152 | 0.7795 | 0.244 | 0.03226 | 0.292 | 0.0702 | 0 | 55 | 3.8943 | -0.10524 | 0.0010072 | 0.0057953 | -6.8438e-06 | -0.00013406 | -6.8992 | 0.29864 | -0.0027344 | -0.010798 | -3.5104e-05 | 0.00023687 | -3.7316 | 0.12177 | -0.00091445 | 0.0071743 | 0.00010804 | -0.00015375 | 113.0469 | -2.7805 | 0.035257 | -0.56155 | 0.015446 | -0.025737 | 0.00018743 | 1.273 | -0.37355 | 0.10035 | 0.00027598 | 1.3082 | -0.43176 | 0.12326 | 0.00037818 | 1.3402 | -0.48604 | 0.14546 | 0.77475 | 0.27512 | -0.050616 | 0.75009 | 0.31116 | -0.062249 | 0.72824 | 0.34403 | -0.073543 | 1 | 1 | 1 | 8.55 | 3.38 | 34400 | 0.2659 | 0.72904 | -0.0037841 | 1.1628e-05 | 0.011498 | 6.4002e-05 | -6.1669e-05 | 0.92604 | 0.011616 | 5.309e-05 | -0.017186 | 0.00016908 | -0.00017176 | 1 | 0 | 0 | 1
SH-13-HL | Split-R | HP | 13 | High | Low | 10.71 | 61042 | 0.7887 | 0.2702 | 0.03276 | 0.329 | 0.0516 | 0 | 100 | 2.7252 | -0.06644 | 0.00068411 | 0.0071699 | -2.3268e-05 | -0.00012818 | -3.4771 | 0.19814 | -0.0019158 | -0.015746 | -1.4583e-05 | 0.00022458 | -1.3687 | 0.079355 | -0.00062022 | -0.016303 | 0.00020668 | -7.5478e-05 | 210.0889 | -6.9504 | 0.052794 | 0.46201 | 0.00018219 | -0.0034578 | 1.5758e-06 | 1.0607 | -0.067351 | 0.006601 | 5.2959e-06 | 1.0891 | -0.10271 | 0.01357 | 1.2009e-05 | 1.1153 | -0.13716 | 0.021831 | 0.94251 | 0.06078 | -0.0033065 | 0.91754 | 0.089226 | -0.0068034 | 0.89536 | 0.11552 | -0.010954 | 1 | 1 | 1 | 8.1 | 3.56 | 60700 | 0.27383 | 0.29224 | 0.0060638 | -5.7661e-05 | 0.0088136 | 8.4399e-05 | -1.0591e-05 | 0.82119 | 0.004555 | 0.00014675 | -0.0087573 | 0.000176 | -0.0002542 | 1 | 0 | 0 | 1
SH-13-HM | Split-R | HP | 13 | High | Median | 11.2 | 48595 | 0.7209 | 0.2625 | 0.02881 | 0.329 | 0.1044 | 0 | 100 | 1.8624 | -0.040109 | 0.00048256 | 0.0047862 | -1.1065e-05 | -0.00010936 | -0.34892 | 0.10001 | -0.0011431 | -0.013187 | -7.8929e-06 | 0.00017339 | -0.9082 | 0.052167 | -0.00040011 | -0.0053105 | 0.00016496 | -0.00012178 | 54.3145 | -2.6217 | 0.01334 | 0.80667 | -0.0080557 | 0.0092311 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 8.5 | 3.56 | 50000 | 0.28112 | 0.13695 | 0.0078798 | -5.5e-05 | 0.010639 | 8.8056e-05 | -3.4524e-05 | 1.2158 | -0.0013435 | 0.00015533 | -0.016892 | 0.00016416 | -0.00013726 | 1 | 0 | 0 | 1
SH-13-HH | Split-R | HP | 13 | High | High | 11.26 | 30086 | 0.7269 | 0.2607 | 0.02908 | 0.328 | 0.0964 | 0 | 100 | 2.0198 | -0.046955 | 0.00053356 | 0.0054815 | -1.625e-05 | -0.00010103 | -0.73682 | 0.10943 | -0.0012023 | -0.012514 | -8.6548e-06 | 0.00016793 | -1.5013 | 0.071962 | -0.00055467 | -0.0054993 | 0.00018843 | -0.00015843 | 62.7122 | -3.0776 | 0.01553 | 0.97282 | -0.0097504 | 0.011073 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 8 | 3.24 | 32000 | 0.30864 | 0.58963 | -0.0039862 | 2.3438e-05 | 0.011473 | 6.8638e-05 | -3.5342e-05 | 0.3699 | 0.023176 | -1.3028e-05 | -0.019057 | 0.00018968 | -0.00013729 | 1 | 0 | 0 | 1
SH-14-ML | Split-R | HP | 14 | Median | Low | 12.05 | 35400 | 0.81 | 0.23553 | 0.03672 | 0.304 | 0.1204 | 0 | 100 | 2.0216 | -0.04673 | 0.00053047 | 0.0051336 | -9.5e-06 | -0.00010587 | 0.98241 | 0.051441 | -0.00078906 | -0.0039263 | -3.3583e-05 | 0.000124 | -1.1465 | 0.062342 | -0.00043984 | -0.0045492 | 0.00016325 | -0.00017238 | -15.1755 | 0.44534 | 0.0066826 | 0.043298 | 0.0072806 | -0.017485 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 8.2 | 3.46 | 32200 | 0.29095 | 0.42287 | 0 | 0 | 0.010207 | 4.4097e-05 | 0 | 2.1337 | 0 | 0 | -0.040808 | 0.00035506 | 0 | 1 | 0 | 0 | 1
SH-14-MM | Split-R | HP | 14 | Median | Median | 12.55 | 36950 | 0.7754 | 0.23562 | 0.03274 | 0.255 | 0.087 | 0 | 100 | 1.5702 | -0.043227 | 0.0004735 | 0.010389 | -5.8583e-05 | -4.05e-05 | 0.6838 | 0.04003 | -0.0006105 | 0.003635 | -5.8167e-05 | 8.71e-05 | 0.028526 | 0.027774 | -0.0001115 | -0.003054 | 0.00018858 | -0.0002829 | 1.4728 | -0.19939 | 0 | 0.16204 | 0 | -1.4361e-05 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | 8.5 | 3.66 | 34400 | 0.28249 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1
SH-14-MH | Split-R | HP | 14 | Median | High | 13.38 | 26120 | 0.7703 | 0.21725 | 0.03369 | 0.263 | 0.1244 | 0 | 100 | 1.3745 | -0.044251 | 0.000499 | 0.013156 | -6.7083e-05 | -4.62e-05 | 0.71073 | 0.027818 | -0.000472 | 0.010752 | -7.05e-05 | 2.5e-05 | 0.29578 | 0.021473 | -6.25e-05 | -0.003101 | 0.00019033 | -0.0002949 | 3.0063 | -0.14365 | 0 | 0.11043 | 0 | -0.00022691 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 8.5 | 3.68 | 24000 | 0.27174 | 0.34365 | -0.00014023 | -7.8125e-06 | 0.02188 | 2.4132e-06 | -0.00010007 | 2.0345 | 0.0021825 | 3.5281e-05 | -0.048786 | 0.00038872 | 2.2519e-05 | 1 | 0 | 0 | 1
SH-14-HL | Split-R | HP | 14 | High | Low | 11.6 | 34678 | 0.7343 | 0.2552 | 0.03028 | 0.292 | 0.1128 | 0 | 100 | 2.0556 | -0.046414 | 0.00053256 | 0.0050607 | -1.1107e-05 | -0.00011265 | -1.0564 | 0.11951 | -0.001281 | -0.012413 | -8.8929e-06 | 0.00016636 | -1.0424 | 0.058979 | -0.00046089 | -0.006088 | 0.00015829 | -0.00010849 | 47.6978 | -2.603 | 0.014265 | 0.96678 | -0.0084764 | 0.0075694 | 9.5772e-07 | 1.0519 | -0.056737 | 0.0048828 | 3.7387e-06 | 1.0799 | -0.090918 | 0.011055 | 9.109e-06 | 1.1057 | -0.12435 | 0.018613 | 0.95056 | 0.051873 | -0.0024452 | 0.92558 | 0.079928 | -0.0055407 | 0.9034 | 0.10588 | -0.0093364 | 1 | 1 | 1 | 8.2 | 3.38 | 36360 | 0.29591 | 0.12206 | 0.0099825 | -7.6389e-05 | 0.0097357 | 6.3602e-05 | -1.3558e-05 | 0.89151 | 0.0055907 | 0.00012433 | -0.013788 | 0.00017108 | -0.00018905 | 1 | 0 | 0 | 1
SH-14-HM | Split-R | HP | 14 | High | Median | 12.19 | 23886 | 0.7306 | 0.25206 | 0.02931 | 0.219 | 0.0932 | 0 | 100 | 2.1353 | -0.05279 | 0.00056622 | 0.0069936 | -2.7161e-05 | -8.7878e-05 | -1.2037 | 0.12174 | -0.0012984 | -0.011162 | -1.4494e-05 | 0.00016767 | -1.4994 | 0.07795 | -0.00061978 | -0.0074045 | 0.0001638 | -0.00011247 | 42.3015 | -3.3546 | 0.018948 | 1.689 | -0.013356 | 0.0090972 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | 8.6 | 3.52 | 24000 | 0.28439 | -0.26067 | 0.019758 | -0.00014792 | 0.012135 | 7.2586e-05 | -3.8988e-05 | 2.3651 | -0.026065 | 0.00033863 | -0.026283 | 0.0002813 | -0.0001781 | 1 | 0 | 0 | 1
SH-14-HH | Split-R | HP | 14 | High | High | 11.77 | 29871 | 0.7249 | 0.25693 | 0.02929 | 0.256 | 0.1082 | 0 | 100 | 2.0281 | -0.047312 | 0.00053756 | 0.0055126 | -1.6327e-05 | -0.00010175 | -0.75112 | 0.11045 | -0.0012138 | -0.012651 | -8.7024e-06 | 0.00016969 | -1.4844 | 0.071787 | -0.000554 | -0.0054032 | 0.00018632 | -0.00015815 | 47.2255 | -2.7022 | 0.014957 | 1.047 | -0.0089877 | 0.0077318 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 8.3 | 3.42 | 32000 | 0.29408 | 0.58963 | -0.0039862 | 2.3438e-05 | 0.011473 | 6.8638e-05 | -3.5342e-05 | 0.3699 | 0.023176 | -1.3028e-05 | -0.019057 | 0.00018968 | -0.00013729 | 1 | 0 | 0 | 1
SH-15-ML | Split-R | HP | 15 | Median | Low | 12.7 | 35800 | 0.81 | 0.2393 | 0.03631 | 0.188 | 0.1105 | 0 | 100 | 2.1076 | -0.048102 | 0.00054453 | 0.0042147 | -4.5833e-06 | -0.00010812 | 0.11245 | 0.07598 | -0.00097109 | -0.0031148 | -3.8333e-05 | 0.00012537 | -1.1825 | 0.063945 | -0.00046016 | -0.0048318 | 0.00016083 | -0.00016163 | 7.9359 | 0.1095 | 0.0074306 | -0.26117 | 0.0080252 | -0.01457 | 9.5772e-07 | 1.0519 | -0.056737 | 0.0048828 | 3.7387e-06 | 1.0799 | -0.090918 | 0.011055 | 9.109e-06 | 1.1057 | -0.12435 | 0.018613 | 0.95056 | 0.051873 | -0.0024452 | 0.92558 | 0.079928 | -0.0055407 | 0.9034 | 0.10588 | -0.0093364 | 1 | 1 | 1 | 8.8 | 3.74 | 32300 | 0.26786 | 0.42204 | 0 | 0 | 0.01019 | 4.4835e-05 | 0 | 2.1186 | 0 | 0 | -0.039322 | 0.00033023 | 0 | 1 | 0 | 0 | 1
SH-15-MM | Split-R | HP | 15 | Median | Median | 12.63 | 25597.9576 | 0.7695 | 0.2406 | 0.03125 | 0.219 | 0.0647 | 0 | 55 | 4.0487 | -0.10901 | 0.0011211 | 0.0060803 | 1.3354e-05 | -0.00023187 | -5.4249 | 0.26345 | -0.0025088 | -0.016551 | -3.449e-05 | 0.00030156 | -3.52 | 0.11152 | -0.00092793 | 0.0098018 | 3.6781e-05 | -7.8125e-06 | 177.5637 | -3.5308 | 0.03984 | -1.6152 | 0.02149 | -0.023723 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | 8.2 | 3.44 | 21800 | 0.2912 | 0.42366 | -0.00040973 | -5.5046e-06 | 0.015659 | 4.8322e-05 | -6.4056e-05 | 1.2676 | 0.011042 | 4.4075e-05 | -0.030183 | 0.00031695 | -0.00016354 | 1 | 0 | 0 | 1
SH-15-MH | Split-R | HP | 15 | Median | High | 13.01 | 29000 | 0.79 | 0.23565 | 0.03448 | 0.18 | 0.1071 | 0 | 100 | 1.7776 | -0.036891 | 0.00048594 | 0.0027071 | 8.6667e-06 | -0.00012925 | 0.75674 | 0.074072 | -0.00097656 | -0.01424 | 1.1667e-05 | 0.00014325 | -0.42968 | 0.027153 | -0.00021094 | 0.0060317 | 0.00010617 | -0.000153 | -46.1038 | 0.099319 | 0.011855 | 1.0982 | 0.0022947 | -0.021513 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 9 | 3.56 | 26400 | 0.27601 | 0.4436 | 0 | 0 | 0.011315 | 1.1138e-05 | 0 | 1.9018 | 0 | 0 | -0.035434 | 0.00034567 | 0 | 1 | 0 | 0 | 1
SH-15-HL | Split-R | HP | 15 | High | Low | 12.58 | 36315 | 0.7329 | 0.2392 | 0.02891 | 0.255 | 0.0747 | 0 | 100 | 2.0612 | -0.046637 | 0.00053511 | 0.0050758 | -1.1137e-05 | -0.00011317 | -1.0703 | 0.12034 | -0.00129 | -0.012499 | -8.994e-06 | 0.00016765 | -1.0306 | 0.058993 | -0.00046244 | -0.0061388 | 0.00015742 | -0.0001074 | 85.0175 | -4.0775 | 0.025692 | 1.2037 | -0.009135 | 0.0067192 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 9.4 | 3.92 | 35280 | 0.25551 | 0.12206 | 0.0099825 | -7.6389e-05 | 0.0097357 | 6.3602e-05 | -1.3558e-05 | 0.89151 | 0.0055907 | 0.00012433 | -0.013788 | 0.00017108 | -0.00018905 | 1 | 0 | 0 | 1
SH-15-HM | Split-R | HP | 15 | High | Median | 12.77 | 32147.447 | 0.776 | 0.23778 | 0.03111 | 0.219 | 0.0443 | 0 | 55 | 3.7929 | -0.10388 | 0.0010096 | 0.0073047 | -7.8021e-06 | -0.00015531 | -7.0875 | 0.30506 | -0.0027945 | -0.010381 | -3.7229e-05 | 0.00023812 | -3.3451 | 0.11845 | -0.00096348 | 0.0018119 | 9.5073e-05 | -4.6563e-05 | 200.8428 | -4.4757 | 0.066834 | -1.4045 | 0.034185 | -0.057167 | 9.6615e-06 | 1.1077 | -0.12697 | 0.019258 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 3.813e-05 | 1.1657 | -0.20777 | 0.042019 | 0.90173 | 0.10786 | -0.0096605 | 0.8768 | 0.13825 | -0.015181 | 0.85466 | 0.16625 | -0.021118 | 1 | 1 | 1 | 9 | 3.68 | 28000 | 0.27304 | 0.53753 | -0.0012164 | 4.7619e-06 | 0.0095819 | 4.2967e-05 | -6.3776e-06 | -0.97352 | 0.0422 | 2.3555e-05 | -0.0057171 | 0.00024131 | -0.00041345 | 1 | 0 | 0 | 1
SH-15-HH | Split-R | HP | 15 | High | High | 13.16 | 19485 | 0.7467 | 0.2351 | 0.03079 | 0.183 | 0.0958 | 0 | 100 | 2.7476 | -0.0651 | 0.00067033 | 0.0032289 | -5.1429e-06 | -0.00010297 | -2.1391 | 0.15614 | -0.001572 | -0.014268 | -1.8155e-06 | 0.00017384 | -1.8255 | 0.080166 | -0.000616 | -0.003625 | 0.0001481 | -0.00012139 | 25.1931 | -3.7122 | 0.024675 | 2.3828 | -0.015855 | 0.0045909 | 4.9876e-05 | 1.1803 | -0.22911 | 0.048793 | 8.486e-05 | 1.2129 | -0.27841 | 0.065382 | 0.00012897 | 1.2428 | -0.32502 | 0.082084 | 0.84333 | 0.18094 | -0.024534 | 0.81849 | 0.21402 | -0.032911 | 0.79646 | 0.24434 | -0.04136 | 1 | 1 | 1 | 8 | 3.08 | 14946 | 0.32353 | 0.30766 | 0.0052087 | -4.133e-05 | 0.010811 | 6.5888e-05 | -3.7511e-05 | 1.0925 | -0.0017511 | 0.00014986 | -0.012437 | 0.0001764 | -0.00015483 | 1 | 0 | 0 | 1
SH-16-CL | Split-TS | HP | 16 | Low | Carrier | 11.99 | 36438.8393 | 0.757 | 0.24112 | 0.03019 | 0.329 | 0.0512 | 0 | 125 | 3.9457 | -0.10243 | 0.0010325 | 0.0052339 | -4.9464e-06 | -0.00018389 | -2.6951 | 0.18033 | -0.0017674 | -0.021841 | -1.4732e-06 | 0.00025688 | -2.6725 | 0.11448 | -0.00094417 | -0.0084116 | 0.00014279 | -3.9141e-05 | 164.0915 | -5.2936 | 0.038449 | 0.29778 | 0.00044519 | -0.001435 | 0.012024 | 1.1751 | -0.7718 | 0.58469 | 0.012054 | 1.2015 | -0.80631 | 0.59278 | 0.012088 | 1.2257 | -0.83922 | 0.60148 | 0.9431 | 0.056902 | 1e-08 | 0.94656 | 0.053436 | 1e-08 | 0.93312 | 0.066882 | 1e-08 | 2 | 0.6 | 0.49257 | 8.8 | 3.7 | 32230 | 0.27109 | 0.16671 | 0.0096675 | -0.00010472 | 0.0074914 | 0.00011554 | 1.8949e-05 | 0.86245 | 0.0055091 | 0.00017596 | -0.0098178 | 0.00028531 | -0.00038879 | 19.4304 | -18.4304 | 1 | 8.3722
SH-16-CH | Split-TS | HP | 16 | High | Carrier | 12.07 | 35271.573 | 0.7537 | 0.243 | 0.03119 | 0.292 | 0.0899 | 0 | 125 | 3.8891 | -0.10186 | 0.0010365 | 0.0063506 | -7.9286e-06 | -0.00019624 | -2.697 | 0.17954 | -0.0017636 | -0.021156 | -7.1607e-06 | 0.00026064 | -2.6366 | 0.11588 | -0.0009625 | -0.010789 | 0.00015592 | -2.9688e-05 | 64.9727 | -3.1756 | 0.016595 | 1.0331 | -0.0093784 | 0.0096412 | 0.010694 | 1.2084 | -0.75112 | 0.53198 | 0.010751 | 1.2367 | -0.79087 | 0.54343 | 0.010816 | 1.2626 | -0.82888 | 0.55549 | 0.96132 | 0.038678 | 1e-08 | 0.92033 | 0.079669 | 1e-08 | 0.90578 | 0.094216 | 1e-08 | 2 | 0.6 | 0.49818 | 8.3 | 3.54 | 31263.1 | 0.28507 | 0.16671 | 0.0096675 | -0.00010472 | 0.0074914 | 0.00011554 | 1.8949e-05 | 0.86245 | 0.0055091 | 0.00017596 | -0.0098178 | 0.00028531 | -0.00038879 | 10.467 | -9.467 | 1 | 4.7868
SH-16-LL | Split-TS | HP | 16 | Low | Lennox | 11.77 | 48500 | 0.8 | 0.24815 | 0.03351 | 0.283 | 0.0584 | 0.02 | 55 | 0.16796 | 0.01112 | 0.00014344 | 0.0044063 | 3.5714e-08 | -0.00015331 | 1.6355 | 0.044455 | -0.00075219 | -0.013395 | -1.0798e-05 | 0.00017794 | 0.79394 | 4.875e-05 | -2.9375e-05 | -0.0026105 | 0.00014002 | -0.000107 | 51.2955 | -1.9528 | -0.0017183 | 0.3733 | -0.012056 | 0.025289 | -0.00064915 | 1.114 | -0.19999 | 0.086606 | -0.0010832 | 1.165 | -0.31549 | 0.1516 | 0.29509 | 0.9886 | 0.576 | -0.8597 | 0.92035 | 0.07965 | 1e-08 | 0.88478 | 0.11522 | 1e-08 | 0.85316 | 0.14684 | 1e-08 | 2 | 0.70154 | 0.70928 | 8.5 | 3.62 | 32400 | 0.2762 | 0.45209 | 0 | 0 | 0.010642 | 2.1602e-05 | 0 | 1.9994 | 0 | 0 | -0.036318 | 0.00032028 | 0 | 0.40588 | 0.59412 | 0.82268 | 1
SH-16-LM | Split-TS | HP | 16 | Median | Lennox | 12.06 | 36000 | 0.78 | 0.2361 | 0.03333 | 0.321 | 0.0991 | 0.02 | 55 | -0.55956 | 0.032939 | -3.1875e-05 | 0.0046798 | -8.5119e-06 | -0.000137 | 2.1895 | 0.02168 | -0.00056344 | -0.0084542 | -2.4321e-05 | 0.00014294 | 1.3605 | -0.025749 | 0.00025313 | 0.003116 | 0.00016812 | -0.000249 | 37.8292 | -1.3306 | -0.001402 | 0.18624 | -0.0080083 | 0.017718 | -0.0011802 | 1.321 | -0.61179 | 0.29198 | -0.0012638 | 1.3702 | -0.72532 | 0.35635 | -0.0012671 | 1.4137 | -0.82661 | 0.41416 | 0.78057 | 0.21943 | 1e-08 | 0.74732 | 0.25268 | 1e-08 | 0.71776 | 0.28224 | 1e-08 | 2 | 0.75 | 0.73889 | 8.4 | 3.48 | 33000 | 0.28731 | 0.4614 | 0 | 0 | 0.010763 | 1.4826e-05 | 0 | 2.0036 | 0 | 0 | -0.037453 | 0.00034253 | 0 | -1.17 | 2.17 | 0.45749 | 1
SH-16-LH | Split-TS | HP | 16 | High | Lennox | 12.59 | 37400 | 0.77 | 0.23054 | 0.03209 | 0.292 | 0.0879 | 0.02 | 55 | 0.85185 | -0.0027197 | 0.00021094 | 0.00086534 | 2.8452e-06 | -0.00011381 | 3.5837 | -0.01614 | -0.00029375 | -0.010281 | -1.5095e-05 | 0.000146 | 0.21032 | 0.0034163 | 4.6875e-05 | 0.0057396 | 0.00015613 | -0.000252 | -43.7856 | 0.39012 | -0.02138 | 0.76993 | -0.016402 | 0.029478 | -0.00085062 | 1.3754 | -0.66073 | 0.28614 | -0.00087402 | 1.4242 | -0.77599 | 0.35268 | -0.00080951 | 1.4671 | -0.87849 | 0.41222 | 0.7455 | 0.2545 | 1e-08 | 0.71226 | 0.28774 | 1e-08 | 0.68271 | 0.31729 | 1e-08 | 2 | 0.75 | 0.72193 | 8.9 | 3.58 | 32800 | 0.27928 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 1.9926 | 0 | 0 | -0.036405 | 0.00032525 | 0 | -1.5901 | 2.5901 | 0.35247 | 1
SH-16-TL | Split-TS | HP | 16 | Low | Trane | 11.06 | 36394.55 | 0.7664 | 0.2656 | 0.03297 | 0.292 | 0.1206 | 0 | 55 | 1.2155 | -0.027067 | 0.00044112 | 0.0087726 | -1.4983e-05 | -0.00016974 | -6.4568 | 0.30417 | -0.0028092 | -0.024422 | -8.1065e-07 | 0.00031655 | -4.8866 | 0.1094 | -0.00061871 | 0.043071 | 1.1458e-05 | -0.00044951 | -14.0461 | -0.9076 | 0.0071098 | 1.103 | -0.005455 | -0.0017518 | -0.00073664 | 0.89887 | -0.15673 | 0.25859 | -0.00060215 | 0.92835 | -0.2391 | 0.31135 | -0.00035112 | 0.95358 | -0.31072 | 0.35749 | 0.9013 | 0.098697 | 1e-08 | 0.85144 | 0.14856 | 1e-08 | 0.80713 | 0.19287 | 1e-08 | 2 | 0.5 | 0.48115 | 8.15 | 2.92 | 31900 | 0.34237 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 0.1475 | 0.8525 | 0.57375 | 1
SH-16-TM | Split-TS | HP | 16 | Median | Trane | 11.28 | 36394.55 | 0.7664 | 0.2599 | 0.03297 | 0.292 | 0.1206 | 0 | 55 | 1.4758 | -0.034476 | 0.00049536 | 0.0086758 | -1.4582e-05 | -0.00017003 | -6.4568 | 0.30417 | -0.0028092 | -0.024422 | -8.1065e-07 | 0.00031655 | -5.1682 | 0.11828 | -0.00069373 | 0.04261 | 9.3745e-06 | -0.00043595 | -14.0461 | -0.9076 | 0.0071098 | 1.103 | -0.005455 | -0.0017518 | -0.00062224 | 0.93144 | -0.15072 | 0.2199 | -0.00050859 | 0.96207 | -0.2361 | 0.27454 | -0.00027329 | 0.98831 | -0.31037 | 0.32233 | 0.9094 | 0.090604 | 1e-08 | 0.85953 | 0.14047 | 1e-08 | 0.81522 | 0.18478 | 1e-08 | 2 | 0.5 | 0.48115 | 8.2 | 2.94 | 31900 | 0.33595 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.2159 | 0.0073246 | 3.7571e-05 | -0.023236 | 0.00022478 | -9.6407e-05 | -0.014434 | 1.0144 | 0.49278 | 1
SH-16-TH | Split-TS | HP | 16 | High | Trane | 11.64 | 33094.55 | 0.8157 | 0.2465 | 0.03626 | 0.292 | 0.0974 | 0 | 55 | 2.7042 | -0.069696 | 0.00074578 | 0.0080602 | -1.5685e-05 | -0.00015813 | -7.6799 | 0.34198 | -0.0030869 | -0.025769 | 5.7976e-06 | 0.00031735 | -7.0828 | 0.16965 | -0.0010891 | 0.044963 | -3.0013e-07 | -0.00041854 | -137.6109 | -2.1155 | 0.018883 | 5.3812 | -0.030699 | -0.00717 | -0.0033745 | 1.1592 | -0.68913 | 0.5333 | -0.0031554 | 1.1966 | -0.79198 | 0.59851 | -0.0027955 | 1.2287 | -0.88154 | 0.6556 | 0.73743 | 0.26257 | 1e-08 | 0.69144 | 0.30856 | 1e-08 | 0.65058 | 0.34942 | 1e-08 | 2 | 0.54167 | 0.54867 | 8.25 | 3.14 | 27500 | 0.30283 | 0.32502 | 0.00035532 | -9.697e-06 | 0.018603 | 2.2135e-05 | -6.8571e-05 | 1.5833 | 0.0078304 | 6.4245e-05 | -0.038504 | 0.00041474 | -0.00016799 | 0.85172 | 0.14828 | 0.93204 | 1
SH-17-CM | Split-TS | HP | 17 | Median | Carrier | 12.62 | 36832.093 | 0.7543 | 0.228 | 0.02987 | 0.328 | 0.0481 | 0 | 125 | 3.8813 | -0.10161 | 0.0010342 | 0.0063481 | -7.8929e-06 | -0.00019606 | -2.6907 | 0.17917 | -0.0017598 | -0.021096 | -7.1875e-06 | 0.00026002 | -2.6323 | 0.11548 | -0.00095906 | -0.010732 | 0.0001561 | -2.97e-05 | 173.8433 | -5.609 | 0.041065 | 0.31142 | 0.0006437 | -0.0019436 | 0.011262 | 1.178 | -0.74032 | 0.55101 | 0.011293 | 1.2045 | -0.77484 | 0.55903 | 0.011332 | 1.2292 | -0.80892 | 0.56845 | 0.94692 | 0.053081 | 1e-08 | 0.94158 | 0.05842 | 1e-08 | 0.92794 | 0.072063 | 1e-08 | 2 | 0.6 | 0.4926 | 9.5 | 3.5 | 32530 | 0.28223 | 0.61532 | 0.0014468 | -5.6871e-05 | 0.0024021 | -0.00011813 | 0.00021584 | 0.99178 | -0.00091762 | 0.0001666 | -0.005442 | 0.00028275 | -0.00033821 | 19.8875 | -18.8875 | 1 | 8.555
SH-17-LM | Split-TS | HP | 17 | Median | Lennox | 12.75 | 36600 | 0.8 | 0.24473 | 0.03292 | 0.162 | 0.0418 | 0.02 | 55 | 0.80181 | -0.0097822 | 0.00030531 | 0.0070129 | -9.75e-06 | -0.00017206 | 2.1098 | 0.031466 | -0.00066656 | -0.013237 | -1.6738e-05 | 0.00018581 | -0.16672 | 0.022526 | -0.00016094 | -0.00052754 | 0.00014811 | -0.00014244 | 33.2253 | 0.074783 | 0.0018162 | -0.85321 | 0.0092707 | -0.0068031 | -0.001532 | 1.1339 | -0.32136 | 0.18901 | -0.0019452 | 1.1836 | -0.43518 | 0.25349 | -0.0022606 | 1.2277 | -0.53709 | 0.31161 | 0.90403 | 0.095967 | 1e-08 | 0.86845 | 0.13155 | 1e-08 | 0.83682 | 0.16318 | 1e-08 | 2 | 0.70124 | 0.70492 | 9 | 3.72 | 32800 | 0.26877 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 1.9663 | 0 | 0 | -0.035053 | 0.00030839 | 0 | 0.5979 | 0.4021 | 0.87987 | 1
SH-17-TL | Split-TS | HP | 17 | Low | Trane | 12.24 | 33094.55 | 0.8157 | 0.2327 | 0.03626 | 0.292 | 0.0974 | 0 | 55 | 2.1279 | -0.053092 | 0.00062879 | 0.0083418 | -1.4978e-05 | -0.00016506 | -7.757 | 0.34148 | -0.0030847 | -0.02395 | -4.1238e-06 | 0.00032013 | -6.61 | 0.15365 | -0.00095304 | 0.046299 | 1.8921e-06 | -0.00044329 | -137.6109 | -2.1155 | 0.018883 | 5.3812 | -0.030699 | -0.00717 | -0.0026034 | 1.1107 | -0.46443 | 0.35635 | -0.0026807 | 1.1504 | -0.57139 | 0.42369 | -0.0026026 | 1.1847 | -0.66493 | 0.48285 | 0.82363 | 0.17637 | 1e-08 | 0.77761 | 0.22239 | 1e-08 | 0.73672 | 0.26328 | 1e-08 | 2 | 0.54167 | 0.54262 | 8.75 | 3.24 | 29000 | 0.29893 | 0.33196 | 0.00023547 | -9.1954e-06 | 0.018417 | 2.1815e-05 | -6.601e-05 | 1.5515 | 0.0085936 | 6.0385e-05 | -0.038365 | 0.00041659 | -0.00017206 | 1.3122 | -0.31222 | 1 | 1.1431
SH-17-TH | Split-TS | HP | 17 | High | Trane | 12.52 | 33494.55 | 0.8059 | 0.2273 | 0.03583 | 0.292 | 0.1069 | 0 | 55 | 2.1181 | -0.052157 | 0.00062526 | 0.007946 | -1.1599e-05 | -0.00016978 | -7.6799 | 0.34198 | -0.0030869 | -0.025769 | 5.7976e-06 | 0.00031735 | -6.5641 | 0.15167 | -0.00094612 | 0.046671 | -3.1176e-06 | -0.00043308 | -139.0671 | -1.8894 | 0.015737 | 5.2181 | -0.030858 | -0.0044665 | -0.002257 | 1.1519 | -0.49486 | 0.34524 | -0.0022683 | 1.192 | -0.60347 | 0.41375 | -0.0021237 | 1.2266 | -0.69836 | 0.4739 | 0.80667 | 0.19333 | 1e-08 | 0.76066 | 0.23934 | 1e-08 | 0.71977 | 0.28023 | 1e-08 | 2 | 0.54167 | 0.54211 | 8.55 | 3.26 | 28700 | 0.29849 | 0.42749 | -0.0024382 | 9.2915e-06 | 0.018525 | 2.1765e-05 | -6.7198e-05 | 1.3028 | 0.015594 | 1.2226e-05 | -0.038766 | 0.00041655 | -0.0001679 | 0.85254 | 0.14746 | 0.93241 | 1
SH-18-LL | Split-TS | HP | 18 | Low | Lennox | 12.8 | 36400 | 0.78 | 0.2335 | 0.03365 | 0.224 | 0.1077 | 0.02 | 55 | -0.35565 | 0.028179 | 2.8125e-06 | 0.0039044 | -4.6429e-06 | -0.00013731 | 2.3156 | 0.020931 | -0.000565 | -0.010609 | -1.6893e-05 | 0.00015375 | 1.4171 | -0.02954 | 0.00027281 | 0.0044561 | 0.00015918 | -0.00023919 | 0.19272 | -0.34386 | -0.0066304 | 0.28252 | -0.0072998 | 0.014501 | -0.00089339 | 1.1828 | -0.33862 | 0.15673 | -0.0011684 | 1.2331 | -0.45211 | 0.22018 | -0.0013616 | 1.2778 | -0.55396 | 0.27756 | 0.87711 | 0.12289 | 1e-08 | 0.84366 | 0.15634 | 1e-08 | 0.81366 | 0.18634 | 1e-08 | 2 | 0.71429 | 0.72527 | 9.2 | 3.66 | 32600 | 0.27063 | 0.45795 | 0 | 0 | 0.010708 | 1.7545e-05 | 0 | 1.9701 | 0 | 0 | -0.035421 | 0.00031449 | 0 | -0.93456 | 1.9346 | 0.44727 | 1
SH-18-LM | Split-TS | HP | 18 | Median | Lennox | 12.88 | 37400 | 0.8 | 0.22694 | 0.0357 | 0.247 | 0.1162 | 0.02 | 55 | 0.21502 | 0.012111 | 0.0001175 | 0.0033447 | -8.4524e-07 | -0.00013575 | 1.6786 | 0.040412 | -0.00071281 | -0.012574 | -1.3786e-05 | 0.00017794 | 0.059441 | 0.008185 | -6.25e-06 | 0.0056626 | 0.00014635 | -0.000226 | 19.1517 | -0.6044 | -0.0066025 | 0.036281 | -0.0066582 | 0.017107 | -0.00091025 | 1.1402 | -0.26717 | 0.1279 | -0.0013101 | 1.1935 | -0.38789 | 0.19573 | -0.0016103 | 1.2408 | -0.49612 | 0.25698 | 0.90212 | 0.097876 | 1e-08 | 0.86511 | 0.13489 | 1e-08 | 0.83221 | 0.16779 | 1e-08 | 2 | 0.67416 | 0.71658 | 8.45 | 3.32 | 32000 | 0.3012 | 0.46708 | 0 | 0 | 0.010842 | 1.0559e-05 | 0 | 1.9287 | 0 | 0 | -0.034642 | 0.00031664 | 0 | -1.0611 | 2.0611 | 0.3284 | 1
SH-18-LH | Split-TS | HP | 18 | High | Lennox | 13.17 | 38500 | 0.8 | 0.22458 | 0.03468 | 0.232 | 0.0902 | 0.02 | 55 | -0.58937 | 0.03541 | -5.4375e-05 | 0.0043569 | -3.5e-06 | -0.00014475 | 2.7171 | 0.012407 | -0.00054563 | -0.014338 | -2.5881e-05 | 0.00023513 | 1.1205 | -0.024397 | 0.00023719 | 0.0058565 | 0.00014555 | -0.00022319 | -26.0773 | 0.57406 | -0.0227 | 0.18998 | -0.012255 | 0.028684 | 0.29419 | 0.93571 | 0.73332 | -0.96321 | -0.00077645 | 1.1851 | -0.30463 | 0.12032 | -0.0011318 | 1.2325 | -0.41452 | 0.18312 | 0.91002 | 0.089983 | 1e-08 | 0.87279 | 0.12721 | 1e-08 | 0.83971 | 0.16029 | 1e-08 | 2 | 0.67041 | 0.7013 | 8.75 | 3.5 | 32800 | 0.28573 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 2.0078 | 0 | 0 | -0.037186 | 0.00033499 | 0 | -0.40968 | 1.4097 | 0.53539 | 1
SH-18-TM | Split-TS | HP | 18 | Median | Trane | 12.63 | 34896.94 | 0.8481 | 0.223 | 0.03725 | 0.292 | 0.0565 | 0 | 55 | -0.067816 | 0.017322 | 8.476e-05 | 0.0042129 | -8.007e-06 | -0.00012587 | -7.7578 | 0.34261 | -0.0030927 | -0.024665 | 1.2002e-07 | 0.00031865 | -4.954 | 0.084947 | -0.00030507 | 0.06034 | 6.6865e-07 | -0.00064513 | -238.8103 | -1.8825 | 0.031646 | 7.7742 | -0.034563 | -0.032994 | -0.0012815 | 1.0497 | -0.54531 | 0.49684 | -0.00077571 | 1.078 | -0.62666 | 0.54944 | -0.0001757 | 1.102 | -0.69709 | 0.59526 | 0.72831 | 0.27169 | 1e-08 | 0.68206 | 0.31794 | 1e-08 | 0.64098 | 0.35902 | 1e-08 | 2 | 0.53846 | 0.50652 | 8.3 | 3.38 | 29570 | 0.29317 | 0.37531 | -0.00104 | -2.6364e-14 | 0.018576 | 2.2225e-05 | -6.8288e-05 | 1.4724 | 0.011061 | 4.1102e-05 | -0.038822 | 0.00041493 | -0.00016416 | 3.0974 | -2.0974 | 1 | 1.968

## DOEresults (hidden)
0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Sys1
| Nominal |  |  |  |  | Effective | Peak | Cooling | Heating |  | Cool + Heat
RunID | SEER | CZ | Vintage | Key 1 | Key 2 | SEER | kW | kWh | kWh | tons | kWh | Alternative
DEER-SFAM-CZ01-V1-eSA-10-HH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-HH | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.7083 | SA-10-HH
DEER-SFAM-CZ01-V1-eSA-10-HL-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-HL | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.8882 | SA-10-HL
DEER-SFAM-CZ01-V1-eSA-10-HM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-HM | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.8559 | SA-10-HM
DEER-SFAM-CZ01-V1-eSA-10-LH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-LH | 0 | 0 | 0 | 0 | 3.711 | 0 | 262.0683 | SA-10-LH
DEER-SFAM-CZ01-V1-eSA-10-LL-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-LL | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.9304 | SA-10-LL
DEER-SFAM-CZ01-V1-eSA-10-LM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-LM | 0 | 0 | 0 | 0 | 3.711 | 0 | 262.0763 | SA-10-LM
DEER-SFAM-CZ01-V1-eSA-10-MH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-MH | 0 | 0 | 0 | 0 | 3.711 | 0 | 262.0056 | SA-10-MH
DEER-SFAM-CZ01-V1-eSA-10-ML-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-ML | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.8929 | SA-10-ML
DEER-SFAM-CZ01-V1-eSA-10-MM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSA-10 | CZ01-V1-eSA-10-MM | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.9119 | SA-10-MM
DEER-SFAM-CZ01-V1-eSA-13-HH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-HH | 0 | 0 | 0 | 0 | 3.711 | 0 | 236.0662 | SA-13-HH
DEER-SFAM-CZ01-V1-eSA-13-HL-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-HL | 0 | 0 | 0 | 0 | 3.711 | 0 | 206.6055 | SA-13-HL
DEER-SFAM-CZ01-V1-eSA-13-HM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-HM | 0 | 0 | 0 | 0 | 3.711 | 0 | 235.9965 | SA-13-HM
DEER-SFAM-CZ01-V1-eSA-13-LH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-LH | 0 | 0 | 0 | 0 | 3.4688 | 0 | 261.8525 | SA-13-LH
DEER-SFAM-CZ01-V1-eSA-13-LL-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-LL | 0 | 0 | 0 | 0 | 3.4688 | 0 | 261.3981 | SA-13-LL
DEER-SFAM-CZ01-V1-eSA-13-LM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-LM | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.7625 | SA-13-LM
DEER-SFAM-CZ01-V1-eSA-13-MH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-MH | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.8569 | SA-13-MH
DEER-SFAM-CZ01-V1-eSA-13-ML-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-ML | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.0615 | SA-13-ML
DEER-SFAM-CZ01-V1-eSA-13-MM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSA-13 | CZ01-V1-eSA-13-MM | 0 | 0 | 0 | 0 | 3.711 | 0 | 261.8257 | SA-13-MM
DEER-SFAM-CZ01-V1-eSA-14-HH-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-HH | 0 | 0 | 0 | 0 | 3.711 | 0 | 219.4669 | SA-14-HH
DEER-SFAM-CZ01-V1-eSA-14-HL-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-HL | 0 | 0 | 0 | 0 | 3.711 | 0 | 161.3766 | SA-14-HL
DEER-SFAM-CZ01-V1-eSA-14-HM-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-HM | 0 | 0 | 0 | 0 | 3.711 | 0 | 247.5811 | SA-14-HM
DEER-SFAM-CZ01-V1-eSA-14-MH-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-MH | 0 | 0 | 0 | 0 | 3.4688 | 0 | 171.9931 | SA-14-MH
DEER-SFAM-CZ01-V1-eSA-14-ML-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-ML | 0 | 0 | 0 | 0 | 3.711 | 0 | 274.7828 | SA-14-ML
DEER-SFAM-CZ01-V1-eSA-14-MM-s1 | 14 | CZ01 | V1 | CZ01-V1-eSA-14 | CZ01-V1-eSA-14-MM | 0 | 0 | 0 | 0 | 3.4688 | 0 | 188.558 | SA-14-MM
DEER-SFAM-CZ01-V1-eSA-15-HH-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-HH | 0 | 0 | 0 | 0 | 3.711 | 0 | 182.9461 | SA-15-HH
DEER-SFAM-CZ01-V1-eSA-15-HL-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-HL | 0 | 0 | 0 | 0 | 3.711 | 0 | 228.0348 | SA-15-HL
DEER-SFAM-CZ01-V1-eSA-15-HM-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-HM | 0 | 0 | 0 | 0 | 3.711 | 0 | 183.6276 | SA-15-HM
DEER-SFAM-CZ01-V1-eSA-15-MH-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-MH | 0 | 0 | 0 | 0 | 3.711 | 0 | 136.3153 | SA-15-MH
DEER-SFAM-CZ01-V1-eSA-15-ML-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-ML | 0 | 0 | 0 | 0 | 3.711 | 0 | 183.3638 | SA-15-ML
DEER-SFAM-CZ01-V1-eSA-15-MM-s1 | 15 | CZ01 | V1 | CZ01-V1-eSA-15 | CZ01-V1-eSA-15-MM | 0 | 0 | 0 | 0 | 3.711 | 0 | 167.1544 | SA-15-MM
DEER-SFAM-CZ01-V1-eSA-16-CH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-CH | 0 | 0 | 0 | 0 | 3.9688 | 0 | 103.9827 | SA-16-CH
DEER-SFAM-CZ01-V1-eSA-16-CL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-CL | 0 | 0 | 0 | 0 | 3.9688 | 0 | 132.1616 | SA-16-CL
DEER-SFAM-CZ01-V1-eSA-16-CM-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-CM | 0 | 0 | 0 | 0 | 3.9688 | 0 | 139.5096 | SA-16-CM
DEER-SFAM-CZ01-V1-eSA-16-LH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-LH | 0 | 0 | 0 | 0 | 3.711 | 0 | 179.1835 | SA-16-LH
DEER-SFAM-CZ01-V1-eSA-16-LL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-LL | 0 | 0 | 0 | 0 | 3.711 | 0 | 117.8589 | SA-16-LL
DEER-SFAM-CZ01-V1-eSA-16-LM-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-LM | 0 | 0 | 0 | 0 | 3.711 | 0 | 106.8237 | SA-16-LM
DEER-SFAM-CZ01-V1-eSA-16-NM-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-NM | 0 | 0 | 0 | 0 | 3.711 | 0 | 104.7303 | SA-16-NM
DEER-SFAM-CZ01-V1-eSA-16-TH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-TH | 0 | 0 | 0 | 0 | 3.711 | 0 | 66.1883 | SA-16-TH
DEER-SFAM-CZ01-V1-eSA-16-TL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSA-16 | CZ01-V1-eSA-16-TL | 0 | 0 | 0 | 0 | 3.711 | 0 | 71.722 | SA-16-TL
DEER-SFAM-CZ01-V1-eSA-17-CH-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-CH | 0 | 0 | 0 | 0 | 3.9688 | 0 | 132.1052 | SA-17-CH
DEER-SFAM-CZ01-V1-eSA-17-CL-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-CL | 0 | 0 | 0 | 0 | 3.9688 | 0 | 132.0744 | SA-17-CL
DEER-SFAM-CZ01-V1-eSA-17-CM-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-CM | 0 | 0 | 0 | 0 | 3.9688 | 0 | 103.6702 | SA-17-CM
DEER-SFAM-CZ01-V1-eSA-17-LH-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-LH | 0 | 0 | 0 | 0 | 3.711 | 0 | 140.4785 | SA-17-LH
DEER-SFAM-CZ01-V1-eSA-17-LL-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-LL | 0 | 0 | 0 | 0 | 3.711 | 0 | 76.6406 | SA-17-LL
DEER-SFAM-CZ01-V1-eSA-17-LM-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-LM | 0 | 0 | 0 | 0 | 3.711 | 0 | 66.1645 | SA-17-LM
DEER-SFAM-CZ01-V1-eSA-17-TH-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-TH | 0 | 0 | 0 | 0 | 3.711 | 0 | 106.2593 | SA-17-TH
DEER-SFAM-CZ01-V1-eSA-17-TL-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-TL | 0 | 0 | 0 | 0 | 3.711 | 0 | 166.9592 | SA-17-TL
DEER-SFAM-CZ01-V1-eSA-17-TM-s2 | 17 | CZ01 | V1 | CZ01-V1-eSA-17 | CZ01-V1-eSA-17-TM | 0 | 0 | 0 | 0 | 3.711 | 0 | 55.3103 | SA-17-TM
DEER-SFAM-CZ01-V1-eSA-18-LH-s2 | 18 | CZ01 | V1 | CZ01-V1-eSA-18 | CZ01-V1-eSA-18-LH | 0 | 0 | 0 | 0 | 3.711 | 0 | 92.1208 | SA-18-LH
DEER-SFAM-CZ01-V1-eSA-18-LL-s2 | 18 | CZ01 | V1 | CZ01-V1-eSA-18 | CZ01-V1-eSA-18-LL | 0 | 0 | 0 | 0 | 3.711 | 0 | 120.1993 | SA-18-LL
DEER-SFAM-CZ01-V1-eSA-18-TH-s2 | 18 | CZ01 | V1 | CZ01-V1-eSA-18 | CZ01-V1-eSA-18-TH | 0 | 0 | 0 | 0 | 3.711 | 0 | 72.3172 | SA-18-TH
DEER-SFAM-CZ01-V1-eSA-18-TL-s2 | 18 | CZ01 | V1 | CZ01-V1-eSA-18 | CZ01-V1-eSA-18-TL | 0 | 0 | 0 | 0 | 3.711 | 0 | 79.2287 | SA-18-TL
DEER-SFAM-CZ01-V1-eSA-18-TM-s2 | 18 | CZ01 | V1 | CZ01-V1-eSA-18 | CZ01-V1-eSA-18-TM | 0 | 0 | 0 | 0 | 3.711 | 0 | 73.841 | SA-18-TM
DEER-SFAM-CZ01-V1-eSH-10-HH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-HH | 0 | 0 | 0 | 5446.978 | 3.711 | 5446.978 | 563.1145 | SH-10-HH
DEER-SFAM-CZ01-V1-eSH-10-HL-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-HL | 0 | 0 | 0 | 5521.8982 | 3.711 | 5521.8982 | 559.7528 | SH-10-HL
DEER-SFAM-CZ01-V1-eSH-10-HM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-HM | 0 | 0 | 0 | 5284.2405 | 3.711 | 5284.2405 | 535.4863 | SH-10-HM
DEER-SFAM-CZ01-V1-eSH-10-LH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-LH | 0 | 0 | 0 | 5786.0083 | 3.4688 | 5786.0083 | 581.8862 | SH-10-LH
DEER-SFAM-CZ01-V1-eSH-10-LL-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-LL | 0 | 0 | 0 | 5530.3086 | 3.711 | 5530.3086 | 602.9458 | SH-10-LL
DEER-SFAM-CZ01-V1-eSH-10-LM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-LM | 0 | 0 | 0 | 5425.7 | 3.711 | 5425.7 | 551.6803 | SH-10-LM
DEER-SFAM-CZ01-V1-eSH-10-MH-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-MH | 0 | 0 | 0 | 5703.4572 | 3.711 | 5703.4572 | 618.3984 | SH-10-MH
DEER-SFAM-CZ01-V1-eSH-10-ML-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-ML | 0 | 0 | 0 | 5144.8253 | 3.711 | 5144.8253 | 552.9397 | SH-10-ML
DEER-SFAM-CZ01-V1-eSH-10-MM-s1 | 10 | CZ01 | V1 | CZ01-V1-eSH-10 | CZ01-V1-eSH-10-MM | 0 | 0 | 0 | 5523.5062 | 3.711 | 5523.5062 | 522.6031 | SH-10-MM
DEER-SFAM-CZ01-V1-eSH-13-HH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-HH | 0 | 0 | 0 | 5301.0367 | 3.711 | 5301.0367 | 513.0109 | SH-13-HH
DEER-SFAM-CZ01-V1-eSH-13-HL-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-HL | 0 | 0 | 0 | 4601.183 | 3.711 | 4601.183 | 510.41 | SH-13-HL
DEER-SFAM-CZ01-V1-eSH-13-HM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-HM | 0 | 0 | 0 | 4707.1569 | 3.711 | 4707.1569 | 461.5312 | SH-13-HM
DEER-SFAM-CZ01-V1-eSH-13-LH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-LH | 0 | 0 | 0 | 5754.6455 | 3.4688 | 5754.6455 | 772.8227 | SH-13-LH
DEER-SFAM-CZ01-V1-eSH-13-LL-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-LL | 0 | 0 | 0 | 4884.8519 | 3.711 | 4884.8519 | 467.7503 | SH-13-LL
DEER-SFAM-CZ01-V1-eSH-13-LM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-LM | 0 | 0 | 0 | 4256.9184 | 3.711 | 4256.9184 | 535.8571 | SH-13-LM
DEER-SFAM-CZ01-V1-eSH-13-MH-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-MH | 0 | 0 | 0 | 5365.6612 | 3.711 | 5365.6612 | 518.0341 | SH-13-MH
DEER-SFAM-CZ01-V1-eSH-13-ML-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-ML | 0 | 0 | 0 | 5087.4522 | 3.711 | 5087.4522 | 532.1159 | SH-13-ML
DEER-SFAM-CZ01-V1-eSH-13-MM-s1 | 13 | CZ01 | V1 | CZ01-V1-eSH-13 | CZ01-V1-eSH-13-MM | 0 | 0 | 0 | 4960.154 | 3.711 | 4960.154 | 413.1442 | SH-13-MM
DEER-SFAM-CZ01-V1-eSH-14-HH-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-HH | 0 | 0 | 0 | 4847.4784 | 3.711 | 4847.4784 | 390.4385 | SH-14-HH
DEER-SFAM-CZ01-V1-eSH-14-HL-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-HL | 0 | 0 | 0 | 4840.3748 | 3.711 | 4840.3748 | 471.1878 | SH-14-HL
DEER-SFAM-CZ01-V1-eSH-14-HM-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-HM | 0 | 0 | 0 | 4753.5819 | 3.711 | 4753.5819 | 333.3473 | SH-14-HM
DEER-SFAM-CZ01-V1-eSH-14-MH-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-MH | 0 | 0 | 0 | 5200.8211 | 3.4688 | 5200.8211 | 507.4994 | SH-14-MH
DEER-SFAM-CZ01-V1-eSH-14-ML-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-ML | 0 | 0 | 0 | 5485.4508 | 3.711 | 5485.4508 | 643.0844 | SH-14-ML
DEER-SFAM-CZ01-V1-eSH-14-MM-s1 | 14 | CZ01 | V1 | CZ01-V1-eSH-14 | CZ01-V1-eSH-14-MM | 0 | 0 | 0 | 4762.76 | 3.4688 | 4762.76 | 443.1663 | SH-14-MM
DEER-SFAM-CZ01-V1-eSH-15-HH-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-HH | 0 | 0 | 0 | 5775.7629 | 3.711 | 5775.7629 | 364.1183 | SH-15-HH
DEER-SFAM-CZ01-V1-eSH-15-HL-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-HL | 0 | 0 | 0 | 4113.4366 | 3.711 | 4113.4366 | 360.1962 | SH-15-HL
DEER-SFAM-CZ01-V1-eSH-15-HM-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-HM | 0 | 0 | 0 | 4285.6309 | 3.711 | 4285.6309 | 361.3358 | SH-15-HM
DEER-SFAM-CZ01-V1-eSH-15-MH-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-MH | 0 | 0 | 0 | 5140.4346 | 3.711 | 5140.4346 | 351.0367 | SH-15-MH
DEER-SFAM-CZ01-V1-eSH-15-ML-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-ML | 0 | 0 | 0 | 4774.0627 | 3.711 | 4774.0627 | 362.4633 | SH-15-ML
DEER-SFAM-CZ01-V1-eSH-15-MM-s1 | 15 | CZ01 | V1 | CZ01-V1-eSH-15 | CZ01-V1-eSH-15-MM | 0 | 0 | 0 | 4989.6837 | 3.711 | 4989.6837 | 380.8086 | SH-15-MM
DEER-SFAM-CZ01-V1-eSH-16-CH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-CH | 0 | 0 | 0 | 5218.3156 | 3.9688 | 5218.3156 | 322.9699 | SH-16-CH
DEER-SFAM-CZ01-V1-eSH-16-CL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-CL | 0 | 0 | 0 | 4859.5842 | 3.9688 | 4859.5842 | 334.2557 | SH-16-CL
DEER-SFAM-CZ01-V1-eSH-16-LH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-LH | 0 | 0 | 0 | 5587.78 | 3.711 | 5587.78 | 375.6906 | SH-16-LH
DEER-SFAM-CZ01-V1-eSH-16-LL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-LL | 0 | 0 | 0 | 5164.8512 | 3.711 | 5164.8512 | 302.4446 | SH-16-LL
DEER-SFAM-CZ01-V1-eSH-16-LM-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-LM | 0 | 0 | 0 | 5626.0222 | 3.711 | 5626.0222 | 420.8552 | SH-16-LM
DEER-SFAM-CZ01-V1-eSH-16-TH-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-TH | 0 | 0 | 0 | 6401.3799 | 3.711 | 6401.3799 | 347.4425 | SH-16-TH
DEER-SFAM-CZ01-V1-eSH-16-TL-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-TL | 0 | 0 | 0 | 6436.6132 | 3.711 | 6436.6132 | 320.9188 | SH-16-TL
DEER-SFAM-CZ01-V1-eSH-16-TM-s2 | 16 | CZ01 | V1 | CZ01-V1-eSH-16 | CZ01-V1-eSH-16-TM | 0 | 0 | 0 | 6514.2148 | 3.711 | 6514.2148 | 329.4728 | SH-16-TM
DEER-SFAM-CZ01-V1-eSH-17-CM-s2 | 17 | CZ01 | V1 | CZ01-V1-eSH-17 | CZ01-V1-eSH-17-CM | 0 | 0 | 0 | 5477.6866 | 3.9688 | 5477.6866 | 386.6459 | SH-17-CM
DEER-SFAM-CZ01-V1-eSH-17-LM-s2 | 17 | CZ01 | V1 | CZ01-V1-eSH-17 | CZ01-V1-eSH-17-LM | 0 | 0 | 0 | 5008.3679 | 3.711 | 5008.3679 | 170.0786 | SH-17-LM
DEER-SFAM-CZ01-V1-eSH-17-TH-s2 | 17 | CZ01 | V1 | CZ01-V1-eSH-17 | CZ01-V1-eSH-17-TH | 0 | 0 | 0 | 6375.0368 | 3.711 | 6375.0368 | 372.7476 | SH-17-TH
DEER-SFAM-CZ01-V1-eSH-17-TL-s2 | 17 | CZ01 | V1 | CZ01-V1-eSH-17 | CZ01-V1-eSH-17-TL | 0 | 0 | 0 | 6351.1474 | 3.711 | 6351.1474 | 368.0151 | SH-17-TL
DEER-SFAM-CZ01-V1-eSH-18-LH-s2 | 18 | CZ01 | V1 | CZ01-V1-eSH-18 | CZ01-V1-eSH-18-LH | 0 | 0 | 0 | 5770.9451 | 3.711 | 5770.9451 | 286.3085 | SH-18-LH
DEER-SFAM-CZ01-V1-eSH-18-LL-s2 | 18 | CZ01 | V1 | CZ01-V1-eSH-18 | CZ01-V1-eSH-18-LL | 0 | 0 | 0 | 5204.2586 | 3.711 | 5204.2586 | 262.4296 | SH-18-LL
DEER-SFAM-CZ01-V1-eSH-18-LM-s2 | 18 | CZ01 | V1 | CZ01-V1-eSH-18 | CZ01-V1-eSH-18-LM | 0 | 0 | 0 | 6064.853 | 3.711 | 6064.853 | 329.2858 | SH-18-LM
DEER-SFAM-CZ01-V1-eSH-18-TM-s2 | 18 | CZ01 | V1 | CZ01-V1-eSH-18 | CZ01-V1-eSH-18-TM | 0 | 0 | 0 | 6310.8655 | 3.711 | 6310.8655 | 543.4529 | SH-18-TM
DEER-SFAM-CZ01-V2-eSA-10-HH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-HH | 0 | 0 | 0 | 0 | 3.1141 | 0 | 153.6536
DEER-SFAM-CZ01-V2-eSA-10-HL-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-HL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7834
DEER-SFAM-CZ01-V2-eSA-10-HM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-HM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7673
DEER-SFAM-CZ01-V2-eSA-10-LH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-LH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.8736
DEER-SFAM-CZ01-V2-eSA-10-LL-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-LL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.8048
DEER-SFAM-CZ01-V2-eSA-10-LM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-LM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.8778
DEER-SFAM-CZ01-V2-eSA-10-MH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-MH | 0 | 0 | 0 | 0 | 3.1141 | 0 | 153.81
DEER-SFAM-CZ01-V2-eSA-10-ML-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-ML | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7855
DEER-SFAM-CZ01-V2-eSA-10-MM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSA-10 | CZ01-V2-eSA-10-MM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7953
DEER-SFAM-CZ01-V2-eSA-13-HH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-HH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 138.6222
DEER-SFAM-CZ01-V2-eSA-13-HL-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-HL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 121.3286
DEER-SFAM-CZ01-V2-eSA-13-HM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-HM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 138.5872
DEER-SFAM-CZ01-V2-eSA-13-LH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-LH | 0 | 0 | 0 | 0 | 3.1141 | 0 | 153.777
DEER-SFAM-CZ01-V2-eSA-13-LL-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-LL | 0 | 0 | 0 | 0 | 3.1141 | 0 | 153.5525
DEER-SFAM-CZ01-V2-eSA-13-LM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-LM | 0 | 0 | 0 | 0 | 3.1141 | 0 | 153.6823
DEER-SFAM-CZ01-V2-eSA-13-MH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-MH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7675
DEER-SFAM-CZ01-V2-eSA-13-ML-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-ML | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.3074
DEER-SFAM-CZ01-V2-eSA-13-MM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSA-13 | CZ01-V2-eSA-13-MM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 153.7523
DEER-SFAM-CZ01-V2-eSA-14-HH-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-HH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 128.8843
DEER-SFAM-CZ01-V2-eSA-14-HL-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-HL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 94.7737
DEER-SFAM-CZ01-V2-eSA-14-HM-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-HM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 145.3798
DEER-SFAM-CZ01-V2-eSA-14-MH-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-MH | 0 | 0 | 0 | 0 | 3.1141 | 0 | 101.0279
DEER-SFAM-CZ01-V2-eSA-14-ML-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-ML | 0 | 0 | 0 | 0 | 3.2676 | 0 | 161.3559
DEER-SFAM-CZ01-V2-eSA-14-MM-s1 | 14 | CZ01 | V2 | CZ01-V2-eSA-14 | CZ01-V2-eSA-14-MM | 0 | 0 | 0 | 0 | 3.1141 | 0 | 110.7492
DEER-SFAM-CZ01-V2-eSA-15-HH-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-HH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 107.4351
DEER-SFAM-CZ01-V2-eSA-15-HL-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-HL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 133.9186
DEER-SFAM-CZ01-V2-eSA-15-HM-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-HM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 107.8381
DEER-SFAM-CZ01-V2-eSA-15-MH-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-MH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 80.0536
DEER-SFAM-CZ01-V2-eSA-15-ML-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-ML | 0 | 0 | 0 | 0 | 3.1141 | 0 | 107.676
DEER-SFAM-CZ01-V2-eSA-15-MM-s1 | 15 | CZ01 | V2 | CZ01-V2-eSA-15 | CZ01-V2-eSA-15-MM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 98.163
DEER-SFAM-CZ01-V2-eSA-16-CH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-CH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 62.1802
DEER-SFAM-CZ01-V2-eSA-16-CL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-CL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 78.7163
DEER-SFAM-CZ01-V2-eSA-16-CM-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-CM | 0 | 0 | 0 | 0 | 3.6141 | 0 | 83.1618
DEER-SFAM-CZ01-V2-eSA-16-LH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-LH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 106.5081
DEER-SFAM-CZ01-V2-eSA-16-LL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-LL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 69.852
DEER-SFAM-CZ01-V2-eSA-16-LM-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-LM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 63.3109
DEER-SFAM-CZ01-V2-eSA-16-NM-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-NM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 62.2087
DEER-SFAM-CZ01-V2-eSA-16-TH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-TH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 39.862
DEER-SFAM-CZ01-V2-eSA-16-TL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSA-16 | CZ01-V2-eSA-16-TL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 42.9452
DEER-SFAM-CZ01-V2-eSA-17-CH-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-CH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 78.6986
DEER-SFAM-CZ01-V2-eSA-17-CL-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-CL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 78.6787
DEER-SFAM-CZ01-V2-eSA-17-CM-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-CM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 61.992
DEER-SFAM-CZ01-V2-eSA-17-LH-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-LH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 83.4456
DEER-SFAM-CZ01-V2-eSA-17-LL-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-LL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 45.2801
DEER-SFAM-CZ01-V2-eSA-17-LM-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-LM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 39.1699
DEER-SFAM-CZ01-V2-eSA-17-TH-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-TH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 63.7238
DEER-SFAM-CZ01-V2-eSA-17-TL-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-TL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 99.907
DEER-SFAM-CZ01-V2-eSA-17-TM-s2 | 17 | CZ01 | V2 | CZ01-V2-eSA-17 | CZ01-V2-eSA-17-TM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 33.0604
DEER-SFAM-CZ01-V2-eSA-18-LH-s2 | 18 | CZ01 | V2 | CZ01-V2-eSA-18 | CZ01-V2-eSA-18-LH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 54.5975
DEER-SFAM-CZ01-V2-eSA-18-LL-s2 | 18 | CZ01 | V2 | CZ01-V2-eSA-18 | CZ01-V2-eSA-18-LL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 71.3124
DEER-SFAM-CZ01-V2-eSA-18-TH-s2 | 18 | CZ01 | V2 | CZ01-V2-eSA-18 | CZ01-V2-eSA-18-TH | 0 | 0 | 0 | 0 | 3.2676 | 0 | 43.2633
DEER-SFAM-CZ01-V2-eSA-18-TL-s2 | 18 | CZ01 | V2 | CZ01-V2-eSA-18 | CZ01-V2-eSA-18-TL | 0 | 0 | 0 | 0 | 3.2676 | 0 | 47.6109
DEER-SFAM-CZ01-V2-eSA-18-TM-s2 | 18 | CZ01 | V2 | CZ01-V2-eSA-18 | CZ01-V2-eSA-18-TM | 0 | 0 | 0 | 0 | 3.2676 | 0 | 44.2487
DEER-SFAM-CZ01-V2-eSH-10-HH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-HH | 0 | 0 | 0 | 3173.8313 | 3.2676 | 3173.8313 | 326.1099
DEER-SFAM-CZ01-V2-eSH-10-HL-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-HL | 0 | 0 | 0 | 3210.2946 | 3.2676 | 3210.2946 | 324.0422
DEER-SFAM-CZ01-V2-eSH-10-HM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-HM | 0 | 0 | 0 | 3100.0329 | 3.2676 | 3100.0329 | 309.5607
DEER-SFAM-CZ01-V2-eSH-10-LH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-LH | 0 | 0 | 0 | 3340.547 | 3.1141 | 3340.547 | 337.2015
DEER-SFAM-CZ01-V2-eSH-10-LL-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-LL | 0 | 0 | 0 | 3176.6172 | 3.1141 | 3176.6172 | 349.279
DEER-SFAM-CZ01-V2-eSH-10-LM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-LM | 0 | 0 | 0 | 3159.1329 | 3.2676 | 3159.1329 | 320.096
DEER-SFAM-CZ01-V2-eSH-10-MH-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-MH | 0 | 0 | 0 | 3287.5036 | 3.1141 | 3287.5036 | 358.0497
DEER-SFAM-CZ01-V2-eSH-10-ML-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-ML | 0 | 0 | 0 | 2976.4225 | 3.2676 | 2976.4225 | 320.814
DEER-SFAM-CZ01-V2-eSH-10-MM-s1 | 10 | CZ01 | V2 | CZ01-V2-eSH-10 | CZ01-V2-eSH-10-MM | 0 | 0 | 0 | 3197.5534 | 3.1141 | 3197.5534 | 303.0954
DEER-SFAM-CZ01-V2-eSH-13-HH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-HH | 0 | 0 | 0 | 3039.7769 | 3.2676 | 3039.7769 | 297.7189
DEER-SFAM-CZ01-V2-eSH-13-HL-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-HL | 0 | 0 | 0 | 2626.034 | 3.2676 | 2626.034 | 295.7766
DEER-SFAM-CZ01-V2-eSH-13-HM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-HM | 0 | 0 | 0 | 2711.1101 | 3.2676 | 2711.1101 | 267.6398
DEER-SFAM-CZ01-V2-eSH-13-LH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-LH | 0 | 0 | 0 | 3155.3796 | 3.1141 | 3155.3796 | 449.3656
DEER-SFAM-CZ01-V2-eSH-13-LL-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-LL | 0 | 0 | 0 | 2765.8535 | 3.2676 | 2765.8535 | 271.41
DEER-SFAM-CZ01-V2-eSH-13-LM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-LM | 0 | 0 | 0 | 2447.2384 | 3.1141 | 2447.2384 | 310.4403
DEER-SFAM-CZ01-V2-eSH-13-MH-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-MH | 0 | 0 | 0 | 3069.1682 | 3.2676 | 3069.1682 | 300.4835
DEER-SFAM-CZ01-V2-eSH-13-ML-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-ML | 0 | 0 | 0 | 2854.0266 | 3.1141 | 2854.0266 | 307.6803
DEER-SFAM-CZ01-V2-eSH-13-MM-s1 | 13 | CZ01 | V2 | CZ01-V2-eSH-13 | CZ01-V2-eSH-13-MM | 0 | 0 | 0 | 2850.9777 | 3.1141 | 2850.9777 | 239.7383
DEER-SFAM-CZ01-V2-eSH-14-HH-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-HH | 0 | 0 | 0 | 2771.2882 | 3.2676 | 2771.2882 | 226.5446
DEER-SFAM-CZ01-V2-eSH-14-HL-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-HL | 0 | 0 | 0 | 2716.5881 | 3.2676 | 2716.5881 | 272.8996
DEER-SFAM-CZ01-V2-eSH-14-HM-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-HM | 0 | 0 | 0 | 2693.5458 | 3.2676 | 2693.5458 | 193.3825
DEER-SFAM-CZ01-V2-eSH-14-MH-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-MH | 0 | 0 | 0 | 2852.2968 | 3.1141 | 2852.2968 | 295.3675
DEER-SFAM-CZ01-V2-eSH-14-ML-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-ML | 0 | 0 | 0 | 2977.8839 | 3.2676 | 2977.8839 | 371.9998
DEER-SFAM-CZ01-V2-eSH-14-MM-s1 | 14 | CZ01 | V2 | CZ01-V2-eSH-14 | CZ01-V2-eSH-14-MM | 0 | 0 | 0 | 2639.7173 | 3.1141 | 2639.7173 | 256.9472
DEER-SFAM-CZ01-V2-eSH-15-HH-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-HH | 0 | 0 | 0 | 3192.7788 | 3.2676 | 3192.7788 | 212.1914
DEER-SFAM-CZ01-V2-eSH-15-HL-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-HL | 0 | 0 | 0 | 2345.611 | 3.2676 | 2345.611 | 208.6805
DEER-SFAM-CZ01-V2-eSH-15-HM-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-HM | 0 | 0 | 0 | 2436.0513 | 3.2676 | 2436.0513 | 209.0657
DEER-SFAM-CZ01-V2-eSH-15-MH-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-MH | 0 | 0 | 0 | 2816.8794 | 3.2676 | 2816.8794 | 202.836
DEER-SFAM-CZ01-V2-eSH-15-ML-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-ML | 0 | 0 | 0 | 2612.4243 | 3.2676 | 2612.4243 | 209.4276
DEER-SFAM-CZ01-V2-eSH-15-MM-s1 | 15 | CZ01 | V2 | CZ01-V2-eSH-15 | CZ01-V2-eSH-15-MM | 0 | 0 | 0 | 2775.7613 | 3.2676 | 2775.7613 | 221.2784
DEER-SFAM-CZ01-V2-eSH-16-CH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-CH | 0 | 0 | 0 | 2895.5642 | 3.2676 | 2895.5642 | 180.5591
DEER-SFAM-CZ01-V2-eSH-16-CL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-CL | 0 | 0 | 0 | 2685.0078 | 3.2676 | 2685.0078 | 187.7591
DEER-SFAM-CZ01-V2-eSH-16-LH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-LH | 0 | 0 | 0 | 3112.1906 | 3.2676 | 3112.1906 | 212.7218
DEER-SFAM-CZ01-V2-eSH-16-LL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-LL | 0 | 0 | 0 | 2807.0539 | 3.2676 | 2807.0539 | 170.1586
DEER-SFAM-CZ01-V2-eSH-16-LM-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-LM | 0 | 0 | 0 | 3112.6935 | 3.2676 | 3112.6935 | 237.8966
DEER-SFAM-CZ01-V2-eSH-16-TH-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-TH | 0 | 0 | 0 | 3647.6219 | 3.2676 | 3647.6219 | 181.8358
DEER-SFAM-CZ01-V2-eSH-16-TL-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-TL | 0 | 0 | 0 | 3595.4171 | 3.2676 | 3595.4171 | 162.8917
DEER-SFAM-CZ01-V2-eSH-16-TM-s2 | 16 | CZ01 | V2 | CZ01-V2-eSH-16 | CZ01-V2-eSH-16-TM | 0 | 0 | 0 | 3657.3553 | 3.2676 | 3657.3553 | 167.2762
DEER-SFAM-CZ01-V2-eSH-17-CM-s2 | 17 | CZ01 | V2 | CZ01-V2-eSH-17 | CZ01-V2-eSH-17-CM | 0 | 0 | 0 | 2987.3423 | 3.2676 | 2987.3423 | 212.6852
DEER-SFAM-CZ01-V2-eSH-17-LM-s2 | 17 | CZ01 | V2 | CZ01-V2-eSH-17 | CZ01-V2-eSH-17-LM | 0 | 0 | 0 | 2725.1183 | 3.2676 | 2725.1183 | 95.7314
DEER-SFAM-CZ01-V2-eSH-17-TH-s2 | 17 | CZ01 | V2 | CZ01-V2-eSH-17 | CZ01-V2-eSH-17-TH | 0 | 0 | 0 | 3640.7174 | 3.2676 | 3640.7174 | 195.151
DEER-SFAM-CZ01-V2-eSH-17-TL-s2 | 17 | CZ01 | V2 | CZ01-V2-eSH-17 | CZ01-V2-eSH-17-TL | 0 | 0 | 0 | 3603.5423 | 3.2676 | 3603.5423 | 192.7971
DEER-SFAM-CZ01-V2-eSH-18-LH-s2 | 18 | CZ01 | V2 | CZ01-V2-eSH-18 | CZ01-V2-eSH-18-LH | 0 | 0 | 0 | 3155.245 | 3.2676 | 3155.245 | 156.3313
DEER-SFAM-CZ01-V2-eSH-18-LL-s2 | 18 | CZ01 | V2 | CZ01-V2-eSH-18 | CZ01-V2-eSH-18-LL | 0 | 0 | 0 | 2813.4556 | 3.2676 | 2813.4556 | 147.0392
DEER-SFAM-CZ01-V2-eSH-18-LM-s2 | 18 | CZ01 | V2 | CZ01-V2-eSH-18 | CZ01-V2-eSH-18-LM | 0 | 0 | 0 | 3329.5405 | 3.2676 | 3329.5405 | 179.5816
DEER-SFAM-CZ01-V2-eSH-18-TM-s2 | 18 | CZ01 | V2 | CZ01-V2-eSH-18 | CZ01-V2-eSH-18-TM | 0 | 0 | 0 | 3589.7861 | 3.2676 | 3589.7861 | 286.9157
DEER-SFAM-CZ01-V3-eSA-10-HH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-HH | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.3024
DEER-SFAM-CZ01-V3-eSA-10-HL-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 160.5453
DEER-SFAM-CZ01-V3-eSA-10-HM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-HM | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.3904
DEER-SFAM-CZ01-V3-eSA-10-LH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-LH | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.5164
DEER-SFAM-CZ01-V3-eSA-10-LL-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 160.5658
DEER-SFAM-CZ01-V3-eSA-10-LM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-LM | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.5216
DEER-SFAM-CZ01-V3-eSA-10-MH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-MH | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.4797
DEER-SFAM-CZ01-V3-eSA-10-ML-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-ML | 0 | 0 | 0 | 0 | 3.9 | 0 | 160.5477
DEER-SFAM-CZ01-V3-eSA-10-MM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSA-10 | CZ01-V3-eSA-10-MM | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.4236
DEER-SFAM-CZ01-V3-eSA-13-HH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.7204
DEER-SFAM-CZ01-V3-eSA-13-HL-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 126.6695
DEER-SFAM-CZ01-V3-eSA-13-HM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.6847
DEER-SFAM-CZ01-V3-eSA-13-LH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-LH | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.4415
DEER-SFAM-CZ01-V3-eSA-13-LL-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-LL | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.1876
DEER-SFAM-CZ01-V3-eSA-13-LM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-LM | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.3349
DEER-SFAM-CZ01-V3-eSA-13-MH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-MH | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.3913
DEER-SFAM-CZ01-V3-eSA-13-ML-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-ML | 0 | 0 | 0 | 0 | 3.4 | 0 | 159.9051
DEER-SFAM-CZ01-V3-eSA-13-MM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSA-13 | CZ01-V3-eSA-13-MM | 0 | 0 | 0 | 0 | 3.4 | 0 | 160.3726
DEER-SFAM-CZ01-V3-eSA-14-HH-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-HH | 0 | 0 | 0 | 0 | 3.4 | 0 | 134.4376
DEER-SFAM-CZ01-V3-eSA-14-HL-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 98.9507
DEER-SFAM-CZ01-V3-eSA-14-HM-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-HM | 0 | 0 | 0 | 0 | 3.4 | 0 | 151.6491
DEER-SFAM-CZ01-V3-eSA-14-MH-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-MH | 0 | 0 | 0 | 0 | 3.4 | 0 | 105.409
DEER-SFAM-CZ01-V3-eSA-14-ML-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-ML | 0 | 0 | 0 | 0 | 3.4 | 0 | 168.3042
DEER-SFAM-CZ01-V3-eSA-14-MM-s1 | 14 | CZ01 | V3 | CZ01-V3-eSA-14 | CZ01-V3-eSA-14-MM | 0 | 0 | 0 | 0 | 3.4 | 0 | 115.5537
DEER-SFAM-CZ01-V3-eSA-15-HH-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 112.1676
DEER-SFAM-CZ01-V3-eSA-15-HL-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 139.8124
DEER-SFAM-CZ01-V3-eSA-15-HM-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 112.5887
DEER-SFAM-CZ01-V3-eSA-15-MH-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-MH | 0 | 0 | 0 | 0 | 3.4 | 0 | 83.5135
DEER-SFAM-CZ01-V3-eSA-15-ML-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-ML | 0 | 0 | 0 | 0 | 3.4 | 0 | 112.335
DEER-SFAM-CZ01-V3-eSA-15-MM-s1 | 15 | CZ01 | V3 | CZ01-V3-eSA-15 | CZ01-V3-eSA-15-MM | 0 | 0 | 0 | 0 | 3.4 | 0 | 102.4018
DEER-SFAM-CZ01-V3-eSA-16-CH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-CH | 0 | 0 | 0 | 0 | 3.9 | 0 | 64.5066
DEER-SFAM-CZ01-V3-eSA-16-CL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-CL | 0 | 0 | 0 | 0 | 3.9 | 0 | 81.5226
DEER-SFAM-CZ01-V3-eSA-16-CM-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-CM | 0 | 0 | 0 | 0 | 3.9 | 0 | 85.887
DEER-SFAM-CZ01-V3-eSA-16-LH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 111.1449
DEER-SFAM-CZ01-V3-eSA-16-LL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 72.8639
DEER-SFAM-CZ01-V3-eSA-16-LM-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-LM | 0 | 0 | 0 | 0 | 3.4 | 0 | 65.945
DEER-SFAM-CZ01-V3-eSA-16-NM-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-NM | 0 | 0 | 0 | 0 | 3.9 | 0 | 64.9006
DEER-SFAM-CZ01-V3-eSA-16-TH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-TH | 0 | 0 | 0 | 0 | 3.4 | 0 | 41.4642
DEER-SFAM-CZ01-V3-eSA-16-TL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSA-16 | CZ01-V3-eSA-16-TL | 0 | 0 | 0 | 0 | 3.9 | 0 | 44.7315
DEER-SFAM-CZ01-V3-eSA-17-CH-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-CH | 0 | 0 | 0 | 0 | 3.9 | 0 | 81.4997
DEER-SFAM-CZ01-V3-eSA-17-CL-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-CL | 0 | 0 | 0 | 0 | 3.9 | 0 | 81.4794
DEER-SFAM-CZ01-V3-eSA-17-CM-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-CM | 0 | 0 | 0 | 0 | 3.9 | 0 | 64.317
DEER-SFAM-CZ01-V3-eSA-17-LH-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-LH | 0 | 0 | 0 | 0 | 3.4 | 0 | 86.9984
DEER-SFAM-CZ01-V3-eSA-17-LL-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 47.1247
DEER-SFAM-CZ01-V3-eSA-17-LM-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-LM | 0 | 0 | 0 | 0 | 3.9 | 0 | 40.8242
DEER-SFAM-CZ01-V3-eSA-17-TH-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-TH | 0 | 0 | 0 | 0 | 3.9 | 0 | 66.4372
DEER-SFAM-CZ01-V3-eSA-17-TL-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-TL | 0 | 0 | 0 | 0 | 3.4 | 0 | 103.2081
DEER-SFAM-CZ01-V3-eSA-17-TM-s2 | 17 | CZ01 | V3 | CZ01-V3-eSA-17 | CZ01-V3-eSA-17-TM | 0 | 0 | 0 | 0 | 3.9 | 0 | 34.3207
DEER-SFAM-CZ01-V3-eSA-18-LH-s2 | 18 | CZ01 | V3 | CZ01-V3-eSA-18 | CZ01-V3-eSA-18-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 56.9323
DEER-SFAM-CZ01-V3-eSA-18-LL-s2 | 18 | CZ01 | V3 | CZ01-V3-eSA-18 | CZ01-V3-eSA-18-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 74.3918
DEER-SFAM-CZ01-V3-eSA-18-TH-s2 | 18 | CZ01 | V3 | CZ01-V3-eSA-18 | CZ01-V3-eSA-18-TH | 0 | 0 | 0 | 0 | 3.9 | 0 | 45.087
DEER-SFAM-CZ01-V3-eSA-18-TL-s2 | 18 | CZ01 | V3 | CZ01-V3-eSA-18 | CZ01-V3-eSA-18-TL | 0 | 0 | 0 | 0 | 3.75 | 0 | 49.511
DEER-SFAM-CZ01-V3-eSA-18-TM-s2 | 18 | CZ01 | V3 | CZ01-V3-eSA-18 | CZ01-V3-eSA-18-TM | 0 | 0 | 0 | 0 | 3.4 | 0 | 46.0583
DEER-SFAM-CZ01-V3-eSH-10-HH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-HH | 0 | 0 | 0 | 3201.412 | 3.9 | 3201.412 | 324.062
DEER-SFAM-CZ01-V3-eSH-10-HL-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-HL | 0 | 0 | 0 | 3236.1454 | 3.9 | 3236.1454 | 322.4454
DEER-SFAM-CZ01-V3-eSH-10-HM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-HM | 0 | 0 | 0 | 3154.2499 | 3.4 | 3154.2499 | 306.6499
DEER-SFAM-CZ01-V3-eSH-10-LH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-LH | 0 | 0 | 0 | 3335.079 | 3.4 | 3335.079 | 334.6789
DEER-SFAM-CZ01-V3-eSH-10-LL-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-LL | 0 | 0 | 0 | 3173.3888 | 3.4 | 3173.3888 | 346.4388
DEER-SFAM-CZ01-V3-eSH-10-LM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-LM | 0 | 0 | 0 | 3157.6555 | 3.4 | 3157.6555 | 318.8055
DEER-SFAM-CZ01-V3-eSH-10-MH-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-MH | 0 | 0 | 0 | 3276.9052 | 3.4 | 3276.9052 | 355.0052
DEER-SFAM-CZ01-V3-eSH-10-ML-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-ML | 0 | 0 | 0 | 3001.0561 | 3.9 | 3001.0561 | 319.6061
DEER-SFAM-CZ01-V3-eSH-10-MM-s1 | 10 | CZ01 | V3 | CZ01-V3-eSH-10 | CZ01-V3-eSH-10-MM | 0 | 0 | 0 | 3207.9546 | 3.4 | 3207.9546 | 302.6046
DEER-SFAM-CZ01-V3-eSH-13-HH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-HH | 0 | 0 | 0 | 3079.5604 | 3.75 | 3079.5604 | 295.8603
DEER-SFAM-CZ01-V3-eSH-13-HL-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-HL | 0 | 0 | 0 | 2650.5389 | 3.9 | 2650.5389 | 294.1389
DEER-SFAM-CZ01-V3-eSH-13-HM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-HM | 0 | 0 | 0 | 2753.7248 | 3.9 | 2753.7248 | 266.8248
DEER-SFAM-CZ01-V3-eSH-13-LH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-LH | 0 | 0 | 0 | 3095.0943 | 3.4 | 3095.0943 | 440.6443
DEER-SFAM-CZ01-V3-eSH-13-LL-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-LL | 0 | 0 | 0 | 2773.6382 | 3.9 | 2773.6382 | 269.7883
DEER-SFAM-CZ01-V3-eSH-13-LM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-LM | 0 | 0 | 0 | 2451.0351 | 3.4 | 2451.0351 | 309.4851
DEER-SFAM-CZ01-V3-eSH-13-MH-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-MH | 0 | 0 | 0 | 3077.1649 | 3.9 | 3077.1649 | 298.0649
DEER-SFAM-CZ01-V3-eSH-13-ML-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-ML | 0 | 0 | 0 | 2824.4569 | 3.4 | 2824.4569 | 304.6569
DEER-SFAM-CZ01-V3-eSH-13-MM-s1 | 13 | CZ01 | V3 | CZ01-V3-eSH-13 | CZ01-V3-eSH-13-MM | 0 | 0 | 0 | 2875.2897 | 3.4 | 2875.2897 | 239.7896
DEER-SFAM-CZ01-V3-eSH-14-HH-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-HH | 0 | 0 | 0 | 2812.4151 | 3.75 | 2812.4151 | 225.4152
DEER-SFAM-CZ01-V3-eSH-14-HL-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-HL | 0 | 0 | 0 | 2734.6651 | 3.9 | 2734.6651 | 270.265
DEER-SFAM-CZ01-V3-eSH-14-HM-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-HM | 0 | 0 | 0 | 2705.5759 | 3.4 | 2705.5759 | 192.076
DEER-SFAM-CZ01-V3-eSH-14-MH-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-MH | 0 | 0 | 0 | 2817.3187 | 3.4 | 2817.3187 | 291.6687
DEER-SFAM-CZ01-V3-eSH-14-ML-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-ML | 0 | 0 | 0 | 2891.5466 | 3.4 | 2891.5466 | 362.1966
DEER-SFAM-CZ01-V3-eSH-14-MM-s1 | 14 | CZ01 | V3 | CZ01-V3-eSH-14 | CZ01-V3-eSH-14-MM | 0 | 0 | 0 | 2632.3924 | 3.4 | 2632.3924 | 254.5423
DEER-SFAM-CZ01-V3-eSH-15-HH-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-HH | 0 | 0 | 0 | 3122.6701 | 3.9 | 3122.6701 | 208.2201
DEER-SFAM-CZ01-V3-eSH-15-HL-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-HL | 0 | 0 | 0 | 2381.7761 | 3.9 | 2381.7761 | 207.8761
DEER-SFAM-CZ01-V3-eSH-15-HM-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-HM | 0 | 0 | 0 | 2504.2124 | 3.9 | 2504.2124 | 206.8124
DEER-SFAM-CZ01-V3-eSH-15-MH-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-MH | 0 | 0 | 0 | 2748.5478 | 3.4 | 2748.5478 | 198.3978
DEER-SFAM-CZ01-V3-eSH-15-ML-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-ML | 0 | 0 | 0 | 2556.7519 | 3.4 | 2556.7519 | 205.052
DEER-SFAM-CZ01-V3-eSH-15-MM-s1 | 15 | CZ01 | V3 | CZ01-V3-eSH-15 | CZ01-V3-eSH-15-MM | 0 | 0 | 0 | 2763.9029 | 3.9 | 2763.9029 | 219.4529
DEER-SFAM-CZ01-V3-eSH-16-CH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-CH | 0 | 0 | 0 | 2651.3888 | 3.9 | 2651.3888 | 170.8388
DEER-SFAM-CZ01-V3-eSH-16-CL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-CL | 0 | 0 | 0 | 2478.6555 | 3.9 | 2478.6555 | 179.1055
DEER-SFAM-CZ01-V3-eSH-16-LH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-LH | 0 | 0 | 0 | 2907.4375 | 3.9 | 2907.4375 | 206.4375
DEER-SFAM-CZ01-V3-eSH-16-LL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-LL | 0 | 0 | 0 | 2622.8427 | 3.9 | 2622.8427 | 165.9927
DEER-SFAM-CZ01-V3-eSH-16-LM-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-LM | 0 | 0 | 0 | 2897.8079 | 3.9 | 2897.8079 | 230.6579
DEER-SFAM-CZ01-V3-eSH-16-TH-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-TH | 0 | 0 | 0 | 3277.6149 | 3.9 | 3277.6149 | 163.7149
DEER-SFAM-CZ01-V3-eSH-16-TL-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-TL | 0 | 0 | 0 | 3195.5475 | 3.9 | 3195.5475 | 146.3476
DEER-SFAM-CZ01-V3-eSH-16-TM-s2 | 16 | CZ01 | V3 | CZ01-V3-eSH-16 | CZ01-V3-eSH-16-TM | 0 | 0 | 0 | 3255.4436 | 3.9 | 3255.4436 | 149.8936
DEER-SFAM-CZ01-V3-eSH-17-CM-s2 | 17 | CZ01 | V3 | CZ01-V3-eSH-17 | CZ01-V3-eSH-17-CM | 0 | 0 | 0 | 2673.0024 | 3.9 | 2673.0024 | 197.7524
DEER-SFAM-CZ01-V3-eSH-17-LM-s2 | 17 | CZ01 | V3 | CZ01-V3-eSH-17 | CZ01-V3-eSH-17-LM | 0 | 0 | 0 | 2553.2656 | 3.9 | 2553.2656 | 93.4655
DEER-SFAM-CZ01-V3-eSH-17-TH-s2 | 17 | CZ01 | V3 | CZ01-V3-eSH-17 | CZ01-V3-eSH-17-TH | 0 | 0 | 0 | 3260.9246 | 3.9 | 3260.9246 | 175.1747
DEER-SFAM-CZ01-V3-eSH-17-TL-s2 | 17 | CZ01 | V3 | CZ01-V3-eSH-17 | CZ01-V3-eSH-17-TL | 0 | 0 | 0 | 3213.8958 | 3.9 | 3213.8958 | 172.8958
DEER-SFAM-CZ01-V3-eSH-18-LH-s2 | 18 | CZ01 | V3 | CZ01-V3-eSH-18 | CZ01-V3-eSH-18-LH | 0 | 0 | 0 | 2842.2396 | 3.9 | 2842.2396 | 148.0896
DEER-SFAM-CZ01-V3-eSH-18-LL-s2 | 18 | CZ01 | V3 | CZ01-V3-eSH-18 | CZ01-V3-eSH-18-LL | 0 | 0 | 0 | 2603.0883 | 3.9 | 2603.0883 | 142.6884
DEER-SFAM-CZ01-V3-eSH-18-LM-s2 | 18 | CZ01 | V3 | CZ01-V3-eSH-18 | CZ01-V3-eSH-18-LM | 0 | 0 | 0 | 2978.6669 | 3.9 | 2978.6669 | 168.367
DEER-SFAM-CZ01-V3-eSH-18-TM-s2 | 18 | CZ01 | V3 | CZ01-V3-eSH-18 | CZ01-V3-eSH-18-TM | 0 | 0 | 0 | 3173.7557 | 3.4 | 3173.7557 | 270.5057
DEER-SFAM-CZ01-V4-eSA-10-HH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 143.9413
DEER-SFAM-CZ01-V4-eSA-10-HL-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0245
DEER-SFAM-CZ01-V4-eSA-10-HM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0094
DEER-SFAM-CZ01-V4-eSA-10-LH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.1075
DEER-SFAM-CZ01-V4-eSA-10-LL-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0437
DEER-SFAM-CZ01-V4-eSA-10-LM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-LM | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.1104
DEER-SFAM-CZ01-V4-eSA-10-MH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-MH | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0786
DEER-SFAM-CZ01-V4-eSA-10-ML-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-ML | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0265
DEER-SFAM-CZ01-V4-eSA-10-MM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSA-10 | CZ01-V4-eSA-10-MM | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0353
DEER-SFAM-CZ01-V4-eSA-13-HH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 129.8281
DEER-SFAM-CZ01-V4-eSA-13-HL-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 113.6351
DEER-SFAM-CZ01-V4-eSA-13-HM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 129.7962
DEER-SFAM-CZ01-V4-eSA-13-LH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-LH | 0 | 0 | 0 | 0 | 3.4 | 0 | 143.9307
DEER-SFAM-CZ01-V4-eSA-13-LL-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 143.8514
DEER-SFAM-CZ01-V4-eSA-13-LM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-LM | 0 | 0 | 0 | 0 | 3.9 | 0 | 143.9666
DEER-SFAM-CZ01-V4-eSA-13-MH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-MH | 0 | 0 | 0 | 0 | 3.9 | 0 | 144.0097
DEER-SFAM-CZ01-V4-eSA-13-ML-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-ML | 0 | 0 | 0 | 0 | 3.9 | 0 | 143.5796
DEER-SFAM-CZ01-V4-eSA-13-MM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSA-13 | CZ01-V4-eSA-13-MM | 0 | 0 | 0 | 0 | 3.9 | 0 | 143.9955
DEER-SFAM-CZ01-V4-eSA-14-HH-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 120.7113
DEER-SFAM-CZ01-V4-eSA-14-HL-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 88.7684
DEER-SFAM-CZ01-V4-eSA-14-HM-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 136.1556
DEER-SFAM-CZ01-V4-eSA-14-MH-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-MH | 0 | 0 | 0 | 0 | 3.9 | 0 | 94.6505
DEER-SFAM-CZ01-V4-eSA-14-ML-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-ML | 0 | 0 | 0 | 0 | 3.9 | 0 | 151.114
DEER-SFAM-CZ01-V4-eSA-14-MM-s1 | 14 | CZ01 | V4 | CZ01-V4-eSA-14 | CZ01-V4-eSA-14-MM | 0 | 0 | 0 | 0 | 3.9 | 0 | 103.7549
DEER-SFAM-CZ01-V4-eSA-15-HH-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-HH | 0 | 0 | 0 | 0 | 3.9 | 0 | 100.6248
DEER-SFAM-CZ01-V4-eSA-15-HL-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-HL | 0 | 0 | 0 | 0 | 3.9 | 0 | 125.4255
DEER-SFAM-CZ01-V4-eSA-15-HM-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-HM | 0 | 0 | 0 | 0 | 3.9 | 0 | 101.0031
DEER-SFAM-CZ01-V4-eSA-15-MH-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-MH | 0 | 0 | 0 | 0 | 3.9 | 0 | 74.9821
DEER-SFAM-CZ01-V4-eSA-15-ML-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-ML | 0 | 0 | 0 | 0 | 3.9 | 0 | 100.8813
DEER-SFAM-CZ01-V4-eSA-15-MM-s1 | 15 | CZ01 | V4 | CZ01-V4-eSA-15 | CZ01-V4-eSA-15-MM | 0 | 0 | 0 | 0 | 3.9 | 0 | 91.9423
DEER-SFAM-CZ01-V4-eSA-16-CH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-CH | 0 | 0 | 0 | 0 | 4.25 | 0 | 57.9517
DEER-SFAM-CZ01-V4-eSA-16-CL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-CL | 0 | 0 | 0 | 0 | 4.25 | 0 | 73.2276
DEER-SFAM-CZ01-V4-eSA-16-CM-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-CM | 0 | 0 | 0 | 0 | 4.25 | 0 | 77.1539
DEER-SFAM-CZ01-V4-eSA-16-LH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 99.744
DEER-SFAM-CZ01-V4-eSA-16-LL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 65.3806
DEER-SFAM-CZ01-V4-eSA-16-LM-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-LM | 0 | 0 | 0 | 0 | 3.9 | 0 | 59.24
DEER-SFAM-CZ01-V4-eSA-16-NM-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-NM | 0 | 0 | 0 | 0 | 3.9 | 0 | 58.2403
DEER-SFAM-CZ01-V4-eSA-16-TH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-TH | 0 | 0 | 0 | 0 | 3.9 | 0 | 37.277
DEER-SFAM-CZ01-V4-eSA-16-TL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSA-16 | CZ01-V4-eSA-16-TL | 0 | 0 | 0 | 0 | 3.9 | 0 | 40.1439
DEER-SFAM-CZ01-V4-eSA-17-CH-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-CH | 0 | 0 | 0 | 0 | 4.25 | 0 | 73.2148
DEER-SFAM-CZ01-V4-eSA-17-CL-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-CL | 0 | 0 | 0 | 0 | 4.25 | 0 | 73.1963
DEER-SFAM-CZ01-V4-eSA-17-CM-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-CM | 0 | 0 | 0 | 0 | 4.25 | 0 | 57.7805
DEER-SFAM-CZ01-V4-eSA-17-LH-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 78.1599
DEER-SFAM-CZ01-V4-eSA-17-LL-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 42.2726
DEER-SFAM-CZ01-V4-eSA-17-LM-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-LM | 0 | 0 | 0 | 0 | 3.9 | 0 | 36.6282
DEER-SFAM-CZ01-V4-eSA-17-TH-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-TH | 0 | 0 | 0 | 0 | 3.9 | 0 | 59.6327
DEER-SFAM-CZ01-V4-eSA-17-TL-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-TL | 0 | 0 | 0 | 0 | 3.9 | 0 | 92.8216
DEER-SFAM-CZ01-V4-eSA-17-TM-s2 | 17 | CZ01 | V4 | CZ01-V4-eSA-17 | CZ01-V4-eSA-17-TM | 0 | 0 | 0 | 0 | 3.9 | 0 | 30.7751
DEER-SFAM-CZ01-V4-eSA-18-LH-s2 | 18 | CZ01 | V4 | CZ01-V4-eSA-18 | CZ01-V4-eSA-18-LH | 0 | 0 | 0 | 0 | 3.9 | 0 | 51.0843
DEER-SFAM-CZ01-V4-eSA-18-LL-s2 | 18 | CZ01 | V4 | CZ01-V4-eSA-18 | CZ01-V4-eSA-18-LL | 0 | 0 | 0 | 0 | 3.9 | 0 | 66.7543
DEER-SFAM-CZ01-V4-eSA-18-TH-s2 | 18 | CZ01 | V4 | CZ01-V4-eSA-18 | CZ01-V4-eSA-18-TH | 0 | 0 | 0 | 0 | 3.9 | 0 | 40.4641
DEER-SFAM-CZ01-V4-eSA-18-TL-s2 | 18 | CZ01 | V4 | CZ01-V4-eSA-18 | CZ01-V4-eSA-18-TL | 0 | 0 | 0 | 0 | 3.9 | 0 | 44.4697
DEER-SFAM-CZ01-V4-eSA-18-TM-s2 | 18 | CZ01 | V4 | CZ01-V4-eSA-18 | CZ01-V4-eSA-18-TM | 0 | 0 | 0 | 0 | 3.9 | 0 | 41.3976
DEER-SFAM-CZ01-V4-eSH-10-HH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-HH | 0 | 0 | 0 | 2888.7731 | 3.9 | 2888.7731 | 291.4232
DEER-SFAM-CZ01-V4-eSH-10-HL-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-HL | 0 | 0 | 0 | 2917.0786 | 3.9 | 2917.0786 | 289.8786
DEER-SFAM-CZ01-V4-eSH-10-HM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-HM | 0 | 0 | 0 | 2865.8446 | 3.9 | 2865.8446 | 276.0446
DEER-SFAM-CZ01-V4-eSH-10-LH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-LH | 0 | 0 | 0 | 3044.4636 | 3.9 | 3044.4636 | 301.3136
DEER-SFAM-CZ01-V4-eSH-10-LL-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-LL | 0 | 0 | 0 | 2876.2958 | 3.9 | 2876.2958 | 311.9458
DEER-SFAM-CZ01-V4-eSH-10-LM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-LM | 0 | 0 | 0 | 2874.5861 | 3.9 | 2874.5861 | 287.0361
DEER-SFAM-CZ01-V4-eSH-10-MH-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-MH | 0 | 0 | 0 | 2982.8087 | 3.9 | 2982.8087 | 319.6087
DEER-SFAM-CZ01-V4-eSH-10-ML-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-ML | 0 | 0 | 0 | 2704.5368 | 3.9 | 2704.5368 | 287.4868
DEER-SFAM-CZ01-V4-eSH-10-MM-s1 | 10 | CZ01 | V4 | CZ01-V4-eSH-10 | CZ01-V4-eSH-10-MM | 0 | 0 | 0 | 2909.4419 | 3.9 | 2909.4419 | 272.3919
DEER-SFAM-CZ01-V4-eSH-13-HH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-HH | 0 | 0 | 0 | 2778.3374 | 3.9 | 2778.3374 | 266.1874
DEER-SFAM-CZ01-V4-eSH-13-HL-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-HL | 0 | 0 | 0 | 2386.6167 | 3.9 | 2386.6167 | 264.5167
DEER-SFAM-CZ01-V4-eSH-13-HM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-HM | 0 | 0 | 0 | 2482.7519 | 3.9 | 2482.7519 | 239.952
DEER-SFAM-CZ01-V4-eSH-13-LH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-LH | 0 | 0 | 0 | 2792.497 | 3.9 | 2792.497 | 396.997
DEER-SFAM-CZ01-V4-eSH-13-LL-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-LL | 0 | 0 | 0 | 2500.1435 | 3.9 | 2500.1435 | 242.6435
DEER-SFAM-CZ01-V4-eSH-13-LM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-LM | 0 | 0 | 0 | 2222.744 | 3.9 | 2222.744 | 278.544
DEER-SFAM-CZ01-V4-eSH-13-MH-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-MH | 0 | 0 | 0 | 2780.8544 | 3.9 | 2780.8544 | 268.0043
DEER-SFAM-CZ01-V4-eSH-13-ML-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-ML | 0 | 0 | 0 | 2547.5233 | 3.9 | 2547.5233 | 274.2733
DEER-SFAM-CZ01-V4-eSH-13-MM-s1 | 13 | CZ01 | V4 | CZ01-V4-eSH-13 | CZ01-V4-eSH-13-MM | 0 | 0 | 0 | 2604.9243 | 3.9 | 2604.9243 | 215.8243
DEER-SFAM-CZ01-V4-eSH-14-HH-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-HH | 0 | 0 | 0 | 2535.6964 | 3.9 | 2535.6964 | 202.7964
DEER-SFAM-CZ01-V4-eSH-14-HL-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-HL | 0 | 0 | 0 | 2461.9004 | 3.9 | 2461.9004 | 243.0504
DEER-SFAM-CZ01-V4-eSH-14-HM-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-HM | 0 | 0 | 0 | 2448.1103 | 3.9 | 2448.1103 | 172.9603
DEER-SFAM-CZ01-V4-eSH-14-MH-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-MH | 0 | 0 | 0 | 2537.3967 | 3.4 | 2537.3967 | 262.3467
DEER-SFAM-CZ01-V4-eSH-14-ML-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-ML | 0 | 0 | 0 | 2590.921 | 3.9 | 2590.921 | 326.3211
DEER-SFAM-CZ01-V4-eSH-14-MM-s1 | 14 | CZ01 | V4 | CZ01-V4-eSH-14 | CZ01-V4-eSH-14-MM | 0 | 0 | 0 | 2376.3352 | 3.9 | 2376.3352 | 229.1852
DEER-SFAM-CZ01-V4-eSH-15-HH-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-HH | 0 | 0 | 0 | 2812.6991 | 3.9 | 2812.6991 | 187.299
DEER-SFAM-CZ01-V4-eSH-15-HL-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-HL | 0 | 0 | 0 | 2145.8162 | 3.9 | 2145.8162 | 186.9162
DEER-SFAM-CZ01-V4-eSH-15-HM-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-HM | 0 | 0 | 0 | 2255.819 | 3.9 | 2255.819 | 185.969
DEER-SFAM-CZ01-V4-eSH-15-MH-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-MH | 0 | 0 | 0 | 2476.3331 | 3.9 | 2476.3331 | 178.6831
DEER-SFAM-CZ01-V4-eSH-15-ML-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-ML | 0 | 0 | 0 | 2298.5338 | 3.9 | 2298.5338 | 184.6838
DEER-SFAM-CZ01-V4-eSH-15-MM-s1 | 15 | CZ01 | V4 | CZ01-V4-eSH-15 | CZ01-V4-eSH-15-MM | 0 | 0 | 0 | 2490.423 | 3.9 | 2490.423 | 197.3731
DEER-SFAM-CZ01-V4-eSH-16-CH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-CH | 0 | 0 | 0 | 2384.1521 | 4.25 | 2384.1521 | 151.6521
DEER-SFAM-CZ01-V4-eSH-16-CL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-CL | 0 | 0 | 0 | 2224.6631 | 4.25 | 2224.6631 | 159.4132
DEER-SFAM-CZ01-V4-eSH-16-LH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-LH | 0 | 0 | 0 | 2625.8306 | 3.9 | 2625.8306 | 185.7305
DEER-SFAM-CZ01-V4-eSH-16-LL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-LL | 0 | 0 | 0 | 2361.6712 | 3.9 | 2361.6712 | 149.3713
DEER-SFAM-CZ01-V4-eSH-16-LM-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-LM | 0 | 0 | 0 | 2614.7069 | 3.9 | 2614.7069 | 207.557
DEER-SFAM-CZ01-V4-eSH-16-TH-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-TH | 0 | 0 | 0 | 2954.4557 | 3.9 | 2954.4557 | 144.9557
DEER-SFAM-CZ01-V4-eSH-16-TL-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-TL | 0 | 0 | 0 | 2871.5395 | 3.9 | 2871.5395 | 129.1894
DEER-SFAM-CZ01-V4-eSH-16-TM-s2 | 16 | CZ01 | V4 | CZ01-V4-eSH-16 | CZ01-V4-eSH-16-TM | 0 | 0 | 0 | 2926.2001 | 3.9 | 2926.2001 | 132.3001
DEER-SFAM-CZ01-V4-eSH-17-CM-s2 | 17 | CZ01 | V4 | CZ01-V4-eSH-17 | CZ01-V4-eSH-17-CM | 0 | 0 | 0 | 2395.5711 | 4.25 | 2395.5711 | 176.0211
DEER-SFAM-CZ01-V4-eSH-17-LM-s2 | 17 | CZ01 | V4 | CZ01-V4-eSH-17 | CZ01-V4-eSH-17-LM | 0 | 0 | 0 | 2300.4963 | 3.9 | 2300.4963 | 84.0962
DEER-SFAM-CZ01-V4-eSH-17-TH-s2 | 17 | CZ01 | V4 | CZ01-V4-eSH-17 | CZ01-V4-eSH-17-TH | 0 | 0 | 0 | 2937.303 | 3.9 | 2937.303 | 154.853
DEER-SFAM-CZ01-V4-eSH-17-TL-s2 | 17 | CZ01 | V4 | CZ01-V4-eSH-17 | CZ01-V4-eSH-17-TL | 0 | 0 | 0 | 2893.5121 | 3.9 | 2893.5121 | 152.9121
DEER-SFAM-CZ01-V4-eSH-18-LH-s2 | 18 | CZ01 | V4 | CZ01-V4-eSH-18 | CZ01-V4-eSH-18-LH | 0 | 0 | 0 | 2553.1993 | 3.9 | 2553.1993 | 133.0494
DEER-SFAM-CZ01-V4-eSH-18-LL-s2 | 18 | CZ01 | V4 | CZ01-V4-eSH-18 | CZ01-V4-eSH-18-LL | 0 | 0 | 0 | 2341.2922 | 3.9 | 2341.2922 | 128.3921
DEER-SFAM-CZ01-V4-eSH-18-LM-s2 | 18 | CZ01 | V4 | CZ01-V4-eSH-18 | CZ01-V4-eSH-18-LM | 0 | 0 | 0 | 2673.4259 | 3.9 | 2673.4259 | 151.176
DEER-SFAM-CZ01-V4-eSH-18-TM-s2 | 18 | CZ01 | V4 | CZ01-V4-eSH-18 | CZ01-V4-eSH-18-TM | 0 | 0 | 0 | 2840.4749 | 3.9 | 2840.4749 | 226.5249
DEER-SFAM-CZ02-V1-eSA-10-HH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-HH | 9.5148 | 3.8336 | 1440.0708 | 0 | 3.4688 | 1440.0708 | 1672.3459
DEER-SFAM-CZ02-V1-eSA-10-HL-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-HL | 9.1152 | 4.2897 | 1495.9053 | 0 | 3.4688 | 1495.9053 | 1728.3544
DEER-SFAM-CZ02-V1-eSA-10-HM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-HM | 9.1188 | 4.0178 | 1466.1015 | 0 | 3.4688 | 1466.1015 | 1698.5197
DEER-SFAM-CZ02-V1-eSA-10-LH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-LH | 9.9729 | 3.74 | 1413.2931 | 0 | 3.4688 | 1413.2931 | 1645.914
DEER-SFAM-CZ02-V1-eSA-10-LL-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-LL | 9.3998 | 4.0582 | 1456.2053 | 0 | 3.4688 | 1456.2053 | 1688.6946
DEER-SFAM-CZ02-V1-eSA-10-LM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-LM | 9.8393 | 3.781 | 1416.134 | 0 | 3.4688 | 1416.134 | 1648.7624
DEER-SFAM-CZ02-V1-eSA-10-MH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-MH | 9.8047 | 3.6406 | 1419.6224 | 0 | 3.4688 | 1419.6224 | 1652.1832
DEER-SFAM-CZ02-V1-eSA-10-ML-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-ML | 9.2177 | 4.1275 | 1494.2169 | 0 | 3.4688 | 1494.2169 | 1726.6702
DEER-SFAM-CZ02-V1-eSA-10-MM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSA-10 | CZ02-V1-eSA-10-MM | 9.5075 | 3.8071 | 1421.2738 | 0 | 3.4688 | 1421.2738 | 1653.7456
DEER-SFAM-CZ02-V1-eSA-13-HH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-HH | 12.0661 | 3.195 | 1122.3155 | 0 | 3.4688 | 1122.3155 | 1331.8466
DEER-SFAM-CZ02-V1-eSA-13-HL-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-HL | 11.8019 | 3.3136 | 1135.869 | 0 | 3.4688 | 1135.869 | 1319.2484
DEER-SFAM-CZ02-V1-eSA-13-HM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-HM | 12.1179 | 3.2866 | 1119.1747 | 0 | 3.4688 | 1119.1747 | 1328.639
DEER-SFAM-CZ02-V1-eSA-13-LH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-LH | 12.5351 | 2.8955 | 1082.2966 | 0 | 3.4688 | 1082.2966 | 1314.7976
DEER-SFAM-CZ02-V1-eSA-13-LL-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-LL | 12.2052 | 3.1258 | 1126.8318 | 0 | 3.4688 | 1126.8318 | 1358.9189
DEER-SFAM-CZ02-V1-eSA-13-LM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-LM | 12.0555 | 3.0151 | 1128.904 | 0 | 3.4688 | 1128.904 | 1361.2322
DEER-SFAM-CZ02-V1-eSA-13-MH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-MH | 12.8844 | 3.0868 | 1095.3513 | 0 | 3.4688 | 1095.3513 | 1327.7707
DEER-SFAM-CZ02-V1-eSA-13-ML-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-ML | 11.6272 | 3.208 | 1117.3118 | 0 | 3.4688 | 1117.3118 | 1349.0188
DEER-SFAM-CZ02-V1-eSA-13-MM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSA-13 | CZ02-V1-eSA-13-MM | 12.7784 | 3.1062 | 1075.995 | 0 | 3.4688 | 1075.995 | 1308.3841
DEER-SFAM-CZ02-V1-eSA-14-HH-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-HH | 11.9185 | 3.082 | 1086.2867 | 0 | 3.4688 | 1086.2867 | 1281.0771
DEER-SFAM-CZ02-V1-eSA-14-HL-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-HL | 13.2836 | 3.069 | 1047.4135 | 0 | 3.4688 | 1047.4135 | 1190.6474
DEER-SFAM-CZ02-V1-eSA-14-HM-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-HM | 12.6657 | 3.1224 | 1088.3426 | 0 | 3.4688 | 1088.3426 | 1308.0957
DEER-SFAM-CZ02-V1-eSA-14-MH-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-MH | 13.0571 | 2.8037 | 1068.6037 | 0 | 3.4688 | 1068.6037 | 1221.3138
DEER-SFAM-CZ02-V1-eSA-14-ML-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-ML | 12.4916 | 3.0023 | 1060.4671 | 0 | 3.4688 | 1060.4671 | 1304.3589
DEER-SFAM-CZ02-V1-eSA-14-MM-s1 | 14 | CZ02 | V1 | CZ02-V1-eSA-14 | CZ02-V1-eSA-14-MM | 12.9208 | 2.8196 | 1048.3182 | 0 | 3.4688 | 1048.3182 | 1215.7386
DEER-SFAM-CZ02-V1-eSA-15-HH-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-HH | 13.8517 | 2.8365 | 974.4481 | 0 | 3.4688 | 974.4481 | 1136.83
DEER-SFAM-CZ02-V1-eSA-15-HL-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-HL | 14.4308 | 2.8811 | 954.3126 | 0 | 3.4688 | 954.3126 | 1156.7049
DEER-SFAM-CZ02-V1-eSA-15-HM-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-HM | 13.7996 | 2.7748 | 967.457 | 0 | 3.4688 | 967.457 | 1130.4407
DEER-SFAM-CZ02-V1-eSA-15-MH-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-MH | 13.1797 | 2.8592 | 1008.5592 | 0 | 3.4688 | 1008.5592 | 1129.5521
DEER-SFAM-CZ02-V1-eSA-15-ML-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-ML | 14.0851 | 2.7981 | 984.8069 | 0 | 3.4688 | 984.8069 | 1147.5368
DEER-SFAM-CZ02-V1-eSA-15-MM-s1 | 15 | CZ02 | V1 | CZ02-V1-eSA-15 | CZ02-V1-eSA-15-MM | 13.6739 | 2.8315 | 987.3294 | 0 | 3.4688 | 987.3294 | 1135.6946
DEER-SFAM-CZ02-V1-eSA-16-CH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-CH | 14.2347 | 3.0957 | 1150.1338 | 0 | 3.4688 | 1150.1338 | 1242.0627
DEER-SFAM-CZ02-V1-eSA-16-CL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-CL | 14.5704 | 3.0968 | 1075.9734 | 0 | 3.4688 | 1075.9734 | 1192.938
DEER-SFAM-CZ02-V1-eSA-16-CM-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-CM | 14.2675 | 3.1072 | 1111.8129 | 0 | 3.4688 | 1111.8129 | 1235.3231
DEER-SFAM-CZ02-V1-eSA-16-LH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-LH | 14.3467 | 2.8226 | 972.5642 | 0 | 3.4688 | 972.5642 | 1131.2298
DEER-SFAM-CZ02-V1-eSA-16-LL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-LL | 13.8379 | 3.044 | 1026.7964 | 0 | 3.4688 | 1026.7964 | 1131.3291
DEER-SFAM-CZ02-V1-eSA-16-LM-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-LM | 13.8492 | 2.9375 | 1026.4237 | 0 | 3.4688 | 1026.4237 | 1121.1668
DEER-SFAM-CZ02-V1-eSA-16-NM-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-NM | 15.4135 | 2.7111 | 942.277 | 0 | 3.4688 | 942.277 | 1035.1226
DEER-SFAM-CZ02-V1-eSA-16-TH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-TH | 13.8543 | 3.2764 | 1186.0475 | 0 | 3.4688 | 1186.0475 | 1244.6395
DEER-SFAM-CZ02-V1-eSA-16-TL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSA-16 | CZ02-V1-eSA-16-TL | 14.8119 | 3.1252 | 1071.0053 | 0 | 3.4688 | 1071.0053 | 1134.5469
DEER-SFAM-CZ02-V1-eSA-17-CH-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-CH | 15.1062 | 2.9516 | 1060.64 | 0 | 3.4688 | 1060.64 | 1177.5157
DEER-SFAM-CZ02-V1-eSA-17-CL-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-CL | 15.0487 | 2.9961 | 1057.6932 | 0 | 3.4688 | 1057.6932 | 1174.5451
DEER-SFAM-CZ02-V1-eSA-17-CM-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-CM | 15.157 | 2.983 | 1073.6393 | 0 | 3.4688 | 1073.6393 | 1165.2941
DEER-SFAM-CZ02-V1-eSA-17-LH-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-LH | 14.7723 | 2.7632 | 943.5389 | 0 | 3.4688 | 943.5389 | 1068.0091
DEER-SFAM-CZ02-V1-eSA-17-LL-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-LL | 14.5491 | 2.9201 | 987.1489 | 0 | 3.4688 | 987.1489 | 1055.1261
DEER-SFAM-CZ02-V1-eSA-17-LM-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-LM | 14.4185 | 2.8514 | 988.0059 | 0 | 3.4688 | 988.0059 | 1046.6917
DEER-SFAM-CZ02-V1-eSA-17-TH-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-TH | 15.7422 | 2.7814 | 999.0907 | 0 | 3.4688 | 999.0907 | 1093.2126
DEER-SFAM-CZ02-V1-eSA-17-TL-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-TL | 16.2739 | 2.8331 | 917.0679 | 0 | 3.4688 | 917.0679 | 1064.917
DEER-SFAM-CZ02-V1-eSA-17-TM-s2 | 17 | CZ02 | V1 | CZ02-V1-eSA-17 | CZ02-V1-eSA-17-TM | 15.9679 | 2.9768 | 1100.5541 | 0 | 3.4688 | 1100.5541 | 1149.4904
DEER-SFAM-CZ02-V1-eSA-18-LH-s2 | 18 | CZ02 | V1 | CZ02-V1-eSA-18 | CZ02-V1-eSA-18-LH | 15.4082 | 2.695 | 925.1558 | 0 | 3.4688 | 925.1558 | 1006.8595
DEER-SFAM-CZ02-V1-eSA-18-LL-s2 | 18 | CZ02 | V1 | CZ02-V1-eSA-18 | CZ02-V1-eSA-18-LL | 15.6587 | 2.6835 | 899.5818 | 0 | 3.4688 | 899.5818 | 1006.1723
DEER-SFAM-CZ02-V1-eSA-18-TH-s2 | 18 | CZ02 | V1 | CZ02-V1-eSA-18 | CZ02-V1-eSA-18-TH | 16.4519 | 2.6412 | 962.3383 | 0 | 3.4688 | 962.3383 | 1026.4272
DEER-SFAM-CZ02-V1-eSA-18-TL-s2 | 18 | CZ02 | V1 | CZ02-V1-eSA-18 | CZ02-V1-eSA-18-TL | 15.8317 | 2.9538 | 1040.8258 | 0 | 3.4688 | 1040.8258 | 1110.9
DEER-SFAM-CZ02-V1-eSA-18-TM-s2 | 18 | CZ02 | V1 | CZ02-V1-eSA-18 | CZ02-V1-eSA-18-TM | 15.7658 | 2.7138 | 990.2814 | 0 | 3.4688 | 990.2814 | 1055.6996
DEER-SFAM-CZ02-V1-eSH-10-HH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-HH | 9.8449 | 3.8558 | 1402.3488 | 5729.91 | 3.4688 | 7132.2588 | 1948.0693
DEER-SFAM-CZ02-V1-eSH-10-HL-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-HL | 9.5349 | 4.0755 | 1449.8572 | 5727.7896 | 3.4688 | 7177.6468 | 1985.1911
DEER-SFAM-CZ02-V1-eSH-10-HM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-HM | 9.8766 | 3.9118 | 1435.9989 | 5553.3003 | 3.4688 | 6989.2991 | 1951.0936
DEER-SFAM-CZ02-V1-eSH-10-LH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-LH | 9.9811 | 3.59 | 1397.6142 | 6095.5627 | 3.4688 | 7493.1769 | 1958.1035
DEER-SFAM-CZ02-V1-eSH-10-LL-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-LL | 9.8532 | 3.9034 | 1425.4061 | 6025.8967 | 3.4688 | 7451.3027 | 2011.6909
DEER-SFAM-CZ02-V1-eSH-10-LM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-LM | 10.0617 | 3.7203 | 1398.4874 | 5817.2184 | 3.4688 | 7215.7057 | 1934.7812
DEER-SFAM-CZ02-V1-eSH-10-MH-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-MH | 10.0019 | 3.7328 | 1406.8983 | 6060.7085 | 3.4688 | 7467.6068 | 2003.3308
DEER-SFAM-CZ02-V1-eSH-10-ML-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-ML | 9.7734 | 4.0655 | 1449.0505 | 5637.3193 | 3.4688 | 7086.3697 | 1993.3911
DEER-SFAM-CZ02-V1-eSH-10-MM-s1 | 10 | CZ02 | V1 | CZ02-V1-eSH-10 | CZ02-V1-eSH-10-MM | 9.8293 | 3.8613 | 1439.3101 | 5792.1541 | 3.4688 | 7231.4642 | 1943.5237
DEER-SFAM-CZ02-V1-eSH-13-HH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-HH | 11.6534 | 3.279 | 1159.6268 | 5816.6639 | 3.4688 | 6976.2907 | 1653.0151
DEER-SFAM-CZ02-V1-eSH-13-HL-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-HL | 12.6147 | 3.2767 | 1106.7575 | 5052.0573 | 3.4688 | 6158.8148 | 1601.699
DEER-SFAM-CZ02-V1-eSH-13-HM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-HM | 11.9327 | 3.2575 | 1137.4263 | 5140.6072 | 3.4688 | 6278.0335 | 1585.1276
DEER-SFAM-CZ02-V1-eSH-13-LH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-LH | 12.3665 | 2.9264 | 1102.5722 | 6515.9353 | 3.4688 | 7618.5075 | 1837.2555
DEER-SFAM-CZ02-V1-eSH-13-LL-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-LL | 13.241 | 3.0336 | 1065.1603 | 5435.9075 | 3.4688 | 6501.0678 | 1518.3336
DEER-SFAM-CZ02-V1-eSH-13-LM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-LM | 11.808 | 3.0773 | 1143.129 | 4498.2274 | 3.4688 | 5641.3564 | 1657.68
DEER-SFAM-CZ02-V1-eSH-13-MH-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-MH | 13.0007 | 3.0113 | 1069.3812 | 5920.0867 | 3.4688 | 6989.4679 | 1563.6302
DEER-SFAM-CZ02-V1-eSH-13-ML-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-ML | 11.7196 | 3.2609 | 1157.7287 | 5551.3791 | 3.4688 | 6709.1079 | 1667.4754
DEER-SFAM-CZ02-V1-eSH-13-MM-s1 | 13 | CZ02 | V1 | CZ02-V1-eSH-13 | CZ02-V1-eSH-13-MM | 12.5591 | 3.2108 | 1121.4858 | 5327.6187 | 3.4688 | 6449.1045 | 1516.2675
DEER-SFAM-CZ02-V1-eSH-14-HH-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-HH | 12.338 | 3.1336 | 1095.2232 | 5372.0487 | 3.4688 | 6467.2719 | 1471.6931
DEER-SFAM-CZ02-V1-eSH-14-HL-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-HL | 12.6624 | 3.1208 | 1065.3184 | 5474.2515 | 3.4688 | 6539.5699 | 1518.2341
DEER-SFAM-CZ02-V1-eSH-14-HM-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-HM | 12.5832 | 2.9947 | 1065.7147 | 5373.1025 | 3.4688 | 6438.8172 | 1388.3169
DEER-SFAM-CZ02-V1-eSH-14-MH-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-MH | 13.1841 | 2.743 | 1028.9408 | 5969.946 | 3.4688 | 6998.8869 | 1516.417
DEER-SFAM-CZ02-V1-eSH-14-ML-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-ML | 13.3093 | 2.9781 | 1033.8101 | 6385.346 | 3.4688 | 7419.1561 | 1649.2258
DEER-SFAM-CZ02-V1-eSH-14-MM-s1 | 14 | CZ02 | V1 | CZ02-V1-eSH-14 | CZ02-V1-eSH-14-MM | 12.9973 | 2.8918 | 1033.6914 | 5350.555 | 3.4688 | 6384.2464 | 1458.9037
DEER-SFAM-CZ02-V1-eSH-15-HH-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-HH | 13.5325 | 2.7515 | 981.9079 | 6611.6688 | 3.4688 | 7593.5767 | 1325.1652
DEER-SFAM-CZ02-V1-eSH-15-HL-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-HL | 13.8193 | 2.9009 | 989.2034 | 4581.1192 | 3.4688 | 5570.3226 | 1336.4894
DEER-SFAM-CZ02-V1-eSH-15-HM-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-HM | 14.4544 | 2.8135 | 953.6233 | 4874.5343 | 3.4688 | 5828.1576 | 1299.511
DEER-SFAM-CZ02-V1-eSH-15-MH-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-MH | 13.8312 | 2.8446 | 995.5496 | 5856.3068 | 3.4688 | 6851.8563 | 1330.2939
DEER-SFAM-CZ02-V1-eSH-15-ML-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-ML | 14.2114 | 2.82 | 965.66 | 5574.2403 | 3.4688 | 6539.9003 | 1315.1597
DEER-SFAM-CZ02-V1-eSH-15-MM-s1 | 15 | CZ02 | V1 | CZ02-V1-eSH-15 | CZ02-V1-eSH-15-MM | 14.6796 | 2.8019 | 948.846 | 5763.0262 | 3.4688 | 6711.8722 | 1315.2302
DEER-SFAM-CZ02-V1-eSH-16-CH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-CH | 14.4906 | 3.0352 | 1107.8103 | 6186.2366 | 3.4688 | 7294.0469 | 1477.4099
DEER-SFAM-CZ02-V1-eSH-16-CL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-CL | 14.6262 | 3.115 | 1130.506 | 5808.6149 | 3.4688 | 6939.1209 | 1514.0483
DEER-SFAM-CZ02-V1-eSH-16-LH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-LH | 14.0661 | 2.7883 | 985.9786 | 6463.8574 | 3.4688 | 7449.8361 | 1375.0658
DEER-SFAM-CZ02-V1-eSH-16-LL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-LL | 13.802 | 2.9978 | 1024.9016 | 6100.5276 | 3.4688 | 7125.4292 | 1348.716
DEER-SFAM-CZ02-V1-eSH-16-LM-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-LM | 13.6563 | 2.918 | 1022.5328 | 6564.9112 | 3.4688 | 7587.444 | 1460.3535
DEER-SFAM-CZ02-V1-eSH-16-TH-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-TH | 14.9846 | 3.0514 | 1045.5911 | 7494.294 | 3.4688 | 8539.8852 | 1466.7426
DEER-SFAM-CZ02-V1-eSH-16-TL-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-TL | 14.0193 | 3.3372 | 1182.426 | 7406.5616 | 3.4688 | 8588.9876 | 1567.9471
DEER-SFAM-CZ02-V1-eSH-16-TM-s2 | 16 | CZ02 | V1 | CZ02-V1-eSH-16 | CZ02-V1-eSH-16-TM | 14.2118 | 3.275 | 1167.2007 | 7463.9548 | 3.4688 | 8631.1555 | 1560.3881
DEER-SFAM-CZ02-V1-eSH-17-CM-s2 | 17 | CZ02 | V1 | CZ02-V1-eSH-17 | CZ02-V1-eSH-17-CM | 15.4481 | 2.9599 | 1068.6428 | 6214.7762 | 3.4688 | 7283.419 | 1486.9941
DEER-SFAM-CZ02-V1-eSH-17-LM-s2 | 17 | CZ02 | V1 | CZ02-V1-eSH-17 | CZ02-V1-eSH-17-LM | 14.5355 | 2.8778 | 1006.7856 | 5907.7713 | 3.4688 | 6914.5569 | 1188.18
DEER-SFAM-CZ02-V1-eSH-17-TH-s2 | 17 | CZ02 | V1 | CZ02-V1-eSH-17 | CZ02-V1-eSH-17-TH | 15.7638 | 2.8609 | 990.1755 | 7470.5349 | 3.4688 | 8460.7104 | 1431.5991
DEER-SFAM-CZ02-V1-eSH-17-TL-s2 | 17 | CZ02 | V1 | CZ02-V1-eSH-17 | CZ02-V1-eSH-17-TL | 15.6775 | 2.9209 | 998.5001 | 7466.3324 | 3.4688 | 8464.8325 | 1437.5106
DEER-SFAM-CZ02-V1-eSH-18-LH-s2 | 18 | CZ02 | V1 | CZ02-V1-eSH-18 | CZ02-V1-eSH-18-LH | 15.3288 | 2.7134 | 924.8004 | 6829.667 | 3.4688 | 7754.4674 | 1244.7033
DEER-SFAM-CZ02-V1-eSH-18-LL-s2 | 18 | CZ02 | V1 | CZ02-V1-eSH-18 | CZ02-V1-eSH-18-LL | 14.6744 | 2.8025 | 957.5451 | 6204.1115 | 3.4688 | 7161.6566 | 1238.0676
DEER-SFAM-CZ02-V1-eSH-18-LM-s2 | 18 | CZ02 | V1 | CZ02-V1-eSH-18 | CZ02-V1-eSH-18-LM | 15.3774 | 2.764 | 929.9326 | 7164.2372 | 3.4688 | 8094.1697 | 1297.0607
DEER-SFAM-CZ02-V1-eSH-18-TM-s2 | 18 | CZ02 | V1 | CZ02-V1-eSH-18 | CZ02-V1-eSH-18-TM | 16.3609 | 2.8227 | 964.0185 | 7504.5274 | 3.4688 | 8468.5459 | 1581.5062
DEER-SFAM-CZ02-V2-eSA-10-HH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-HH | 9.3075 | 3.1775 | 920.6979 | 0 | 3.1141 | 920.6979 | 1049.3052
DEER-SFAM-CZ02-V2-eSA-10-HL-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-HL | 8.891 | 3.536 | 953.5008 | 0 | 3.1141 | 953.5008 | 1082.1906
DEER-SFAM-CZ02-V2-eSA-10-HM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-HM | 8.8782 | 3.3062 | 931.9703 | 0 | 3.1141 | 931.9703 | 1060.6454
DEER-SFAM-CZ02-V2-eSA-10-LH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-LH | 9.8337 | 3.1142 | 898.0173 | 0 | 3.1141 | 898.0173 | 1026.789
DEER-SFAM-CZ02-V2-eSA-10-LL-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-LL | 9.2141 | 3.3539 | 924.3391 | 0 | 3.1141 | 924.3391 | 1053.0479
DEER-SFAM-CZ02-V2-eSA-10-LM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-LM | 9.7116 | 3.1405 | 898.1345 | 0 | 3.1141 | 898.1345 | 1026.91
DEER-SFAM-CZ02-V2-eSA-10-MH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-MH | 9.5639 | 3.0418 | 911.6204 | 0 | 3.1141 | 911.6204 | 1040.3637
DEER-SFAM-CZ02-V2-eSA-10-ML-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-ML | 9.0201 | 3.4227 | 949.5251 | 0 | 3.1141 | 949.5251 | 1078.217
DEER-SFAM-CZ02-V2-eSA-10-MM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSA-10 | CZ02-V2-eSA-10-MM | 9.382 | 3.154 | 901.6303 | 0 | 3.1141 | 901.6303 | 1030.3309
DEER-SFAM-CZ02-V2-eSA-13-HH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-HH | 11.7727 | 2.6544 | 719.8882 | 0 | 3.1141 | 719.8882 | 835.8895
DEER-SFAM-CZ02-V2-eSA-13-HL-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-HL | 11.7179 | 2.713 | 716.9091 | 0 | 3.1141 | 716.9091 | 818.4363
DEER-SFAM-CZ02-V2-eSA-13-HM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-HM | 11.85 | 2.6913 | 713.7414 | 0 | 3.1141 | 713.7414 | 829.7113
DEER-SFAM-CZ02-V2-eSA-13-LH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-LH | 12.3001 | 2.3977 | 690.8669 | 0 | 3.1141 | 690.8669 | 819.5815
DEER-SFAM-CZ02-V2-eSA-13-LL-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-LL | 12.0795 | 2.5727 | 714.1627 | 0 | 3.1141 | 714.1627 | 842.6824
DEER-SFAM-CZ02-V2-eSA-13-LM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-LM | 11.8536 | 2.5072 | 719.2637 | 0 | 3.1141 | 719.2637 | 847.8959
DEER-SFAM-CZ02-V2-eSA-13-MH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-MH | 12.6019 | 2.5604 | 701.0148 | 0 | 3.1141 | 701.0148 | 829.6903
DEER-SFAM-CZ02-V2-eSA-13-ML-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-ML | 11.4697 | 2.6165 | 706.2963 | 0 | 3.1141 | 706.2963 | 834.5838
DEER-SFAM-CZ02-V2-eSA-13-MM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSA-13 | CZ02-V2-eSA-13-MM | 12.5575 | 2.5387 | 684.8952 | 0 | 3.1141 | 684.8952 | 813.5566
DEER-SFAM-CZ02-V2-eSA-14-HH-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-HH | 11.6431 | 2.5319 | 692.3089 | 0 | 3.1141 | 692.3089 | 800.158
DEER-SFAM-CZ02-V2-eSA-14-HL-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-HL | 13.1493 | 2.4974 | 662.213 | 0 | 3.1141 | 662.213 | 741.5166
DEER-SFAM-CZ02-V2-eSA-14-HM-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-HM | 12.5542 | 2.5749 | 688.4698 | 0 | 3.1141 | 688.4698 | 810.1285
DEER-SFAM-CZ02-V2-eSA-14-MH-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-MH | 12.7902 | 2.3383 | 684.4259 | 0 | 3.1141 | 684.4259 | 768.9823
DEER-SFAM-CZ02-V2-eSA-14-ML-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-ML | 12.3574 | 2.4715 | 670.9574 | 0 | 3.1141 | 670.9574 | 805.9836
DEER-SFAM-CZ02-V2-eSA-14-MM-s1 | 14 | CZ02 | V2 | CZ02-V2-eSA-14 | CZ02-V2-eSA-14-MM | 12.6598 | 2.3468 | 669.967 | 0 | 3.1141 | 669.967 | 762.6621
DEER-SFAM-CZ02-V2-eSA-15-HH-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-HH | 13.3953 | 2.3241 | 628.2313 | 0 | 3.1141 | 628.2313 | 718.1324
DEER-SFAM-CZ02-V2-eSA-15-HL-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-HL | 14.1881 | 2.3534 | 607.0736 | 0 | 3.1141 | 607.0736 | 719.1334
DEER-SFAM-CZ02-V2-eSA-15-HM-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-HM | 13.4551 | 2.246 | 618.801 | 0 | 3.1141 | 618.801 | 709.0382
DEER-SFAM-CZ02-V2-eSA-15-MH-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-MH | 12.8915 | 2.3667 | 644.5438 | 0 | 3.1141 | 644.5438 | 711.5312
DEER-SFAM-CZ02-V2-eSA-15-ML-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-ML | 13.9404 | 2.2925 | 624.3963 | 0 | 3.1141 | 624.3963 | 714.5142
DEER-SFAM-CZ02-V2-eSA-15-MM-s1 | 15 | CZ02 | V2 | CZ02-V2-eSA-15 | CZ02-V2-eSA-15-MM | 13.5277 | 2.3275 | 624.8445 | 0 | 3.1141 | 624.8445 | 706.9862
DEER-SFAM-CZ02-V2-eSA-16-CH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-CH | 14.1806 | 2.6082 | 727.6423 | 0 | 3.1141 | 727.6423 | 779.6139
DEER-SFAM-CZ02-V2-eSA-16-CL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-CL | 14.5227 | 2.494 | 677.9883 | 0 | 3.1141 | 677.9883 | 743.8207
DEER-SFAM-CZ02-V2-eSA-16-CM-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-CM | 14.1891 | 2.55 | 703.9277 | 0 | 3.1141 | 703.9277 | 773.446
DEER-SFAM-CZ02-V2-eSA-16-LH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-LH | 13.8775 | 2.2687 | 624.6099 | 0 | 3.1141 | 624.6099 | 713.4858
DEER-SFAM-CZ02-V2-eSA-16-LL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-LL | 13.5416 | 2.4611 | 652.768 | 0 | 3.1141 | 652.768 | 711.1985
DEER-SFAM-CZ02-V2-eSA-16-LM-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-LM | 13.5368 | 2.3858 | 652.6074 | 0 | 3.1141 | 652.6074 | 705.5839
DEER-SFAM-CZ02-V2-eSA-16-NM-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-NM | 15.301 | 2.1643 | 590.3025 | 0 | 3.1141 | 590.3025 | 642.3068
DEER-SFAM-CZ02-V2-eSA-16-TH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-TH | 13.4428 | 2.7024 | 774.6607 | 0 | 3.1141 | 774.6607 | 807.9608
DEER-SFAM-CZ02-V2-eSA-16-TL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSA-16 | CZ02-V2-eSA-16-TL | 14.5989 | 2.4987 | 682.014 | 0 | 3.1141 | 682.014 | 717.9682
DEER-SFAM-CZ02-V2-eSA-17-CH-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-CH | 15.061 | 2.4736 | 668.4744 | 0 | 3.1141 | 668.4744 | 734.282
DEER-SFAM-CZ02-V2-eSA-17-CL-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-CL | 15.0558 | 2.4803 | 664.4905 | 0 | 3.1141 | 664.4905 | 730.2824
DEER-SFAM-CZ02-V2-eSA-17-CM-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-CM | 15.1384 | 2.4815 | 677.0595 | 0 | 3.1141 | 677.0595 | 728.8735
DEER-SFAM-CZ02-V2-eSA-17-LH-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-LH | 14.3706 | 2.2231 | 602.8197 | 0 | 3.1141 | 602.8197 | 672.4789
DEER-SFAM-CZ02-V2-eSA-17-LL-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-LL | 14.2756 | 2.3709 | 625.6577 | 0 | 3.1141 | 625.6577 | 663.6372
DEER-SFAM-CZ02-V2-eSA-17-LM-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-LM | 14.1285 | 2.3049 | 626.8599 | 0 | 3.1141 | 626.8599 | 659.6572
DEER-SFAM-CZ02-V2-eSA-17-TH-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-TH | 15.1105 | 2.2816 | 655.432 | 0 | 3.1141 | 655.432 | 708.6822
DEER-SFAM-CZ02-V2-eSA-17-TL-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-TL | 16.2088 | 2.2745 | 583.1475 | 0 | 3.1141 | 583.1475 | 666.7141
DEER-SFAM-CZ02-V2-eSA-17-TM-s2 | 17 | CZ02 | V2 | CZ02-V2-eSA-17 | CZ02-V2-eSA-17-TM | 15.6333 | 2.5189 | 707.5409 | 0 | 3.1141 | 707.5409 | 735.35
DEER-SFAM-CZ02-V2-eSA-18-LH-s2 | 18 | CZ02 | V2 | CZ02-V2-eSA-18 | CZ02-V2-eSA-18-LH | 15.0214 | 2.1851 | 589.4332 | 0 | 3.1141 | 589.4332 | 635.1189
DEER-SFAM-CZ02-V2-eSA-18-LL-s2 | 18 | CZ02 | V2 | CZ02-V2-eSA-18 | CZ02-V2-eSA-18-LL | 15.3687 | 2.1581 | 569.7291 | 0 | 3.1141 | 569.7291 | 629.3669
DEER-SFAM-CZ02-V2-eSA-18-TH-s2 | 18 | CZ02 | V2 | CZ02-V2-eSA-18 | CZ02-V2-eSA-18-TH | 15.7494 | 2.1572 | 632.715 | 0 | 3.1141 | 632.715 | 668.906
DEER-SFAM-CZ02-V2-eSA-18-TL-s2 | 18 | CZ02 | V2 | CZ02-V2-eSA-18 | CZ02-V2-eSA-18-TL | 15.4211 | 2.4859 | 674.7549 | 0 | 3.1141 | 674.7549 | 714.5203
DEER-SFAM-CZ02-V2-eSA-18-TM-s2 | 18 | CZ02 | V2 | CZ02-V2-eSA-18 | CZ02-V2-eSA-18-TM | 15.2003 | 2.2164 | 645.7329 | 0 | 3.1141 | 645.7329 | 682.7189
DEER-SFAM-CZ02-V2-eSH-10-HH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-HH | 9.583 | 3.2005 | 901.336 | 2991.1062 | 3.1141 | 3892.4422 | 1200.3525
DEER-SFAM-CZ02-V2-eSH-10-HL-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-HL | 9.3327 | 3.3609 | 925.6927 | 3019.2836 | 3.1141 | 3944.9763 | 1218.3245
DEER-SFAM-CZ02-V2-eSH-10-HM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-HM | 9.7123 | 3.2351 | 914.7778 | 2936.9658 | 3.1141 | 3851.7436 | 1196.1791
DEER-SFAM-CZ02-V2-eSH-10-LH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-LH | 9.7516 | 2.9866 | 897.6984 | 3136.5857 | 3.1141 | 4034.284 | 1206.1717
DEER-SFAM-CZ02-V2-eSH-10-LL-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-LL | 9.7116 | 3.2422 | 903.1388 | 3101.2602 | 3.1141 | 4004.399 | 1224.9585
DEER-SFAM-CZ02-V2-eSH-10-LM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-LM | 9.8652 | 3.0834 | 892.3657 | 3039.0404 | 3.1141 | 3931.4061 | 1186.8248
DEER-SFAM-CZ02-V2-eSH-10-MH-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-MH | 9.8231 | 3.1021 | 898.3866 | 3121.8131 | 3.1141 | 4020.1997 | 1225.9607
DEER-SFAM-CZ02-V2-eSH-10-ML-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-ML | 9.6671 | 3.3553 | 915.7437 | 2936.8348 | 3.1141 | 3852.5785 | 1214.6128
DEER-SFAM-CZ02-V2-eSH-10-MM-s1 | 10 | CZ02 | V2 | CZ02-V2-eSH-10 | CZ02-V2-eSH-10-MM | 9.6834 | 3.2022 | 915.6205 | 3033.8027 | 3.1141 | 3949.4232 | 1192.0038
DEER-SFAM-CZ02-V2-eSH-13-HH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-HH | 11.2732 | 2.6897 | 747.7913 | 2921.3455 | 3.1141 | 3669.1369 | 1020.9571
DEER-SFAM-CZ02-V2-eSH-13-HL-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-HL | 12.4693 | 2.6956 | 702.3169 | 2536.3717 | 3.1141 | 3238.6887 | 973.9951
DEER-SFAM-CZ02-V2-eSH-13-HM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-HM | 11.6068 | 2.6684 | 729.9274 | 2601.7824 | 3.1141 | 3331.7098 | 976.2035
DEER-SFAM-CZ02-V2-eSH-13-LH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-LH | 12.1077 | 2.4385 | 705.2284 | 3157.9185 | 3.1141 | 3863.1469 | 1117.5942
DEER-SFAM-CZ02-V2-eSH-13-LL-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-LL | 13.0269 | 2.5043 | 678.7687 | 2680.4327 | 3.1141 | 3359.2014 | 928.9416
DEER-SFAM-CZ02-V2-eSH-13-LM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-LM | 11.6188 | 2.5595 | 727.2491 | 2290.6784 | 3.1141 | 3017.9275 | 1009.0566
DEER-SFAM-CZ02-V2-eSH-13-MH-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-MH | 12.5913 | 2.4895 | 691.3794 | 2954.607 | 3.1141 | 3645.9864 | 964.3771
DEER-SFAM-CZ02-V2-eSH-13-ML-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-ML | 11.5991 | 2.6993 | 733.2036 | 2740.9298 | 3.1141 | 3474.1334 | 1013.106
DEER-SFAM-CZ02-V2-eSH-13-MM-s1 | 13 | CZ02 | V2 | CZ02-V2-eSH-13 | CZ02-V2-eSH-13-MM | 12.3891 | 2.6298 | 713.6155 | 2727.4013 | 3.1141 | 3441.0168 | 930.4469
DEER-SFAM-CZ02-V2-eSH-14-HH-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-HH | 11.9909 | 2.5597 | 703.0567 | 2679.7973 | 3.1141 | 3382.8541 | 910.9392
DEER-SFAM-CZ02-V2-eSH-14-HL-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-HL | 12.4338 | 2.5278 | 676.5449 | 2672.2483 | 3.1141 | 3348.7932 | 926.5644
DEER-SFAM-CZ02-V2-eSH-14-HM-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-HM | 12.2772 | 2.4335 | 680.981 | 2652.919 | 3.1141 | 3333.8999 | 859.3852
DEER-SFAM-CZ02-V2-eSH-14-MH-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-MH | 12.9313 | 2.2781 | 657.1871 | 2886.0321 | 3.1141 | 3543.2192 | 930.5792
DEER-SFAM-CZ02-V2-eSH-14-ML-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-ML | 13.2229 | 2.4328 | 651.6723 | 3028.0676 | 3.1141 | 3679.7399 | 994.9085
DEER-SFAM-CZ02-V2-eSH-14-MM-s1 | 14 | CZ02 | V2 | CZ02-V2-eSH-14 | CZ02-V2-eSH-14-MM | 12.8563 | 2.3781 | 654.7013 | 2598.3547 | 3.1141 | 3253.056 | 889.3766
DEER-SFAM-CZ02-V2-eSH-15-HH-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-HH | 13.1456 | 2.2346 | 630.0065 | 3208.1734 | 3.1141 | 3838.1799 | 825.0327
DEER-SFAM-CZ02-V2-eSH-15-HL-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-HL | 13.5491 | 2.3902 | 631.3704 | 2274.6564 | 3.1141 | 2906.0268 | 821.9798
DEER-SFAM-CZ02-V2-eSH-15-HM-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-HM | 14.1697 | 2.3076 | 609.1546 | 2376.315 | 3.1141 | 2985.4696 | 799.4874
DEER-SFAM-CZ02-V2-eSH-15-MH-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-MH | 13.6474 | 2.3395 | 633.033 | 2767.7448 | 3.1141 | 3400.7777 | 818.3533
DEER-SFAM-CZ02-V2-eSH-15-ML-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-ML | 14.1353 | 2.29 | 608.4278 | 2633.8336 | 3.1141 | 3242.2614 | 801.461
DEER-SFAM-CZ02-V2-eSH-15-MM-s1 | 15 | CZ02 | V2 | CZ02-V2-eSH-15 | CZ02-V2-eSH-15-MM | 14.3842 | 2.308 | 605.9426 | 2796.7982 | 3.1141 | 3402.7409 | 810.3233
DEER-SFAM-CZ02-V2-eSH-16-CH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-CH | 14.358 | 2.4751 | 705.1493 | 3165.6683 | 3.1141 | 3870.8176 | 899.8932
DEER-SFAM-CZ02-V2-eSH-16-CL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-CL | 14.54 | 2.6443 | 715.2846 | 2930.6593 | 3.1141 | 3645.944 | 914.938
DEER-SFAM-CZ02-V2-eSH-16-LH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-LH | 13.4605 | 2.2634 | 640.1657 | 3198.7746 | 3.1141 | 3838.9402 | 841.8271
DEER-SFAM-CZ02-V2-eSH-16-LL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-LL | 13.54 | 2.424 | 648.7659 | 2945.2449 | 3.1141 | 3594.0108 | 810.3429
DEER-SFAM-CZ02-V2-eSH-16-LM-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-LM | 13.1653 | 2.3527 | 658.497 | 3228.8423 | 3.1141 | 3887.3393 | 884.367
DEER-SFAM-CZ02-V2-eSH-16-TH-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-TH | 14.4282 | 2.4648 | 681.7644 | 4016.2215 | 3.1141 | 4697.986 | 900.3173
DEER-SFAM-CZ02-V2-eSH-16-TL-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-TL | 13.9257 | 2.7808 | 755.3259 | 3917.693 | 3.1141 | 4673.019 | 953.7546
DEER-SFAM-CZ02-V2-eSH-16-TM-s2 | 16 | CZ02 | V2 | CZ02-V2-eSH-16 | CZ02-V2-eSH-16-TM | 14.0898 | 2.7313 | 746.8093 | 3960.2503 | 3.1141 | 4707.0596 | 950.6543
DEER-SFAM-CZ02-V2-eSH-17-CM-s2 | 17 | CZ02 | V2 | CZ02-V2-eSH-17 | CZ02-V2-eSH-17-CM | 15.3438 | 2.5108 | 676.8038 | 3110.4468 | 3.1141 | 3787.2506 | 887.8813
DEER-SFAM-CZ02-V2-eSH-17-LM-s2 | 17 | CZ02 | V2 | CZ02-V2-eSH-17 | CZ02-V2-eSH-17-LM | 14.1555 | 2.4108 | 644.971 | 2843.7866 | 3.1141 | 3488.7576 | 735.4756
DEER-SFAM-CZ02-V2-eSH-17-TH-s2 | 17 | CZ02 | V2 | CZ02-V2-eSH-17 | CZ02-V2-eSH-17-TH | 15.2586 | 2.3302 | 642.5725 | 4009.6179 | 3.1141 | 4652.1904 | 876.7852
DEER-SFAM-CZ02-V2-eSH-17-TL-s2 | 17 | CZ02 | V2 | CZ02-V2-eSH-17 | CZ02-V2-eSH-17-TL | 15.2438 | 2.375 | 645.3741 | 3993.1653 | 3.1141 | 4638.5394 | 877.0427
DEER-SFAM-CZ02-V2-eSH-18-LH-s2 | 18 | CZ02 | V2 | CZ02-V2-eSH-18 | CZ02-V2-eSH-18-LH | 14.964 | 2.2031 | 587.8982 | 3417.4903 | 3.1141 | 4005.3885 | 747.1923
DEER-SFAM-CZ02-V2-eSH-18-LL-s2 | 18 | CZ02 | V2 | CZ02-V2-eSH-18 | CZ02-V2-eSH-18-LL | 14.356 | 2.2721 | 607.1992 | 2988.9047 | 3.1141 | 3596.1039 | 748.1993
DEER-SFAM-CZ02-V2-eSH-18-LM-s2 | 18 | CZ02 | V2 | CZ02-V2-eSH-18 | CZ02-V2-eSH-18-LM | 15.0192 | 2.237 | 591.194 | 3626.6788 | 3.1141 | 4217.8728 | 775.9737
DEER-SFAM-CZ02-V2-eSH-18-TM-s2 | 18 | CZ02 | V2 | CZ02-V2-eSH-18 | CZ02-V2-eSH-18-TM | 15.9718 | 2.3104 | 628.3656 | 4038.6171 | 3.1141 | 4666.9827 | 967.6452
DEER-SFAM-CZ02-V3-eSA-10-HH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-HH | 9.5679 | 3.7681 | 1762.5204 | 0 | 3.4 | 1762.5204 | 1887.5575
DEER-SFAM-CZ02-V3-eSA-10-HL-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-HL | 9.2508 | 4.1384 | 1830.851 | 0 | 3.4 | 1830.851 | 1955.9705
DEER-SFAM-CZ02-V3-eSA-10-HM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-HM | 9.2513 | 3.8479 | 1797.52 | 0 | 3.4 | 1797.52 | 1922.6243
DEER-SFAM-CZ02-V3-eSA-10-LH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-LH | 9.8207 | 3.7033 | 1741.7542 | 0 | 3.4 | 1741.7542 | 1866.9563
DEER-SFAM-CZ02-V3-eSA-10-LL-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-LL | 9.4732 | 3.9481 | 1796.4183 | 0 | 3.4 | 1796.4183 | 1921.5569
DEER-SFAM-CZ02-V3-eSA-10-LM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-LM | 9.7375 | 3.7288 | 1742.0408 | 0 | 3.4 | 1742.0408 | 1867.2466
DEER-SFAM-CZ02-V3-eSA-10-MH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-MH | 9.7236 | 3.6049 | 1744.2046 | 0 | 3.4 | 1744.2046 | 1869.3778
DEER-SFAM-CZ02-V3-eSA-10-ML-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-ML | 9.2712 | 3.9956 | 1835.6898 | 0 | 3.4 | 1835.6898 | 1960.8108
DEER-SFAM-CZ02-V3-eSA-10-MM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSA-10 | CZ02-V3-eSA-10-MM | 9.5787 | 3.426 | 1730.5324 | 0 | 3.05 | 1730.5324 | 1855.5838
DEER-SFAM-CZ02-V3-eSA-13-HH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-HH | 12.2765 | 3.1663 | 1386.8501 | 0 | 3.4 | 1386.8501 | 1499.6361
DEER-SFAM-CZ02-V3-eSA-13-HL-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-HL | 11.8145 | 3.3458 | 1401.5669 | 0 | 3.4 | 1401.5669 | 1500.2814
DEER-SFAM-CZ02-V3-eSA-13-HM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-HM | 12.2615 | 3.2186 | 1378.3504 | 0 | 3.4 | 1378.3504 | 1491.1049
DEER-SFAM-CZ02-V3-eSA-13-LH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-LH | 12.5113 | 2.8878 | 1331.9625 | 0 | 3.4 | 1331.9625 | 1457.1071
DEER-SFAM-CZ02-V3-eSA-13-LL-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-LL | 12.1327 | 3.1175 | 1393.8607 | 0 | 3.4 | 1393.8607 | 1518.8057
DEER-SFAM-CZ02-V3-eSA-13-LM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-LM | 11.9737 | 3.0136 | 1396.8316 | 0 | 3.4 | 1396.8316 | 1521.8938
DEER-SFAM-CZ02-V3-eSA-13-MH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-MH | 12.9146 | 3.0671 | 1336.1631 | 0 | 3.4 | 1336.1631 | 1461.2679
DEER-SFAM-CZ02-V3-eSA-13-ML-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-ML | 11.7369 | 3.1969 | 1376.6536 | 0 | 3.4 | 1376.6536 | 1501.3808
DEER-SFAM-CZ02-V3-eSA-13-MM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSA-13 | CZ02-V3-eSA-13-MM | 12.9595 | 3.0838 | 1306.9814 | 0 | 3.4 | 1306.9814 | 1432.0724
DEER-SFAM-CZ02-V3-eSA-14-HH-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-HH | 12.0831 | 3.0653 | 1333.2631 | 0 | 3.4 | 1333.2631 | 1438.123
DEER-SFAM-CZ02-V3-eSA-14-HL-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-HL | 13.2385 | 3.0878 | 1287.6324 | 0 | 3.4 | 1287.6324 | 1364.7425
DEER-SFAM-CZ02-V3-eSA-14-HM-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-HM | 12.5661 | 3.1233 | 1343.3234 | 0 | 3.4 | 1343.3234 | 1461.6086
DEER-SFAM-CZ02-V3-eSA-14-MH-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-MH | 12.886 | 2.806 | 1322.5724 | 0 | 3.4 | 1322.5724 | 1404.7879
DEER-SFAM-CZ02-V3-eSA-14-ML-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-ML | 12.517 | 3.0244 | 1309.0102 | 0 | 3.4 | 1309.0102 | 1440.2882
DEER-SFAM-CZ02-V3-eSA-14-MM-s1 | 14 | CZ02 | V3 | CZ02-V3-eSA-14 | CZ02-V3-eSA-14-MM | 12.8633 | 2.8196 | 1293.8942 | 0 | 3.4 | 1293.8942 | 1384.0232
DEER-SFAM-CZ02-V3-eSA-15-HH-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-HH | 14.1014 | 2.7671 | 1194.6983 | 0 | 3.4 | 1194.6983 | 1282.1113
DEER-SFAM-CZ02-V3-eSA-15-HL-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-HL | 14.3327 | 2.8742 | 1181.5648 | 0 | 3.4 | 1181.5648 | 1290.5178
DEER-SFAM-CZ02-V3-eSA-15-HM-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-HM | 14.075 | 2.6946 | 1190.3845 | 0 | 3.4 | 1190.3845 | 1278.1236
DEER-SFAM-CZ02-V3-eSA-15-MH-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-MH | 13.2504 | 2.8891 | 1236.2718 | 0 | 3.4 | 1236.2718 | 1301.4079
DEER-SFAM-CZ02-V3-eSA-15-ML-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-ML | 14.0074 | 2.807 | 1215.6157 | 0 | 3.4 | 1215.6157 | 1303.2324
DEER-SFAM-CZ02-V3-eSA-15-MM-s1 | 15 | CZ02 | V3 | CZ02-V3-eSA-15 | CZ02-V3-eSA-15-MM | 13.6335 | 2.8451 | 1215.1061 | 0 | 3.4 | 1215.1061 | 1294.9754
DEER-SFAM-CZ02-V3-eSA-16-CH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-CH | 14.3946 | 3.0139 | 1307.4534 | 0 | 3.4 | 1307.4534 | 1357.7166
DEER-SFAM-CZ02-V3-eSA-16-CL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-CL | 14.8248 | 2.9083 | 1228.4374 | 0 | 3.4 | 1228.4374 | 1292.0016
DEER-SFAM-CZ02-V3-eSA-16-CM-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-CM | 14.4939 | 2.9619 | 1267.0733 | 0 | 3.4 | 1267.0733 | 1334.0724
DEER-SFAM-CZ02-V3-eSA-16-LH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-LH | 14.7116 | 2.7298 | 1138.8465 | 0 | 3.4 | 1138.8465 | 1225.3196
DEER-SFAM-CZ02-V3-eSA-16-LL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-LL | 14.162 | 2.9457 | 1195.6855 | 0 | 3.4 | 1195.6855 | 1252.4548
DEER-SFAM-CZ02-V3-eSA-16-LM-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-LM | 14.0691 | 2.8437 | 1202.2299 | 0 | 3.4 | 1202.2299 | 1253.6862
DEER-SFAM-CZ02-V3-eSA-16-NM-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-NM | 15.6899 | 2.6418 | 1103.7861 | 0 | 3.4 | 1103.7861 | 1154.3189
DEER-SFAM-CZ02-V3-eSA-16-TH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-TH | 14.2391 | 3.1745 | 1307.2936 | 0 | 3.4 | 1307.2936 | 1339.6227
DEER-SFAM-CZ02-V3-eSA-16-TL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSA-16 | CZ02-V3-eSA-16-TL | 15.3297 | 2.9494 | 1184.1082 | 0 | 3.4 | 1184.1082 | 1219.0009
DEER-SFAM-CZ02-V3-eSA-17-CH-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-CH | 15.3031 | 2.8689 | 1212.6525 | 0 | 3.4 | 1212.6525 | 1276.1879
DEER-SFAM-CZ02-V3-eSA-17-CL-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-CL | 15.248 | 2.8868 | 1209.5794 | 0 | 3.4 | 1209.5794 | 1273.1
DEER-SFAM-CZ02-V3-eSA-17-CM-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-CM | 15.3711 | 2.8899 | 1216.7678 | 0 | 3.4 | 1216.7678 | 1266.883
DEER-SFAM-CZ02-V3-eSA-17-LH-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-LH | 15.1142 | 2.6611 | 1106.0426 | 0 | 3.4 | 1106.0426 | 1173.8084
DEER-SFAM-CZ02-V3-eSA-17-LL-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-LL | 14.8687 | 2.8223 | 1145.3648 | 0 | 3.4 | 1145.3648 | 1182.1933
DEER-SFAM-CZ02-V3-eSA-17-LM-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-LM | 14.7282 | 2.7716 | 1153.3389 | 0 | 3.4 | 1153.3389 | 1185.1804
DEER-SFAM-CZ02-V3-eSA-17-TH-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-TH | 16.0498 | 2.6925 | 1129.049 | 0 | 3.4 | 1129.049 | 1180.7701
DEER-SFAM-CZ02-V3-eSA-17-TL-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-TL | 16.7608 | 2.6527 | 1038.4796 | 0 | 3.4 | 1038.4796 | 1119.0862
DEER-SFAM-CZ02-V3-eSA-17-TM-s2 | 17 | CZ02 | V3 | CZ02-V3-eSA-17 | CZ02-V3-eSA-17-TM | 16.5746 | 2.8423 | 1173.9845 | 0 | 3.4 | 1173.9845 | 1200.9165
DEER-SFAM-CZ02-V3-eSA-18-LH-s2 | 18 | CZ02 | V3 | CZ02-V3-eSA-18 | CZ02-V3-eSA-18-LH | 15.7761 | 2.6111 | 1074.0095 | 0 | 3.4 | 1074.0095 | 1118.3827
DEER-SFAM-CZ02-V3-eSA-18-LL-s2 | 18 | CZ02 | V3 | CZ02-V3-eSA-18 | CZ02-V3-eSA-18-LL | 15.9618 | 2.5985 | 1053.24 | 0 | 3.4 | 1053.24 | 1111.1863
DEER-SFAM-CZ02-V3-eSA-18-TH-s2 | 18 | CZ02 | V3 | CZ02-V3-eSA-18 | CZ02-V3-eSA-18-TH | 16.9352 | 2.5404 | 1078.5645 | 0 | 3.4 | 1078.5645 | 1113.6981
DEER-SFAM-CZ02-V3-eSA-18-TL-s2 | 18 | CZ02 | V3 | CZ02-V3-eSA-18 | CZ02-V3-eSA-18-TL | 16.3435 | 2.8689 | 1147.6146 | 0 | 3.4 | 1147.6146 | 1186.1882
DEER-SFAM-CZ02-V3-eSA-18-TM-s2 | 18 | CZ02 | V3 | CZ02-V3-eSA-18 | CZ02-V3-eSA-18-TM | 16.0688 | 2.6089 | 1120.0332 | 0 | 3.4 | 1120.0332 | 1155.9481
DEER-SFAM-CZ02-V3-eSH-10-HH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-HH | 9.7517 | 3.8035 | 1732.3921 | 2782.664 | 3.4 | 4515.0562 | 2006.6062
DEER-SFAM-CZ02-V3-eSH-10-HL-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-HL | 9.4523 | 3.9759 | 1789.7642 | 2812.8705 | 3.4 | 4602.6347 | 2058.8847
DEER-SFAM-CZ02-V3-eSH-10-HM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-HM | 9.8411 | 3.8941 | 1761.9643 | 2776.8094 | 3.4 | 4538.7738 | 2019.8238
DEER-SFAM-CZ02-V3-eSH-10-LH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-LH | 9.8851 | 3.5706 | 1723.8666 | 2904.238 | 3.4 | 4628.1047 | 2006.7547
DEER-SFAM-CZ02-V3-eSH-10-LL-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-LL | 9.7887 | 3.8723 | 1752.7767 | 2860.8043 | 3.4 | 4613.5809 | 2047.281
DEER-SFAM-CZ02-V3-eSH-10-LM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-LM | 10.0337 | 3.6997 | 1716.0546 | 2822.8251 | 3.4 | 4538.8796 | 1986.8797
DEER-SFAM-CZ02-V3-eSH-10-MH-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-MH | 9.8963 | 3.6997 | 1729.9857 | 2883.3423 | 3.4 | 4613.3281 | 2029.928
DEER-SFAM-CZ02-V3-eSH-10-ML-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-ML | 9.7413 | 4.0457 | 1776.1345 | 2726.0772 | 3.4 | 4502.2117 | 2050.5117
DEER-SFAM-CZ02-V3-eSH-10-MM-s1 | 10 | CZ02 | V3 | CZ02-V3-eSH-10 | CZ02-V3-eSH-10-MM | 9.7647 | 3.7992 | 1767.9793 | 2823.1022 | 3.4 | 4591.0815 | 2022.9815
DEER-SFAM-CZ02-V3-eSH-13-HH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-HH | 11.8822 | 3.1788 | 1418.8053 | 2710.9734 | 3.4 | 4129.7787 | 1669.3787
DEER-SFAM-CZ02-V3-eSH-13-HL-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-HL | 12.564 | 3.3256 | 1370.0798 | 2361.5527 | 3.4 | 3731.6325 | 1619.3825
DEER-SFAM-CZ02-V3-eSH-13-HM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-HM | 12.1449 | 3.1641 | 1392.001 | 2433.8496 | 3.4 | 3825.8506 | 1618.6006
DEER-SFAM-CZ02-V3-eSH-13-LH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-LH | 12.2951 | 2.9249 | 1358.0845 | 2791.3163 | 3.4 | 4149.4008 | 1730.6508
DEER-SFAM-CZ02-V3-eSH-13-LL-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-LL | 13.2826 | 3.0413 | 1298.9642 | 2466.922 | 3.4 | 3765.8862 | 1528.2362
DEER-SFAM-CZ02-V3-eSH-13-LM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-LM | 11.7443 | 3.0808 | 1414.667 | 2132.678 | 3.4 | 3547.345 | 1674.495
DEER-SFAM-CZ02-V3-eSH-13-MH-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-MH | 12.9043 | 3.005 | 1320.0849 | 2716.8962 | 3.4 | 4036.9812 | 1569.9312
DEER-SFAM-CZ02-V3-eSH-13-ML-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-ML | 11.6427 | 3.2881 | 1437.3828 | 2507.5368 | 3.4 | 3944.9196 | 1693.6696
DEER-SFAM-CZ02-V3-eSH-13-MM-s1 | 13 | CZ02 | V3 | CZ02-V3-eSH-13 | CZ02-V3-eSH-13-MM | 12.5484 | 3.2153 | 1374.3389 | 2552.3193 | 3.4 | 3926.6581 | 1574.9581
DEER-SFAM-CZ02-V3-eSH-14-HH-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-HH | 12.5797 | 3.0312 | 1338.8775 | 2495.7656 | 3.4 | 3834.6431 | 1529.8431
DEER-SFAM-CZ02-V3-eSH-14-HL-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-HL | 12.8646 | 3.0105 | 1307.802 | 2464.7568 | 3.4 | 3772.5588 | 1536.2587
DEER-SFAM-CZ02-V3-eSH-14-HM-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-HM | 12.8131 | 2.8893 | 1307.1059 | 2448.9934 | 3.4 | 3756.0993 | 1470.6994
DEER-SFAM-CZ02-V3-eSH-14-MH-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-MH | 13.1218 | 2.7418 | 1268.3601 | 2573.0925 | 3.4 | 3841.4526 | 1517.0026
DEER-SFAM-CZ02-V3-eSH-14-ML-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-ML | 13.2131 | 2.9661 | 1267.5284 | 2642.3596 | 3.4 | 3909.8879 | 1575.5379
DEER-SFAM-CZ02-V3-eSH-14-MM-s1 | 14 | CZ02 | V3 | CZ02-V3-eSH-14 | CZ02-V3-eSH-14-MM | 12.9389 | 2.9062 | 1277.9025 | 2377.0729 | 3.4 | 3654.9753 | 1492.5753
DEER-SFAM-CZ02-V3-eSH-15-HH-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-HH | 13.8404 | 2.6613 | 1204.8785 | 2828.9774 | 3.4 | 4033.856 | 1381.0059
DEER-SFAM-CZ02-V3-eSH-15-HL-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-HL | 14.0389 | 2.8741 | 1215.2882 | 2132.6759 | 3.4 | 3347.964 | 1390.664
DEER-SFAM-CZ02-V3-eSH-15-HM-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-HM | 14.2777 | 2.7933 | 1186.0318 | 2240.4536 | 3.4 | 3426.4855 | 1359.8854
DEER-SFAM-CZ02-V3-eSH-15-MH-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-MH | 13.7378 | 2.8558 | 1224.6022 | 2457.6779 | 3.4 | 3682.2801 | 1391.9801
DEER-SFAM-CZ02-V3-eSH-15-ML-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-ML | 14.1327 | 2.8203 | 1184.2879 | 2342.6017 | 3.4 | 3526.8896 | 1358.6396
DEER-SFAM-CZ02-V3-eSH-15-MM-s1 | 15 | CZ02 | V3 | CZ02-V3-eSH-15 | CZ02-V3-eSH-15-MM | 14.5366 | 2.7921 | 1175.1731 | 2535.0831 | 3.4 | 3710.2562 | 1361.8562
DEER-SFAM-CZ02-V3-eSH-16-CH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-CH | 14.6914 | 2.8838 | 1260.366 | 2582.8542 | 3.4 | 3843.2202 | 1426.8702
DEER-SFAM-CZ02-V3-eSH-16-CL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-CL | 14.8208 | 3.0282 | 1277.6879 | 2414.1497 | 3.4 | 3691.8376 | 1450.0876
DEER-SFAM-CZ02-V3-eSH-16-LH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-LH | 14.4508 | 2.7125 | 1154.6305 | 2661.0855 | 3.4 | 3815.716 | 1332.716
DEER-SFAM-CZ02-V3-eSH-16-LL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-LL | 14.0408 | 2.9043 | 1201.9588 | 2451.9084 | 3.4 | 3653.8673 | 1345.3673
DEER-SFAM-CZ02-V3-eSH-16-LM-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-LM | 14.0015 | 2.8161 | 1197.9134 | 2672.8021 | 3.4 | 3870.7155 | 1396.8655
DEER-SFAM-CZ02-V3-eSH-16-TH-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-TH | 15.559 | 2.9277 | 1166.218 | 3195.5341 | 3.4 | 4361.7521 | 1342.4521
DEER-SFAM-CZ02-V3-eSH-16-TL-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-TL | 14.3057 | 3.2349 | 1308.3119 | 3125.3385 | 3.4 | 4433.6503 | 1469.5003
DEER-SFAM-CZ02-V3-eSH-16-TM-s2 | 16 | CZ02 | V3 | CZ02-V3-eSH-16 | CZ02-V3-eSH-16-TM | 14.5029 | 3.1736 | 1290.6673 | 3163.9736 | 3.4 | 4454.6409 | 1456.3409
DEER-SFAM-CZ02-V3-eSH-17-CM-s2 | 17 | CZ02 | V3 | CZ02-V3-eSH-17 | CZ02-V3-eSH-17-CM | 15.6501 | 2.8775 | 1208.4931 | 2495.8954 | 3.4 | 3704.3884 | 1387.4885
DEER-SFAM-CZ02-V3-eSH-17-LM-s2 | 17 | CZ02 | V3 | CZ02-V3-eSH-17 | CZ02-V3-eSH-17-LM | 14.8792 | 2.7832 | 1165.0989 | 2375.4362 | 3.4 | 3540.535 | 1245.6351
DEER-SFAM-CZ02-V3-eSH-17-TH-s2 | 17 | CZ02 | V3 | CZ02-V3-eSH-17 | CZ02-V3-eSH-17-TH | 16.1711 | 2.7505 | 1113.5173 | 3188.5869 | 3.4 | 4302.1041 | 1303.6041
DEER-SFAM-CZ02-V3-eSH-17-TL-s2 | 17 | CZ02 | V3 | CZ02-V3-eSH-17 | CZ02-V3-eSH-17-TL | 16.1268 | 2.8119 | 1121.3517 | 3160.8187 | 3.4 | 4282.1704 | 1308.5204
DEER-SFAM-CZ02-V3-eSH-18-LH-s2 | 18 | CZ02 | V3 | CZ02-V3-eSH-18 | CZ02-V3-eSH-18-LH | 15.6036 | 2.6256 | 1079.3485 | 2735.2976 | 3.4 | 3814.6462 | 1213.6462
DEER-SFAM-CZ02-V3-eSH-18-LL-s2 | 18 | CZ02 | V3 | CZ02-V3-eSH-18 | CZ02-V3-eSH-18-LL | 14.922 | 2.7044 | 1124.7677 | 2461.3419 | 3.4 | 3586.1096 | 1248.6597
DEER-SFAM-CZ02-V3-eSH-18-LM-s2 | 18 | CZ02 | V3 | CZ02-V3-eSH-18 | CZ02-V3-eSH-18-LM | 15.7235 | 2.6644 | 1079.7538 | 2879.0478 | 3.4 | 3958.8016 | 1233.7516
DEER-SFAM-CZ02-V3-eSH-18-TM-s2 | 18 | CZ02 | V3 | CZ02-V3-eSH-18 | CZ02-V3-eSH-18-TM | 16.5583 | 2.7529 | 1102.7048 | 3156.6297 | 3.4 | 4259.3345 | 1379.2344
DEER-SFAM-CZ02-V4-eSA-10-HH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-HH | 9.5682 | 3.7421 | 1715.1076 | 0 | 3.4 | 1715.1076 | 1828.0962
DEER-SFAM-CZ02-V4-eSA-10-HL-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-HL | 9.262 | 4.0979 | 1778.8441 | 0 | 3.4 | 1778.8441 | 1891.9063
DEER-SFAM-CZ02-V4-eSA-10-HM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-HM | 9.2565 | 3.8127 | 1747.8215 | 0 | 3.4 | 1747.8215 | 1860.871
DEER-SFAM-CZ02-V4-eSA-10-LH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-LH | 9.8229 | 3.6761 | 1695.2341 | 0 | 3.4 | 1695.2341 | 1808.3717
DEER-SFAM-CZ02-V4-eSA-10-LL-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-LL | 9.4852 | 3.9086 | 1745.106 | 0 | 3.4 | 1745.106 | 1858.1865
DEER-SFAM-CZ02-V4-eSA-10-LM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-LM | 9.7399 | 3.7012 | 1695.3357 | 0 | 3.4 | 1695.3357 | 1808.4767
DEER-SFAM-CZ02-V4-eSA-10-MH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-MH | 9.7193 | 3.5793 | 1698.6261 | 0 | 3.4 | 1698.6261 | 1811.7377
DEER-SFAM-CZ02-V4-eSA-10-ML-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-ML | 9.2822 | 3.9653 | 1785.3949 | 0 | 3.4 | 1785.3949 | 1898.459
DEER-SFAM-CZ02-V4-eSA-10-MM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSA-10 | CZ02-V4-eSA-10-MM | 9.4884 | 3.6989 | 1706.2384 | 0 | 3.4 | 1706.2384 | 1819.3109
DEER-SFAM-CZ02-V4-eSA-13-HH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-HH | 12.2528 | 3.1397 | 1346.2272 | 0 | 3.4 | 1346.2272 | 1448.1451
DEER-SFAM-CZ02-V4-eSA-13-HL-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-HL | 11.8257 | 3.3155 | 1360.395 | 0 | 3.4 | 1360.395 | 1449.597
DEER-SFAM-CZ02-V4-eSA-13-HM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-HM | 12.2717 | 3.1879 | 1337.7803 | 0 | 3.4 | 1337.7803 | 1439.6692
DEER-SFAM-CZ02-V4-eSA-13-LH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-LH | 12.5024 | 2.863 | 1296.4808 | 0 | 3.4 | 1296.4808 | 1409.5667
DEER-SFAM-CZ02-V4-eSA-13-LL-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-LL | 12.1483 | 3.0942 | 1354.7753 | 0 | 3.4 | 1354.7753 | 1467.6846
DEER-SFAM-CZ02-V4-eSA-13-LM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-LM | 11.9772 | 2.9915 | 1358.3371 | 0 | 3.4 | 1358.3371 | 1471.3476
DEER-SFAM-CZ02-V4-eSA-13-MH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-MH | 12.928 | 3.041 | 1296.88 | 0 | 3.4 | 1296.88 | 1409.93
DEER-SFAM-CZ02-V4-eSA-13-ML-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-ML | 11.7345 | 3.1706 | 1335.9335 | 0 | 3.4 | 1335.9335 | 1448.6413
DEER-SFAM-CZ02-V4-eSA-13-MM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSA-13 | CZ02-V4-eSA-13-MM | 12.9631 | 3.0589 | 1270.0179 | 0 | 3.4 | 1270.0179 | 1383.0541
DEER-SFAM-CZ02-V4-eSA-14-HH-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-HH | 12.0807 | 3.0396 | 1294.8879 | 0 | 3.4 | 1294.8879 | 1389.6427
DEER-SFAM-CZ02-V4-eSA-14-HL-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-HL | 13.2552 | 3.0568 | 1250.1684 | 0 | 3.4 | 1250.1684 | 1319.8475
DEER-SFAM-CZ02-V4-eSA-14-HM-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-HM | 12.5864 | 3.096 | 1305.4473 | 0 | 3.4 | 1305.4473 | 1412.3346
DEER-SFAM-CZ02-V4-eSA-14-MH-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-MH | 12.8918 | 2.7849 | 1286.4825 | 0 | 3.4 | 1286.4825 | 1360.7759
DEER-SFAM-CZ02-V4-eSA-14-ML-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-ML | 12.5208 | 2.9972 | 1269.9857 | 0 | 3.4 | 1269.9857 | 1388.6138
DEER-SFAM-CZ02-V4-eSA-14-MM-s1 | 14 | CZ02 | V4 | CZ02-V4-eSA-14 | CZ02-V4-eSA-14-MM | 12.8659 | 2.7992 | 1259.2352 | 0 | 3.4 | 1259.2352 | 1340.6787
DEER-SFAM-CZ02-V4-eSA-15-HH-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-HH | 14.1041 | 2.7401 | 1160.2449 | 0 | 3.4 | 1160.2449 | 1239.2345
DEER-SFAM-CZ02-V4-eSA-15-HL-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-HL | 14.3728 | 2.8454 | 1144.7982 | 0 | 3.4 | 1144.7982 | 1243.2517
DEER-SFAM-CZ02-V4-eSA-15-HM-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-HM | 14.072 | 2.6677 | 1155.936 | 0 | 3.4 | 1155.936 | 1235.2201
DEER-SFAM-CZ02-V4-eSA-15-MH-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-MH | 13.2517 | 2.8641 | 1200.9118 | 0 | 3.4 | 1200.9118 | 1259.771
DEER-SFAM-CZ02-V4-eSA-15-ML-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-ML | 14.0269 | 2.7813 | 1181.4545 | 0 | 3.4 | 1181.4545 | 1260.6314
DEER-SFAM-CZ02-V4-eSA-15-MM-s1 | 15 | CZ02 | V4 | CZ02-V4-eSA-15 | CZ02-V4-eSA-15-MM | 13.6498 | 2.8205 | 1179.4168 | 0 | 3.4 | 1179.4168 | 1251.5896
DEER-SFAM-CZ02-V4-eSA-16-CH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-CH | 14.4293 | 2.9861 | 1272.1463 | 0 | 3.4 | 1272.1463 | 1317.5875
DEER-SFAM-CZ02-V4-eSA-16-CL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-CL | 14.8665 | 2.8745 | 1194.7333 | 0 | 3.4 | 1194.7333 | 1252.1965
DEER-SFAM-CZ02-V4-eSA-16-CM-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-CM | 14.5204 | 2.9313 | 1234.6195 | 0 | 3.4 | 1234.6195 | 1295.1916
DEER-SFAM-CZ02-V4-eSA-16-LH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-LH | 14.7117 | 2.7012 | 1108.3799 | 0 | 3.4 | 1108.3799 | 1186.5332
DEER-SFAM-CZ02-V4-eSA-16-LL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-LL | 14.1695 | 2.9172 | 1163.7781 | 0 | 3.4 | 1163.7781 | 1215.084
DEER-SFAM-CZ02-V4-eSA-16-LM-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-LM | 14.0797 | 2.815 | 1169.9767 | 0 | 3.4 | 1169.9767 | 1216.4823
DEER-SFAM-CZ02-V4-eSA-16-NM-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-NM | 15.726 | 2.6089 | 1071.8643 | 0 | 3.4 | 1071.8643 | 1117.5355
DEER-SFAM-CZ02-V4-eSA-16-TH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-TH | 14.2548 | 3.1432 | 1273.3413 | 0 | 3.4 | 1273.3413 | 1302.5677
DEER-SFAM-CZ02-V4-eSA-16-TL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSA-16 | CZ02-V4-eSA-16-TL | 15.3628 | 2.9183 | 1149.7811 | 0 | 3.4 | 1149.7811 | 1181.3233
DEER-SFAM-CZ02-V4-eSA-17-CH-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-CH | 15.3357 | 2.8398 | 1180.2625 | 0 | 3.4 | 1180.2625 | 1237.7016
DEER-SFAM-CZ02-V4-eSA-17-CL-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-CL | 15.3001 | 2.8547 | 1175.97 | 0 | 3.4 | 1175.97 | 1233.3954
DEER-SFAM-CZ02-V4-eSA-17-CM-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-CM | 15.4122 | 2.8598 | 1184.7289 | 0 | 3.4 | 1184.7289 | 1230.0365
DEER-SFAM-CZ02-V4-eSA-17-LH-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-LH | 15.1199 | 2.634 | 1075.9179 | 0 | 3.4 | 1075.9179 | 1137.1623
DEER-SFAM-CZ02-V4-eSA-17-LL-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-LL | 14.8862 | 2.7963 | 1114.0904 | 0 | 3.4 | 1114.0904 | 1147.3788
DEER-SFAM-CZ02-V4-eSA-17-LM-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-LM | 14.748 | 2.7403 | 1122.4714 | 0 | 3.4 | 1122.4714 | 1151.2484
DEER-SFAM-CZ02-V4-eSA-17-TH-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-TH | 16.0798 | 2.667 | 1100.311 | 0 | 3.4 | 1100.311 | 1147.0649
DEER-SFAM-CZ02-V4-eSA-17-TL-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-TL | 16.8486 | 2.6262 | 1010.5085 | 0 | 3.4 | 1010.5085 | 1083.3899
DEER-SFAM-CZ02-V4-eSA-17-TM-s2 | 17 | CZ02 | V4 | CZ02-V4-eSA-17 | CZ02-V4-eSA-17-TM | 16.5843 | 2.8241 | 1141.0561 | 0 | 3.4 | 1141.0561 | 1165.4088
DEER-SFAM-CZ02-V4-eSA-18-LH-s2 | 18 | CZ02 | V4 | CZ02-V4-eSA-18 | CZ02-V4-eSA-18-LH | 15.7837 | 2.5848 | 1045.4902 | 0 | 3.4 | 1045.4902 | 1085.5938
DEER-SFAM-CZ02-V4-eSA-18-LL-s2 | 18 | CZ02 | V4 | CZ02-V4-eSA-18 | CZ02-V4-eSA-18-LL | 15.9902 | 2.5699 | 1023.8255 | 0 | 3.4 | 1023.8255 | 1076.1954
DEER-SFAM-CZ02-V4-eSA-18-TH-s2 | 18 | CZ02 | V4 | CZ02-V4-eSA-18 | CZ02-V4-eSA-18-TH | 16.9275 | 2.5154 | 1049.5573 | 0 | 3.4 | 1049.5573 | 1081.3156
DEER-SFAM-CZ02-V4-eSA-18-TL-s2 | 18 | CZ02 | V4 | CZ02-V4-eSA-18 | CZ02-V4-eSA-18-TL | 16.3512 | 2.842 | 1117.1027 | 0 | 3.4 | 1117.1027 | 1151.9741
DEER-SFAM-CZ02-V4-eSA-18-TM-s2 | 18 | CZ02 | V4 | CZ02-V4-eSA-18 | CZ02-V4-eSA-18-TM | 16.0973 | 2.5833 | 1091.5617 | 0 | 3.4 | 1091.5617 | 1124.0268
DEER-SFAM-CZ02-V4-eSH-10-HH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-HH | 9.7556 | 3.7688 | 1682.1284 | 2527.2574 | 3.4 | 4209.3858 | 1930.4358
DEER-SFAM-CZ02-V4-eSH-10-HL-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-HL | 9.4582 | 3.9415 | 1735.5767 | 2552.0715 | 3.4 | 4287.6482 | 1979.1982
DEER-SFAM-CZ02-V4-eSH-10-HM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-HM | 9.8447 | 3.8707 | 1709.1571 | 2519.5116 | 3.4 | 4228.6687 | 1942.6187
DEER-SFAM-CZ02-V4-eSH-10-LH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-LH | 9.8819 | 3.5455 | 1677.8761 | 2637.8678 | 3.4 | 4315.7439 | 1934.0439
DEER-SFAM-CZ02-V4-eSH-10-LL-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-LL | 9.8006 | 3.8377 | 1701.3681 | 2595.2031 | 3.4 | 4296.5711 | 1968.0711
DEER-SFAM-CZ02-V4-eSH-10-LM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-LM | 10.0307 | 3.6709 | 1667.6485 | 2563.8864 | 3.4 | 4231.5349 | 1912.8848
DEER-SFAM-CZ02-V4-eSH-10-MH-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-MH | 9.8989 | 3.6741 | 1684.402 | 2617.5107 | 3.4 | 4301.9127 | 1956.0126
DEER-SFAM-CZ02-V4-eSH-10-ML-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-ML | 9.7523 | 4.0098 | 1723.8471 | 2472.3716 | 3.4 | 4196.2186 | 1972.3686
DEER-SFAM-CZ02-V4-eSH-10-MM-s1 | 10 | CZ02 | V4 | CZ02-V4-eSH-10 | CZ02-V4-eSH-10-MM | 9.7744 | 3.7713 | 1719.8083 | 2560.9121 | 3.4 | 4280.7203 | 1950.6704
DEER-SFAM-CZ02-V4-eSH-13-HH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-HH | 11.8805 | 3.1505 | 1376.0395 | 2458.6242 | 3.4 | 3834.6637 | 1602.9637
DEER-SFAM-CZ02-V4-eSH-13-HL-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-HL | 12.5828 | 3.295 | 1328.9885 | 2139.9566 | 3.4 | 3468.9451 | 1554.7451
DEER-SFAM-CZ02-V4-eSH-13-HM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-HM | 12.1463 | 3.1347 | 1349.8307 | 2206.8 | 3.4 | 3556.6307 | 1555.0306
DEER-SFAM-CZ02-V4-eSH-13-LH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-LH | 12.2932 | 2.903 | 1323.8403 | 2525.0718 | 3.4 | 3848.9122 | 1661.4122
DEER-SFAM-CZ02-V4-eSH-13-LL-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-LL | 13.2975 | 3.0154 | 1261.0813 | 2235.2342 | 3.4 | 3496.3156 | 1468.7156
DEER-SFAM-CZ02-V4-eSH-13-LM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-LM | 11.7469 | 3.0574 | 1375.5934 | 1933.7803 | 3.4 | 3309.3737 | 1610.8237
DEER-SFAM-CZ02-V4-eSH-13-MH-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-MH | 12.9261 | 2.9813 | 1281.1999 | 2466.3684 | 3.4 | 3747.5683 | 1507.4183
DEER-SFAM-CZ02-V4-eSH-13-ML-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-ML | 11.659 | 3.2617 | 1396.2101 | 2271.6558 | 3.4 | 3667.8659 | 1628.2659
DEER-SFAM-CZ02-V4-eSH-13-MM-s1 | 13 | CZ02 | V4 | CZ02-V4-eSH-13 | CZ02-V4-eSH-13-MM | 12.5636 | 3.1877 | 1333.4731 | 2314.0511 | 3.4 | 3647.5242 | 1515.0742
DEER-SFAM-CZ02-V4-eSH-14-HH-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-HH | 12.5817 | 3.0036 | 1300.3166 | 2263.0323 | 3.4 | 3563.3488 | 1473.2488
DEER-SFAM-CZ02-V4-eSH-14-HL-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-HL | 12.8766 | 2.9809 | 1268.8179 | 2230.9929 | 3.4 | 3499.8108 | 1475.7108
DEER-SFAM-CZ02-V4-eSH-14-HM-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-HM | 12.8155 | 2.8613 | 1269.2218 | 2219.265 | 3.4 | 3488.4868 | 1417.3867
DEER-SFAM-CZ02-V4-eSH-14-MH-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-MH | 13.1204 | 2.7215 | 1235.1054 | 2327.6504 | 3.4 | 3562.7558 | 1460.4058
DEER-SFAM-CZ02-V4-eSH-14-ML-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-ML | 13.2206 | 2.9415 | 1231.2112 | 2387.9019 | 3.4 | 3619.113 | 1510.313
DEER-SFAM-CZ02-V4-eSH-14-MM-s1 | 14 | CZ02 | V4 | CZ02-V4-eSH-14 | CZ02-V4-eSH-14-MM | 12.9451 | 2.881 | 1240.2422 | 2153.2982 | 3.4 | 3393.5404 | 1434.6403
DEER-SFAM-CZ02-V4-eSH-15-HH-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-HH | 13.8332 | 2.635 | 1170.1574 | 2551.2802 | 3.4 | 3721.4376 | 1329.7876
DEER-SFAM-CZ02-V4-eSH-15-HL-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-HL | 14.0515 | 2.8484 | 1179.2404 | 1931.5923 | 3.4 | 3110.8328 | 1338.0328
DEER-SFAM-CZ02-V4-eSH-15-HM-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-HM | 14.3085 | 2.7682 | 1149.8473 | 2029.8249 | 3.4 | 3179.6722 | 1307.2722
DEER-SFAM-CZ02-V4-eSH-15-MH-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-MH | 13.7503 | 2.8264 | 1189.322 | 2224.8592 | 3.4 | 3414.1812 | 1340.9312
DEER-SFAM-CZ02-V4-eSH-15-ML-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-ML | 14.1445 | 2.7967 | 1151.133 | 2120.1392 | 3.4 | 3271.2722 | 1309.0722
DEER-SFAM-CZ02-V4-eSH-15-MM-s1 | 15 | CZ02 | V4 | CZ02-V4-eSH-15 | CZ02-V4-eSH-15-MM | 14.5786 | 2.7665 | 1139.6623 | 2292.6203 | 3.4 | 3432.2825 | 1308.7825
DEER-SFAM-CZ02-V4-eSH-16-CH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-CH | 14.7227 | 2.8532 | 1226.8804 | 2333.6001 | 3.4 | 3560.4805 | 1376.1805
DEER-SFAM-CZ02-V4-eSH-16-CL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-CL | 14.853 | 3.0039 | 1244.4577 | 2180.7787 | 3.4 | 3425.2364 | 1399.0864
DEER-SFAM-CZ02-V4-eSH-16-LH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-LH | 14.4418 | 2.6851 | 1124.9714 | 2404.703 | 3.4 | 3529.6744 | 1285.8744
DEER-SFAM-CZ02-V4-eSH-16-LL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-LL | 14.0605 | 2.8733 | 1168.8845 | 2212.6103 | 3.4 | 3381.4947 | 1298.4947
DEER-SFAM-CZ02-V4-eSH-16-LM-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-LM | 13.9998 | 2.7864 | 1165.9908 | 2412.2778 | 3.4 | 3578.2686 | 1345.8186
DEER-SFAM-CZ02-V4-eSH-16-TH-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-TH | 15.5698 | 2.8972 | 1133.2897 | 2894.1602 | 3.4 | 4027.45 | 1289.6499
DEER-SFAM-CZ02-V4-eSH-16-TL-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-TL | 14.3485 | 3.2024 | 1270.9875 | 2826.0992 | 3.4 | 4097.0866 | 1413.9366
DEER-SFAM-CZ02-V4-eSH-16-TM-s2 | 16 | CZ02 | V4 | CZ02-V4-eSH-16 | CZ02-V4-eSH-16-TM | 14.533 | 3.1435 | 1255.0354 | 2862.6917 | 3.4 | 4117.7271 | 1402.0271
DEER-SFAM-CZ02-V4-eSH-17-CM-s2 | 17 | CZ02 | V4 | CZ02-V4-eSH-17 | CZ02-V4-eSH-17-CM | 15.6843 | 2.854 | 1177.0093 | 2254.2926 | 3.4 | 3431.3019 | 1337.4019
DEER-SFAM-CZ02-V4-eSH-17-LM-s2 | 17 | CZ02 | V4 | CZ02-V4-eSH-17 | CZ02-V4-eSH-17-LM | 14.8819 | 2.7618 | 1131.7497 | 2145.1377 | 3.4 | 3276.8874 | 1204.5374
DEER-SFAM-CZ02-V4-eSH-17-TH-s2 | 17 | CZ02 | V4 | CZ02-V4-eSH-17 | CZ02-V4-eSH-17-TH | 16.211 | 2.7221 | 1083.2285 | 2886.071 | 3.4 | 3969.2995 | 1252.0995
DEER-SFAM-CZ02-V4-eSH-17-TL-s2 | 17 | CZ02 | V4 | CZ02-V4-eSH-17 | CZ02-V4-eSH-17-TL | 16.1687 | 2.7841 | 1090.5818 | 2860.9999 | 3.4 | 3951.5817 | 1256.8317
DEER-SFAM-CZ02-V4-eSH-18-LH-s2 | 18 | CZ02 | V4 | CZ02-V4-eSH-18 | CZ02-V4-eSH-18-LH | 15.6234 | 2.5993 | 1049.675 | 2462.9468 | 3.4 | 3512.6217 | 1170.2217
DEER-SFAM-CZ02-V4-eSH-18-LL-s2 | 18 | CZ02 | V4 | CZ02-V4-eSH-18 | CZ02-V4-eSH-18-LL | 14.9453 | 2.6776 | 1093.4777 | 2217.8864 | 3.4 | 3311.3641 | 1205.364
DEER-SFAM-CZ02-V4-eSH-18-LM-s2 | 18 | CZ02 | V4 | CZ02-V4-eSH-18 | CZ02-V4-eSH-18-LM | 15.7477 | 2.6359 | 1049.8701 | 2591.4855 | 3.4 | 3641.3556 | 1187.9056
DEER-SFAM-CZ02-V4-eSH-18-TM-s2 | 18 | CZ02 | V4 | CZ02-V4-eSH-18 | CZ02-V4-eSH-18-TM | 16.6293 | 2.7247 | 1071.1571 | 2857.3859 | 3.4 | 3928.543 | 1318.293
DEER-SFAM-CZ03-V1-eSA-10-HH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-HH | 10.4049 | 2.2029 | 324.7956 | 0 | 3.4688 | 324.7956 | 508.5444
DEER-SFAM-CZ03-V1-eSA-10-HL-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-HL | 10.38 | 2.2472 | 322.6924 | 0 | 3.711 | 322.6924 | 506.6591
DEER-SFAM-CZ03-V1-eSA-10-HM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-HM | 10.2364 | 2.2375 | 323.451 | 0 | 3.711 | 323.451 | 507.3943
DEER-SFAM-CZ03-V1-eSA-10-LH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-LH | 10.3994 | 2.1086 | 309.947 | 0 | 3.4688 | 309.947 | 493.9867
DEER-SFAM-CZ03-V1-eSA-10-LL-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-LL | 10.1485 | 2.2673 | 327.6699 | 0 | 3.711 | 327.6699 | 511.6689
DEER-SFAM-CZ03-V1-eSA-10-LM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-LM | 10.3794 | 2.1534 | 312.6413 | 0 | 3.4688 | 312.6413 | 496.687
DEER-SFAM-CZ03-V1-eSA-10-MH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-MH | 10.2645 | 2.1079 | 316.452 | 0 | 3.4688 | 316.452 | 500.4418
DEER-SFAM-CZ03-V1-eSA-10-ML-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-ML | 10.2859 | 2.3136 | 332.0421 | 0 | 3.711 | 332.0421 | 516.0126
DEER-SFAM-CZ03-V1-eSA-10-MM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSA-10 | CZ03-V1-eSA-10-MM | 10.5691 | 2.0453 | 305.7687 | 0 | 3.4688 | 305.7687 | 489.6817
DEER-SFAM-CZ03-V1-eSA-13-HH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-HH | 12.8488 | 1.6616 | 245.768 | 0 | 3.711 | 245.768 | 411.5971
DEER-SFAM-CZ03-V1-eSA-13-HL-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-HL | 13.439 | 1.6517 | 240.932 | 0 | 3.711 | 240.932 | 386.0652
DEER-SFAM-CZ03-V1-eSA-13-HM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-HM | 13.3349 | 1.6961 | 243.5489 | 0 | 3.711 | 243.5489 | 409.3258
DEER-SFAM-CZ03-V1-eSA-13-LH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-LH | 13.2976 | 1.614 | 238.7565 | 0 | 3.4688 | 238.7565 | 422.6952
DEER-SFAM-CZ03-V1-eSA-13-LL-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-LL | 13.4274 | 1.698 | 246.9157 | 0 | 3.4688 | 246.9157 | 430.507
DEER-SFAM-CZ03-V1-eSA-13-LM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-LM | 13.0126 | 1.6737 | 249.5959 | 0 | 3.4688 | 249.5959 | 433.3888
DEER-SFAM-CZ03-V1-eSA-13-MH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-MH | 14.3139 | 1.6177 | 233.0847 | 0 | 3.4688 | 233.0847 | 416.9546
DEER-SFAM-CZ03-V1-eSA-13-ML-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-ML | 13.1529 | 1.6689 | 241.4878 | 0 | 3.4688 | 241.4878 | 424.7903
DEER-SFAM-CZ03-V1-eSA-13-MM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSA-13 | CZ03-V1-eSA-13-MM | 14.3127 | 1.6403 | 231.8099 | 0 | 3.711 | 231.8099 | 415.7297
DEER-SFAM-CZ03-V1-eSA-14-HH-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-HH | 13.6604 | 1.5977 | 232.7279 | 0 | 3.4688 | 232.7279 | 386.8274
DEER-SFAM-CZ03-V1-eSA-14-HL-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-HL | 14.5605 | 1.5333 | 223.086 | 0 | 3.711 | 223.086 | 336.4468
DEER-SFAM-CZ03-V1-eSA-14-HM-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-HM | 14.4654 | 1.5356 | 223.4286 | 0 | 3.4688 | 223.4286 | 397.2827
DEER-SFAM-CZ03-V1-eSA-14-MH-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-MH | 13.8904 | 1.5873 | 237.883 | 0 | 3.4688 | 237.883 | 358.6909
DEER-SFAM-CZ03-V1-eSA-14-ML-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-ML | 13.9655 | 1.5418 | 225.5797 | 0 | 3.4688 | 225.5797 | 418.5255
DEER-SFAM-CZ03-V1-eSA-14-MM-s1 | 14 | CZ03 | V1 | CZ03-V1-eSA-14 | CZ03-V1-eSA-14-MM | 13.9835 | 1.5412 | 229.8106 | 0 | 3.4688 | 229.8106 | 362.2582
DEER-SFAM-CZ03-V1-eSA-15-HH-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-HH | 15.415 | 1.4318 | 208.284 | 0 | 3.711 | 208.284 | 336.7984
DEER-SFAM-CZ03-V1-eSA-15-HL-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-HL | 15.9002 | 1.4074 | 203.7682 | 0 | 3.711 | 203.7682 | 363.9484
DEER-SFAM-CZ03-V1-eSA-15-HM-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-HM | 15.2349 | 1.4321 | 210.6193 | 0 | 3.711 | 210.6193 | 339.6108
DEER-SFAM-CZ03-V1-eSA-15-MH-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-MH | 15.1332 | 1.4205 | 210.7603 | 0 | 3.4688 | 210.7603 | 306.482
DEER-SFAM-CZ03-V1-eSA-15-ML-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-ML | 15.8369 | 1.4629 | 210.5132 | 0 | 3.4688 | 210.5132 | 339.2397
DEER-SFAM-CZ03-V1-eSA-15-MM-s1 | 15 | CZ03 | V1 | CZ03-V1-eSA-15 | CZ03-V1-eSA-15-MM | 15.3044 | 1.4299 | 209.7668 | 0 | 3.4688 | 209.7668 | 327.1419
DEER-SFAM-CZ03-V1-eSA-16-CH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-CH | 16.2273 | 1.6258 | 241.8052 | 0 | 3.711 | 241.8052 | 314.9451
DEER-SFAM-CZ03-V1-eSA-16-CL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-CL | 16.6911 | 1.5469 | 226.3551 | 0 | 3.711 | 226.3551 | 319.2581
DEER-SFAM-CZ03-V1-eSA-16-CM-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-CM | 16.3666 | 1.5852 | 231.8871 | 0 | 3.711 | 231.8871 | 329.9253
DEER-SFAM-CZ03-V1-eSA-16-LH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-LH | 15.8749 | 1.4507 | 221.3748 | 0 | 3.711 | 221.3748 | 347.5127
DEER-SFAM-CZ03-V1-eSA-16-LL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-LL | 15.4901 | 1.5054 | 228.9353 | 0 | 3.711 | 228.9353 | 311.8188
DEER-SFAM-CZ03-V1-eSA-16-LM-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-LM | 15.5041 | 1.5023 | 229.3351 | 0 | 3.4688 | 229.3351 | 304.4108
DEER-SFAM-CZ03-V1-eSA-16-NM-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-NM | 16.7486 | 1.3945 | 221.845 | 0 | 3.4688 | 221.845 | 295.4649
DEER-SFAM-CZ03-V1-eSA-16-TH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-TH | 16.7467 | 1.592 | 242.6476 | 0 | 3.4688 | 242.6476 | 289.271
DEER-SFAM-CZ03-V1-eSA-16-TL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSA-16 | CZ03-V1-eSA-16-TL | 17.4883 | 1.5925 | 231.5093 | 0 | 3.711 | 231.5093 | 282.0084
DEER-SFAM-CZ03-V1-eSA-17-CH-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-CH | 17.3691 | 1.4949 | 220.453 | 0 | 3.711 | 220.453 | 313.3049
DEER-SFAM-CZ03-V1-eSA-17-CL-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-CL | 17.3655 | 1.5014 | 220.3921 | 0 | 3.711 | 220.3921 | 313.2231
DEER-SFAM-CZ03-V1-eSA-17-CM-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-CM | 17.4903 | 1.5183 | 224.4466 | 0 | 3.711 | 224.4466 | 297.3685
DEER-SFAM-CZ03-V1-eSA-17-LH-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-LH | 16.5736 | 1.3666 | 209.1327 | 0 | 3.4688 | 209.1327 | 307.9462
DEER-SFAM-CZ03-V1-eSA-17-LL-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-LL | 16.4906 | 1.4351 | 217.3853 | 0 | 3.711 | 217.3853 | 271.2632
DEER-SFAM-CZ03-V1-eSA-17-LM-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-LM | 16.2537 | 1.4439 | 220.2868 | 0 | 3.711 | 220.2868 | 266.8065
DEER-SFAM-CZ03-V1-eSA-17-TH-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-TH | 19.0676 | 1.3983 | 206.7424 | 0 | 3.711 | 206.7424 | 281.5992
DEER-SFAM-CZ03-V1-eSA-17-TL-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-TL | 20.3135 | 1.3919 | 189.26 | 0 | 3.711 | 189.26 | 306.7822
DEER-SFAM-CZ03-V1-eSA-17-TM-s2 | 17 | CZ03 | V1 | CZ03-V1-eSA-17 | CZ03-V1-eSA-17-TM | 18.6806 | 1.5551 | 231.9266 | 0 | 3.711 | 231.9266 | 270.8743
DEER-SFAM-CZ03-V1-eSA-18-LH-s2 | 18 | CZ03 | V1 | CZ03-V1-eSA-18 | CZ03-V1-eSA-18-LH | 17.3441 | 1.3456 | 205.7398 | 0 | 3.711 | 205.7398 | 270.5191
DEER-SFAM-CZ03-V1-eSA-18-LL-s2 | 18 | CZ03 | V1 | CZ03-V1-eSA-18 | CZ03-V1-eSA-18-LL | 17.8134 | 1.3359 | 199.0995 | 0 | 3.711 | 199.0995 | 283.6387
DEER-SFAM-CZ03-V1-eSA-18-TH-s2 | 18 | CZ03 | V1 | CZ03-V1-eSA-18 | CZ03-V1-eSA-18-TH | 19.4931 | 1.345 | 202.2465 | 0 | 3.711 | 202.2465 | 253.1618
DEER-SFAM-CZ03-V1-eSA-18-TL-s2 | 18 | CZ03 | V1 | CZ03-V1-eSA-18 | CZ03-V1-eSA-18-TL | 19.2879 | 1.4012 | 207.114 | 0 | 3.711 | 207.114 | 262.9599
DEER-SFAM-CZ03-V1-eSA-18-TM-s2 | 18 | CZ03 | V1 | CZ03-V1-eSA-18 | CZ03-V1-eSA-18-TM | 18.967 | 1.3706 | 206.4692 | 0 | 3.4688 | 206.4692 | 258.4401
DEER-SFAM-CZ03-V1-eSH-10-HH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-HH | 10.147 | 2.1132 | 315.0202 | 3645.9223 | 3.711 | 3960.9424 | 696.6306
DEER-SFAM-CZ03-V1-eSH-10-HL-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-HL | 10.1027 | 2.1988 | 322.5228 | 3701.403 | 3.711 | 4023.9258 | 703.9106
DEER-SFAM-CZ03-V1-eSH-10-HM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-HM | 10.6113 | 2.1759 | 317.7089 | 3520.2066 | 3.4688 | 3837.9154 | 681.0259
DEER-SFAM-CZ03-V1-eSH-10-LH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-LH | 10.295 | 2.0869 | 316.8126 | 3861.7503 | 3.4688 | 4178.5629 | 712.157
DEER-SFAM-CZ03-V1-eSH-10-LL-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-LL | 10.354 | 2.1906 | 320.9351 | 3634.4083 | 3.4688 | 3955.3433 | 728.6339
DEER-SFAM-CZ03-V1-eSH-10-LM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-LM | 10.3979 | 2.1425 | 319.5646 | 3583.3379 | 3.4688 | 3902.9025 | 692.7944
DEER-SFAM-CZ03-V1-eSH-10-MH-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-MH | 10.4406 | 2.1082 | 312.3384 | 3794.5898 | 3.4688 | 4106.9282 | 732.1868
DEER-SFAM-CZ03-V1-eSH-10-ML-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-ML | 10.4174 | 2.2087 | 319.6075 | 3389.977 | 3.711 | 3709.5845 | 692.4771
DEER-SFAM-CZ03-V1-eSH-10-MM-s1 | 10 | CZ03 | V1 | CZ03-V1-eSH-10 | CZ03-V1-eSH-10-MM | 10.5603 | 2.2172 | 320.7996 | 3675.051 | 3.4688 | 3995.8506 | 675.4606
DEER-SFAM-CZ03-V1-eSH-13-HH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-HH | 13.318 | 1.6876 | 246.3457 | 3507.625 | 3.711 | 3753.9707 | 594.4882
DEER-SFAM-CZ03-V1-eSH-13-HL-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-HL | 13.2368 | 1.6411 | 238.4936 | 3037.4625 | 3.711 | 3275.9561 | 584.3193
DEER-SFAM-CZ03-V1-eSH-13-HM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-HM | 13.5158 | 1.6872 | 244.2159 | 3118.4703 | 3.711 | 3362.6862 | 556.7909
DEER-SFAM-CZ03-V1-eSH-13-LH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-LH | 13.2043 | 1.617 | 241.0218 | 3717.0646 | 3.4688 | 3958.0864 | 767.0814
DEER-SFAM-CZ03-V1-eSH-13-LL-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-LL | 14.1676 | 1.6329 | 233.9393 | 3209.1828 | 3.711 | 3443.1221 | 550.563
DEER-SFAM-CZ03-V1-eSH-13-LM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-LM | 12.836 | 1.6886 | 251.2757 | 2844.3338 | 3.4688 | 3095.6095 | 615.989
DEER-SFAM-CZ03-V1-eSH-13-MH-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-MH | 13.8436 | 1.5561 | 232.7909 | 3535.8634 | 3.711 | 3768.6543 | 585.4844
DEER-SFAM-CZ03-V1-eSH-13-ML-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-ML | 13.1986 | 1.6883 | 247.8393 | 3364.281 | 3.4688 | 3612.1203 | 609.4359
DEER-SFAM-CZ03-V1-eSH-13-MM-s1 | 13 | CZ03 | V1 | CZ03-V1-eSH-13 | CZ03-V1-eSH-13-MM | 14.1076 | 1.6423 | 235.74 | 3284.8647 | 3.4688 | 3520.6047 | 517.2086
DEER-SFAM-CZ03-V1-eSH-14-HH-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-HH | 14.1875 | 1.5975 | 231.2335 | 3197.4903 | 3.711 | 3428.7239 | 496.1252
DEER-SFAM-CZ03-V1-eSH-14-HL-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-HL | 14.3761 | 1.6008 | 227.3434 | 3160.4935 | 3.711 | 3387.8369 | 547.0752
DEER-SFAM-CZ03-V1-eSH-14-HM-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-HM | 14.1091 | 1.5891 | 230.962 | 3110.5824 | 3.711 | 3341.5444 | 456.7275
DEER-SFAM-CZ03-V1-eSH-14-MH-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-MH | 13.9916 | 1.5157 | 226.3327 | 3345.3988 | 3.4688 | 3571.7315 | 570.8054
DEER-SFAM-CZ03-V1-eSH-14-ML-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-ML | 14.5624 | 1.5054 | 219.4045 | 3533.8447 | 3.711 | 3753.2492 | 655.1676
DEER-SFAM-CZ03-V1-eSH-14-MM-s1 | 14 | CZ03 | V1 | CZ03-V1-eSH-14 | CZ03-V1-eSH-14-MM | 14.0347 | 1.5374 | 224.2299 | 3086.0204 | 3.4688 | 3310.2503 | 525.6763
DEER-SFAM-CZ03-V1-eSH-15-HH-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-HH | 15.093 | 1.4435 | 213.0939 | 3753.4013 | 3.711 | 3966.4953 | 460.6453
DEER-SFAM-CZ03-V1-eSH-15-HL-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-HL | 15.3511 | 1.4866 | 213.3465 | 2705.0381 | 3.711 | 2918.3846 | 457.8738
DEER-SFAM-CZ03-V1-eSH-15-HM-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-HM | 15.7107 | 1.393 | 205.1143 | 2808.9202 | 3.711 | 3014.0345 | 450.7891
DEER-SFAM-CZ03-V1-eSH-15-MH-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-MH | 15.6781 | 1.3915 | 204.4902 | 3367.1803 | 3.4688 | 3571.6706 | 442.8849
DEER-SFAM-CZ03-V1-eSH-15-ML-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-ML | 15.6314 | 1.4132 | 204.748 | 3080.0757 | 3.711 | 3284.8237 | 450.2349
DEER-SFAM-CZ03-V1-eSH-15-MM-s1 | 15 | CZ03 | V1 | CZ03-V1-eSH-15 | CZ03-V1-eSH-15-MM | 16.0816 | 1.4049 | 203.0179 | 3232.6687 | 3.711 | 3435.6866 | 461.1903
DEER-SFAM-CZ03-V1-eSH-16-CH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-CH | 16.5293 | 1.5858 | 236.5691 | 3316.0401 | 3.711 | 3552.6093 | 448.3708
DEER-SFAM-CZ03-V1-eSH-16-CL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-CL | 16.7564 | 1.5809 | 234.0589 | 3090.3926 | 3.711 | 3324.4515 | 454.261
DEER-SFAM-CZ03-V1-eSH-16-LH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-LH | 15.7078 | 1.4261 | 222.2047 | 3615.226 | 3.711 | 3837.4307 | 473.636
DEER-SFAM-CZ03-V1-eSH-16-LL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-LL | 15.5731 | 1.5084 | 229.4562 | 3327.8801 | 3.4688 | 3557.3363 | 431.754
DEER-SFAM-CZ03-V1-eSH-16-LM-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-LM | 15.3093 | 1.4608 | 229.5334 | 3636.2916 | 3.4688 | 3865.825 | 512.3116
DEER-SFAM-CZ03-V1-eSH-16-TH-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-TH | 17.8208 | 1.4839 | 219.965 | 4095.694 | 3.711 | 4315.6589 | 437.4168
DEER-SFAM-CZ03-V1-eSH-16-TL-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-TL | 17.0765 | 1.639 | 239.1269 | 4119.4202 | 3.711 | 4358.5471 | 437.6884
DEER-SFAM-CZ03-V1-eSH-16-TM-s2 | 16 | CZ03 | V1 | CZ03-V1-eSH-16 | CZ03-V1-eSH-16-TM | 17.2752 | 1.6261 | 236.3922 | 4181.25 | 3.711 | 4417.6422 | 440.1971
DEER-SFAM-CZ03-V1-eSH-17-CM-s2 | 17 | CZ03 | V1 | CZ03-V1-eSH-17 | CZ03-V1-eSH-17-CM | 17.8035 | 1.4922 | 220.2901 | 3530.1945 | 3.711 | 3750.4846 | 480.4415
DEER-SFAM-CZ03-V1-eSH-17-LM-s2 | 17 | CZ03 | V1 | CZ03-V1-eSH-17 | CZ03-V1-eSH-17-LM | 16.6227 | 1.4271 | 216.5108 | 3211.2601 | 3.711 | 3427.7709 | 329.8687
DEER-SFAM-CZ03-V1-eSH-17-TH-s2 | 17 | CZ03 | V1 | CZ03-V1-eSH-17 | CZ03-V1-eSH-17-TH | 19.0441 | 1.4125 | 205.8406 | 4081.0205 | 3.711 | 4286.8611 | 438.7595
DEER-SFAM-CZ03-V1-eSH-17-TL-s2 | 17 | CZ03 | V1 | CZ03-V1-eSH-17 | CZ03-V1-eSH-17-TL | 19.0039 | 1.4224 | 206.1576 | 4052.8058 | 3.711 | 4258.9634 | 436.2216
DEER-SFAM-CZ03-V1-eSH-18-LH-s2 | 18 | CZ03 | V1 | CZ03-V1-eSH-18 | CZ03-V1-eSH-18-LH | 17.6526 | 1.3299 | 201.5033 | 3670.8211 | 3.711 | 3872.3244 | 388.9439
DEER-SFAM-CZ03-V1-eSH-18-LL-s2 | 18 | CZ03 | V1 | CZ03-V1-eSH-18 | CZ03-V1-eSH-18-LL | 16.9572 | 1.3657 | 207.6771 | 3337.271 | 3.4688 | 3544.9481 | 383.2953
DEER-SFAM-CZ03-V1-eSH-18-LM-s2 | 18 | CZ03 | V1 | CZ03-V1-eSH-18 | CZ03-V1-eSH-18-LM | 17.716 | 1.3418 | 202.2675 | 3861.8762 | 3.711 | 4064.1437 | 417.622
DEER-SFAM-CZ03-V1-eSH-18-TM-s2 | 18 | CZ03 | V1 | CZ03-V1-eSH-18 | CZ03-V1-eSH-18-TM | 20.5009 | 1.3004 | 191.6808 | 4008.6082 | 3.4688 | 4200.289 | 539.4623
DEER-SFAM-CZ03-V2-eSA-10-HH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-HH | 10.081 | 1.5458 | 154.0685 | 0 | 3.1141 | 154.0685 | 244.8636
DEER-SFAM-CZ03-V2-eSA-10-HL-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-HL | 10.1227 | 1.5586 | 152.7769 | 0 | 3.1141 | 152.7769 | 243.638
DEER-SFAM-CZ03-V2-eSA-10-HM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-HM | 10.0629 | 1.5511 | 152.2332 | 0 | 3.1141 | 152.2332 | 243.0824
DEER-SFAM-CZ03-V2-eSA-10-LH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-LH | 10.2637 | 1.4934 | 146.6207 | 0 | 3.1141 | 146.6207 | 237.5479
DEER-SFAM-CZ03-V2-eSA-10-LL-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-LL | 10.0315 | 1.5782 | 153.4098 | 0 | 3.1141 | 153.4098 | 244.2865
DEER-SFAM-CZ03-V2-eSA-10-LM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-LM | 10.2268 | 1.5168 | 147.6838 | 0 | 3.1141 | 147.6838 | 238.6137
DEER-SFAM-CZ03-V2-eSA-10-MH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-MH | 10.0277 | 1.5042 | 150.7245 | 0 | 3.1141 | 150.7245 | 241.6286
DEER-SFAM-CZ03-V2-eSA-10-ML-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-ML | 10.0964 | 1.6024 | 155.9462 | 0 | 3.1141 | 155.9462 | 246.8091
DEER-SFAM-CZ03-V2-eSA-10-MM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSA-10 | CZ03-V2-eSA-10-MM | 10.3418 | 1.4491 | 144.7638 | 0 | 3.1141 | 144.7638 | 235.6334
DEER-SFAM-CZ03-V2-eSA-13-HH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-HH | 12.6163 | 1.164 | 116.0748 | 0 | 3.1141 | 116.0748 | 197.9785
DEER-SFAM-CZ03-V2-eSA-13-HL-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-HL | 13.2219 | 1.1553 | 112.8838 | 0 | 3.1141 | 112.8838 | 184.5664
DEER-SFAM-CZ03-V2-eSA-13-HM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-HM | 13.1242 | 1.1852 | 114.9955 | 0 | 3.2676 | 114.9955 | 196.8964
DEER-SFAM-CZ03-V2-eSA-13-LH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-LH | 13.0446 | 1.1402 | 113.1843 | 0 | 3.1141 | 113.1843 | 204.0653
DEER-SFAM-CZ03-V2-eSA-13-LL-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-LL | 13.1445 | 1.191 | 116.2344 | 0 | 3.1141 | 116.2344 | 206.958
DEER-SFAM-CZ03-V2-eSA-13-LM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-LM | 12.73 | 1.1923 | 118.2152 | 0 | 3.1141 | 118.2152 | 209.0304
DEER-SFAM-CZ03-V2-eSA-13-MH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-MH | 13.8338 | 1.1361 | 111.9741 | 0 | 3.1141 | 111.9741 | 202.8239
DEER-SFAM-CZ03-V2-eSA-13-ML-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-ML | 12.9148 | 1.175 | 113.7211 | 0 | 3.1141 | 113.7211 | 204.2933
DEER-SFAM-CZ03-V2-eSA-13-MM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSA-13 | CZ03-V2-eSA-13-MM | 13.9081 | 1.1277 | 110.0381 | 0 | 3.1141 | 110.0381 | 200.8763
DEER-SFAM-CZ03-V2-eSA-14-HH-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-HH | 13.2075 | 1.1291 | 111.0748 | 0 | 3.1141 | 111.0748 | 187.2179
DEER-SFAM-CZ03-V2-eSA-14-HL-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-HL | 14.2963 | 1.0752 | 105.0088 | 0 | 3.1141 | 105.0088 | 160.9999
DEER-SFAM-CZ03-V2-eSA-14-HM-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-HM | 14.1377 | 1.0841 | 105.8691 | 0 | 3.1141 | 105.8691 | 191.7684
DEER-SFAM-CZ03-V2-eSA-14-MH-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-MH | 13.5808 | 1.1319 | 112.9471 | 0 | 3.1141 | 112.9471 | 172.6438
DEER-SFAM-CZ03-V2-eSA-14-ML-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-ML | 13.677 | 1.0868 | 106.8179 | 0 | 3.1141 | 106.8179 | 202.1515
DEER-SFAM-CZ03-V2-eSA-14-MM-s1 | 14 | CZ03 | V2 | CZ03-V2-eSA-14 | CZ03-V2-eSA-14-MM | 13.6932 | 1.1021 | 108.8541 | 0 | 3.1141 | 108.8541 | 174.2994
DEER-SFAM-CZ03-V2-eSA-15-HH-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-HH | 14.9907 | 1.01 | 99.5956 | 0 | 3.2676 | 99.5956 | 163.0872
DEER-SFAM-CZ03-V2-eSA-15-HL-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-HL | 15.4872 | 0.98375 | 96.5511 | 0 | 3.1141 | 96.5511 | 175.6661
DEER-SFAM-CZ03-V2-eSA-15-HM-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-HM | 14.8432 | 1.0117 | 100.1689 | 0 | 3.2676 | 100.1689 | 163.8968
DEER-SFAM-CZ03-V2-eSA-15-MH-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-MH | 14.6251 | 1.015 | 100.5478 | 0 | 3.1141 | 100.5478 | 147.8451
DEER-SFAM-CZ03-V2-eSA-15-ML-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-ML | 15.3613 | 1.0249 | 99.8913 | 0 | 3.1141 | 99.8913 | 163.5057
DEER-SFAM-CZ03-V2-eSA-15-MM-s1 | 15 | CZ03 | V2 | CZ03-V2-eSA-15 | CZ03-V2-eSA-15-MM | 14.9541 | 1.0064 | 99.0054 | 0 | 3.1141 | 99.0054 | 157.0019
DEER-SFAM-CZ03-V2-eSA-16-CH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-CH | 15.7926 | 1.1493 | 114.4019 | 0 | 3.2676 | 114.4019 | 151.1394
DEER-SFAM-CZ03-V2-eSA-16-CL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-CL | 16.2107 | 1.0866 | 107.9965 | 0 | 3.2676 | 107.9965 | 154.4918
DEER-SFAM-CZ03-V2-eSA-16-CM-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-CM | 15.9068 | 1.1173 | 110.6666 | 0 | 3.2676 | 110.6666 | 159.7315
DEER-SFAM-CZ03-V2-eSA-16-LH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-LH | 15.252 | 1.0014 | 105.2291 | 0 | 3.1141 | 105.2291 | 168.1447
DEER-SFAM-CZ03-V2-eSA-16-LL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-LL | 14.9465 | 1.0522 | 108.4416 | 0 | 3.1141 | 108.4416 | 149.7063
DEER-SFAM-CZ03-V2-eSA-16-LM-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-LM | 14.9738 | 1.0538 | 108.5053 | 0 | 3.1141 | 108.5053 | 145.9089
DEER-SFAM-CZ03-V2-eSA-16-NM-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-NM | 16.4267 | 0.98555 | 102.4087 | 0 | 3.1141 | 102.4087 | 139.1484
DEER-SFAM-CZ03-V2-eSA-16-TH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-TH | 15.5 | 1.1321 | 120.1671 | 0 | 3.1141 | 120.1671 | 143.7216
DEER-SFAM-CZ03-V2-eSA-16-TL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSA-16 | CZ03-V2-eSA-16-TL | 16.6259 | 1.0871 | 110.3009 | 0 | 3.1141 | 110.3009 | 135.6874
DEER-SFAM-CZ03-V2-eSA-17-CH-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-CH | 16.8892 | 1.0544 | 104.6601 | 0 | 3.2676 | 104.6601 | 151.1419
DEER-SFAM-CZ03-V2-eSA-17-CL-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-CL | 16.8976 | 1.056 | 104.5909 | 0 | 3.2676 | 104.5909 | 151.0608
DEER-SFAM-CZ03-V2-eSA-17-CM-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-CM | 17.0066 | 1.0692 | 106.2527 | 0 | 3.2676 | 106.2527 | 142.8794
DEER-SFAM-CZ03-V2-eSA-17-LH-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-LH | 15.8857 | 0.95756 | 100.1557 | 0 | 3.1141 | 100.1557 | 149.447
DEER-SFAM-CZ03-V2-eSA-17-LL-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-LL | 15.9434 | 0.99942 | 102.9198 | 0 | 3.1141 | 102.9198 | 129.711
DEER-SFAM-CZ03-V2-eSA-17-LM-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-LM | 15.6923 | 1.0168 | 104.2786 | 0 | 3.1141 | 104.2786 | 127.4265
DEER-SFAM-CZ03-V2-eSA-17-TH-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-TH | 17.6887 | 0.98575 | 102.1208 | 0 | 3.1141 | 102.1208 | 139.7717
DEER-SFAM-CZ03-V2-eSA-17-TL-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-TL | 19.0443 | 0.93866 | 92.289 | 0 | 3.1141 | 92.289 | 151.2752
DEER-SFAM-CZ03-V2-eSA-17-TM-s2 | 17 | CZ03 | V2 | CZ03-V2-eSA-17 | CZ03-V2-eSA-17-TM | 17.6824 | 1.0702 | 109.9429 | 0 | 3.1141 | 109.9429 | 129.5601
DEER-SFAM-CZ03-V2-eSA-18-LH-s2 | 18 | CZ03 | V2 | CZ03-V2-eSA-18 | CZ03-V2-eSA-18-LH | 16.7023 | 0.93791 | 97.7284 | 0 | 3.1141 | 97.7284 | 129.9838
DEER-SFAM-CZ03-V2-eSA-18-LL-s2 | 18 | CZ03 | V2 | CZ03-V2-eSA-18 | CZ03-V2-eSA-18-LL | 17.1973 | 0.9233 | 94.2089 | 0 | 3.1141 | 94.2089 | 136.3324
DEER-SFAM-CZ03-V2-eSA-18-TH-s2 | 18 | CZ03 | V2 | CZ03-V2-eSA-18 | CZ03-V2-eSA-18-TH | 18.1921 | 0.94689 | 99.4437 | 0 | 3.1141 | 99.4437 | 125.0066
DEER-SFAM-CZ03-V2-eSA-18-TL-s2 | 18 | CZ03 | V2 | CZ03-V2-eSA-18 | CZ03-V2-eSA-18-TL | 18.0701 | 0.98052 | 101.2676 | 0 | 3.1141 | 101.2676 | 129.3959
DEER-SFAM-CZ03-V2-eSA-18-TM-s2 | 18 | CZ03 | V2 | CZ03-V2-eSA-18 | CZ03-V2-eSA-18-TM | 17.6086 | 0.9851 | 102.1214 | 0 | 3.1141 | 102.1214 | 128.2643
DEER-SFAM-CZ03-V2-eSH-10-HH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-HH | 9.9676 | 1.4831 | 149.0451 | 1818.1484 | 3.1141 | 1967.1935 | 336.4834
DEER-SFAM-CZ03-V2-eSH-10-HL-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-HL | 9.9645 | 1.5357 | 151.6933 | 1836.8239 | 3.1141 | 1988.5173 | 338.6579
DEER-SFAM-CZ03-V2-eSH-10-HM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-HM | 10.3488 | 1.5258 | 150.7807 | 1768.4847 | 3.1141 | 1919.2653 | 329.02
DEER-SFAM-CZ03-V2-eSH-10-LH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-LH | 10.0969 | 1.49 | 150.3017 | 1929.7248 | 3.1141 | 2080.0265 | 344.4248
DEER-SFAM-CZ03-V2-eSH-10-LL-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-LL | 10.1804 | 1.5361 | 151.1135 | 1803.0976 | 3.1141 | 1954.2111 | 351.6772
DEER-SFAM-CZ03-V2-eSH-10-LM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-LM | 10.1768 | 1.5087 | 151.1809 | 1797.1186 | 3.1141 | 1948.2995 | 334.9669
DEER-SFAM-CZ03-V2-eSH-10-MH-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-MH | 10.2581 | 1.4929 | 148.1893 | 1888.9138 | 3.1141 | 2037.1031 | 354.3268
DEER-SFAM-CZ03-V2-eSH-10-ML-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-ML | 10.241 | 1.5388 | 150.273 | 1682.0513 | 3.1141 | 1832.3243 | 333.9932
DEER-SFAM-CZ03-V2-eSH-10-MM-s1 | 10 | CZ03 | V2 | CZ03-V2-eSH-10 | CZ03-V2-eSH-10-MM | 10.2771 | 1.5421 | 152.1299 | 1828.0272 | 3.1141 | 1980.1571 | 326.6048
DEER-SFAM-CZ03-V2-eSH-13-HH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-HH | 12.9638 | 1.1801 | 117.1223 | 1736.3799 | 3.1141 | 1853.5021 | 288.2006
DEER-SFAM-CZ03-V2-eSH-13-HL-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-HL | 13.004 | 1.1445 | 112.815 | 1495.2392 | 3.2676 | 1608.0541 | 282.8261
DEER-SFAM-CZ03-V2-eSH-13-HM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-HM | 13.1853 | 1.1752 | 115.7831 | 1546.7931 | 3.1141 | 1662.5761 | 269.4874
DEER-SFAM-CZ03-V2-eSH-13-LH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-LH | 12.8932 | 1.1552 | 114.8309 | 1788.3931 | 3.1141 | 1903.224 | 373.231
DEER-SFAM-CZ03-V2-eSH-13-LL-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-LL | 13.8741 | 1.1376 | 110.6256 | 1573.7152 | 3.1141 | 1684.3408 | 266.3662
DEER-SFAM-CZ03-V2-eSH-13-LM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-LM | 12.5987 | 1.2047 | 118.5858 | 1408.9029 | 3.1141 | 1527.4887 | 297.648
DEER-SFAM-CZ03-V2-eSH-13-MH-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-MH | 13.3987 | 1.098 | 111.2988 | 1751.7452 | 3.1141 | 1863.044 | 284.3523
DEER-SFAM-CZ03-V2-eSH-13-ML-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-ML | 12.8746 | 1.194 | 117.1518 | 1631.6546 | 3.1141 | 1748.8064 | 294.4459
DEER-SFAM-CZ03-V2-eSH-13-MM-s1 | 13 | CZ03 | V2 | CZ03-V2-eSH-13 | CZ03-V2-eSH-13-MM | 13.6603 | 1.1495 | 112.7178 | 1628.8125 | 3.1141 | 1741.5304 | 251.0458
DEER-SFAM-CZ03-V2-eSH-14-HH-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-HH | 13.7641 | 1.1141 | 110.3008 | 1579.3343 | 3.1141 | 1689.6351 | 240.4885
DEER-SFAM-CZ03-V2-eSH-14-HL-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-HL | 14.1195 | 1.1103 | 107.1865 | 1538.6648 | 3.1141 | 1645.8513 | 264.0612
DEER-SFAM-CZ03-V2-eSH-14-HM-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-HM | 13.8077 | 1.1076 | 109.1597 | 1528.6543 | 3.1141 | 1637.814 | 220.1507
DEER-SFAM-CZ03-V2-eSH-14-MH-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-MH | 13.704 | 1.0791 | 107.4793 | 1615.8683 | 3.1141 | 1723.3476 | 277.0265
DEER-SFAM-CZ03-V2-eSH-14-ML-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-ML | 14.3851 | 1.0471 | 102.9465 | 1676.5528 | 3.1141 | 1779.4993 | 316.4331
DEER-SFAM-CZ03-V2-eSH-14-MM-s1 | 14 | CZ03 | V2 | CZ03-V2-eSH-14 | CZ03-V2-eSH-14-MM | 13.8143 | 1.0836 | 105.8089 | 1500.4721 | 3.1141 | 1606.281 | 253.7811
DEER-SFAM-CZ03-V2-eSH-15-HH-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-HH | 14.6333 | 1.0155 | 101.5744 | 1799.7048 | 3.1141 | 1901.2791 | 223.3677
DEER-SFAM-CZ03-V2-eSH-15-HL-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-HL | 15.0253 | 1.0335 | 100.9028 | 1333.3671 | 3.1141 | 1434.2699 | 220.9687
DEER-SFAM-CZ03-V2-eSH-15-HM-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-HM | 15.2389 | 0.9761 | 97.5405 | 1384.189 | 3.1141 | 1481.7295 | 217.9184
DEER-SFAM-CZ03-V2-eSH-15-MH-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-MH | 15.3285 | 0.98594 | 97.2183 | 1603.5323 | 3.1141 | 1700.7505 | 213.9294
DEER-SFAM-CZ03-V2-eSH-15-ML-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-ML | 15.3868 | 0.98163 | 96.152 | 1475.0733 | 3.1141 | 1571.2253 | 216.4015
DEER-SFAM-CZ03-V2-eSH-15-MM-s1 | 15 | CZ03 | V2 | CZ03-V2-eSH-15 | CZ03-V2-eSH-15-MM | 15.5722 | 0.98693 | 96.9605 | 1569.1998 | 3.2676 | 1666.1604 | 224.0012
DEER-SFAM-CZ03-V2-eSH-16-CH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-CH | 15.9703 | 1.12 | 112.9147 | 1587.6825 | 3.2676 | 1700.5972 | 213.2692
DEER-SFAM-CZ03-V2-eSH-16-CL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-CL | 16.2982 | 1.1114 | 110.7643 | 1472.5533 | 3.2676 | 1583.3176 | 215.539
DEER-SFAM-CZ03-V2-eSH-16-LH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-LH | 14.9807 | 1.0007 | 106.4701 | 1752.1211 | 3.1141 | 1858.5912 | 228.2786
DEER-SFAM-CZ03-V2-eSH-16-LL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-LL | 15.0168 | 1.0582 | 108.4987 | 1568.0409 | 3.1141 | 1676.5396 | 206.0271
DEER-SFAM-CZ03-V2-eSH-16-LM-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-LM | 14.5676 | 1.0403 | 110.279 | 1748.0797 | 3.1141 | 1858.3587 | 246.4981
DEER-SFAM-CZ03-V2-eSH-16-TH-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-TH | 16.5308 | 1.0436 | 109.1709 | 2006.0216 | 3.2676 | 2115.1925 | 207.3557
DEER-SFAM-CZ03-V2-eSH-16-TL-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-TL | 16.273 | 1.1441 | 114.7164 | 1963.9332 | 3.1141 | 2078.6496 | 202.9721
DEER-SFAM-CZ03-V2-eSH-16-TM-s2 | 16 | CZ03 | V2 | CZ03-V2-eSH-16 | CZ03-V2-eSH-16-TM | 16.4326 | 1.1333 | 113.6019 | 2001.093 | 3.1141 | 2114.6949 | 204.1441
DEER-SFAM-CZ03-V2-eSH-17-CM-s2 | 17 | CZ03 | V2 | CZ03-V2-eSH-17 | CZ03-V2-eSH-17-CM | 17.2437 | 1.0488 | 104.6744 | 1650.3331 | 3.2676 | 1755.0076 | 225.2416
DEER-SFAM-CZ03-V2-eSH-17-LM-s2 | 17 | CZ03 | V2 | CZ03-V2-eSH-17 | CZ03-V2-eSH-17-LM | 16.0025 | 1.0046 | 102.9123 | 1525.4553 | 3.1141 | 1628.3676 | 157.8199
DEER-SFAM-CZ03-V2-eSH-17-TH-s2 | 17 | CZ03 | V2 | CZ03-V2-eSH-17 | CZ03-V2-eSH-17-TH | 17.863 | 0.99167 | 100.7222 | 1993.4113 | 3.1141 | 2094.1335 | 207.1263
DEER-SFAM-CZ03-V2-eSH-17-TL-s2 | 17 | CZ03 | V2 | CZ03-V2-eSH-17 | CZ03-V2-eSH-17-TL | 17.7804 | 0.9977 | 101.255 | 1968.2917 | 3.1141 | 2069.5467 | 206.4128
DEER-SFAM-CZ03-V2-eSH-18-LH-s2 | 18 | CZ03 | V2 | CZ03-V2-eSH-18 | CZ03-V2-eSH-18-LH | 17.0744 | 0.92869 | 95.3689 | 1739.1639 | 3.1141 | 1834.5329 | 183.6907
DEER-SFAM-CZ03-V2-eSH-18-LL-s2 | 18 | CZ03 | V2 | CZ03-V2-eSH-18 | CZ03-V2-eSH-18-LL | 16.3387 | 0.9639 | 98.5783 | 1563.4155 | 3.1141 | 1661.9939 | 182.6659
DEER-SFAM-CZ03-V2-eSH-18-LM-s2 | 18 | CZ03 | V2 | CZ03-V2-eSH-18 | CZ03-V2-eSH-18-LM | 17.0039 | 0.93311 | 96.3541 | 1833.0095 | 3.1141 | 1929.3636 | 197.4988
DEER-SFAM-CZ03-V2-eSH-18-TM-s2 | 18 | CZ03 | V2 | CZ03-V2-eSH-18 | CZ03-V2-eSH-18-TM | 18.8901 | 0.93139 | 96.306 | 1952.2341 | 3.1141 | 2048.5402 | 252.6444
DEER-SFAM-CZ03-V3-eSA-10-HH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-HH | 10.5919 | 2.503 | 540.0302 | 0 | 3.4 | 540.0302 | 627.2736
DEER-SFAM-CZ03-V3-eSA-10-HL-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-HL | 10.6756 | 2.5711 | 537.6181 | 0 | 3.4 | 537.6181 | 624.9312
DEER-SFAM-CZ03-V3-eSA-10-HM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-HM | 10.4892 | 2.5464 | 541.0932 | 0 | 3.4 | 541.0932 | 628.3939
DEER-SFAM-CZ03-V3-eSA-10-LH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-LH | 10.4338 | 2.4382 | 527.3923 | 0 | 3.4 | 527.3923 | 614.7744
DEER-SFAM-CZ03-V3-eSA-10-LL-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-LL | 10.3655 | 2.6094 | 550.6606 | 0 | 3.4 | 550.6606 | 637.9895
DEER-SFAM-CZ03-V3-eSA-10-LM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-LM | 10.4182 | 2.4834 | 531.3233 | 0 | 3.4 | 531.3233 | 618.7082
DEER-SFAM-CZ03-V3-eSA-10-MH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-MH | 10.3918 | 2.4139 | 532.9031 | 0 | 3.4 | 532.9031 | 620.2612
DEER-SFAM-CZ03-V3-eSA-10-ML-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-ML | 10.4918 | 2.65 | 554.2584 | 0 | 3.4 | 554.2584 | 641.5738
DEER-SFAM-CZ03-V3-eSA-10-MM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSA-10 | CZ03-V3-eSA-10-MM | 10.6591 | 2.3751 | 517.0936 | 0 | 3.4 | 517.0936 | 604.4157
DEER-SFAM-CZ03-V3-eSA-13-HH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-HH | 13.2113 | 1.9168 | 415.3983 | 0 | 3.4 | 415.3983 | 494.106
DEER-SFAM-CZ03-V3-eSA-13-HL-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-HL | 13.5444 | 1.9261 | 406.777 | 0 | 3.4 | 406.777 | 475.6635
DEER-SFAM-CZ03-V3-eSA-13-HM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-HM | 13.6411 | 1.9659 | 410.5402 | 0 | 3.4 | 410.5402 | 489.2212
DEER-SFAM-CZ03-V3-eSA-13-LH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-LH | 13.4141 | 1.86 | 405.4908 | 0 | 3.4 | 405.4908 | 492.8247
DEER-SFAM-CZ03-V3-eSA-13-LL-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-LL | 13.5342 | 1.9709 | 416.5496 | 0 | 3.4 | 416.5496 | 503.7176
DEER-SFAM-CZ03-V3-eSA-13-LM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-LM | 13.0968 | 1.9345 | 423.1092 | 0 | 3.4 | 423.1092 | 510.3739
DEER-SFAM-CZ03-V3-eSA-13-MH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-MH | 14.67 | 1.8558 | 388.1563 | 0 | 3.4 | 388.1563 | 475.4574
DEER-SFAM-CZ03-V3-eSA-13-ML-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-ML | 13.2317 | 1.9457 | 410.2867 | 0 | 3.4 | 410.2867 | 497.3186
DEER-SFAM-CZ03-V3-eSA-13-MM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSA-13 | CZ03-V3-eSA-13-MM | 14.7626 | 1.8817 | 384.2898 | 0 | 3.4 | 384.2898 | 471.579
DEER-SFAM-CZ03-V3-eSA-14-HH-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-HH | 13.7961 | 1.8564 | 394.3713 | 0 | 3.4 | 394.3713 | 467.5417
DEER-SFAM-CZ03-V3-eSA-14-HL-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-HL | 14.8321 | 1.7996 | 377.41 | 0 | 3.4 | 377.41 | 431.2188
DEER-SFAM-CZ03-V3-eSA-14-HM-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-HM | 14.515 | 1.8112 | 379.9452 | 0 | 3.4 | 379.9452 | 462.4924
DEER-SFAM-CZ03-V3-eSA-14-MH-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-MH | 13.9471 | 1.8205 | 402.2694 | 0 | 3.4 | 402.2694 | 459.6352
DEER-SFAM-CZ03-V3-eSA-14-ML-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-ML | 13.9846 | 1.8085 | 385.6452 | 0 | 3.4 | 385.6452 | 477.2544
DEER-SFAM-CZ03-V3-eSA-14-MM-s1 | 14 | CZ03 | V3 | CZ03-V3-eSA-14 | CZ03-V3-eSA-14-MM | 14.0905 | 1.7818 | 389.5982 | 0 | 3.4 | 389.5982 | 452.4903
DEER-SFAM-CZ03-V3-eSA-15-HH-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-HH | 15.9516 | 1.6453 | 348.2199 | 0 | 3.4 | 348.2199 | 409.2208
DEER-SFAM-CZ03-V3-eSA-15-HL-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-HL | 16.3228 | 1.6447 | 341.9846 | 0 | 3.4 | 341.9846 | 418.0084
DEER-SFAM-CZ03-V3-eSA-15-HM-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-HM | 15.5363 | 1.6911 | 358.8181 | 0 | 3.9 | 358.8181 | 420.1085
DEER-SFAM-CZ03-V3-eSA-15-MH-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-MH | 15.4172 | 1.6558 | 354.3662 | 0 | 3.4 | 354.3662 | 399.822
DEER-SFAM-CZ03-V3-eSA-15-ML-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-ML | 16.0108 | 1.702 | 353.9939 | 0 | 3.4 | 353.9939 | 415.1184
DEER-SFAM-CZ03-V3-eSA-15-MM-s1 | 15 | CZ03 | V3 | CZ03-V3-eSA-15 | CZ03-V3-eSA-15-MM | 15.4408 | 1.6685 | 355.5368 | 0 | 3.4 | 355.5368 | 411.2732
DEER-SFAM-CZ03-V3-eSA-16-CH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-CH | 16.4156 | 1.8203 | 385.4074 | 0 | 3.4 | 385.4074 | 420.4731
DEER-SFAM-CZ03-V3-eSA-16-CL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-CL | 16.9899 | 1.7275 | 363.4819 | 0 | 3.9 | 363.4819 | 407.8766
DEER-SFAM-CZ03-V3-eSA-16-CM-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-CM | 16.5976 | 1.7682 | 373.3856 | 0 | 3.9 | 373.3856 | 420.1615
DEER-SFAM-CZ03-V3-eSA-16-LH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-LH | 16.665 | 1.6151 | 348.8009 | 0 | 3.4 | 348.8009 | 409.2225
DEER-SFAM-CZ03-V3-eSA-16-LL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-LL | 16.023 | 1.6846 | 365.7013 | 0 | 3.4 | 365.7013 | 405.3121
DEER-SFAM-CZ03-V3-eSA-16-LM-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-LM | 15.8582 | 1.6917 | 371.1069 | 0 | 3.4 | 371.1069 | 407.0009
DEER-SFAM-CZ03-V3-eSA-16-NM-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-NM | 17.0283 | 1.5951 | 357.4835 | 0 | 3.4 | 357.4835 | 392.7496
DEER-SFAM-CZ03-V3-eSA-16-TH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-TH | 17.8178 | 1.7228 | 352.7656 | 0 | 3.4 | 352.7656 | 375.3372
DEER-SFAM-CZ03-V3-eSA-16-TL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSA-16 | CZ03-V3-eSA-16-TL | 18.6941 | 1.7051 | 335.4271 | 0 | 3.4 | 335.4271 | 359.7569
DEER-SFAM-CZ03-V3-eSA-17-CH-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-CH | 17.5351 | 1.6742 | 354.7729 | 0 | 3.4 | 354.7729 | 399.0817
DEER-SFAM-CZ03-V3-eSA-17-CL-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-CL | 17.549 | 1.6887 | 354.3911 | 0 | 3.4 | 354.3911 | 398.6901
DEER-SFAM-CZ03-V3-eSA-17-CM-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-CM | 17.6661 | 1.6889 | 351.6596 | 0 | 3.4 | 351.6596 | 386.6229
DEER-SFAM-CZ03-V3-eSA-17-LH-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-LH | 17.1565 | 1.5497 | 334.9311 | 0 | 3.4 | 334.9311 | 382.2796
DEER-SFAM-CZ03-V3-eSA-17-LL-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-LL | 17.0062 | 1.5993 | 347.2689 | 0 | 3.4 | 347.2689 | 372.948
DEER-SFAM-CZ03-V3-eSA-17-LM-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-LM | 16.7133 | 1.6105 | 350.6371 | 0 | 3.4 | 350.6371 | 372.8421
DEER-SFAM-CZ03-V3-eSA-17-TH-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-TH | 20.444 | 1.5313 | 307.6755 | 0 | 3.4 | 307.6755 | 343.7861
DEER-SFAM-CZ03-V3-eSA-17-TL-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-TL | 21.5474 | 1.5401 | 285.6852 | 0 | 3.4 | 285.6852 | 341.8902
DEER-SFAM-CZ03-V3-eSA-17-TM-s2 | 17 | CZ03 | V3 | CZ03-V3-eSA-17 | CZ03-V3-eSA-17-TM | 19.9882 | 1.6262 | 329.7991 | 0 | 3.4 | 329.7991 | 348.5625
DEER-SFAM-CZ03-V3-eSA-18-LH-s2 | 18 | CZ03 | V3 | CZ03-V3-eSA-18 | CZ03-V3-eSA-18-LH | 18.016 | 1.4959 | 327.5199 | 0 | 3.4 | 327.5199 | 358.472
DEER-SFAM-CZ03-V3-eSA-18-LL-s2 | 18 | CZ03 | V3 | CZ03-V3-eSA-18 | CZ03-V3-eSA-18-LL | 18.3595 | 1.5046 | 316.8277 | 0 | 3.4 | 316.8277 | 357.2629
DEER-SFAM-CZ03-V3-eSA-18-TH-s2 | 18 | CZ03 | V3 | CZ03-V3-eSA-18 | CZ03-V3-eSA-18-TH | 20.9856 | 1.4385 | 294.3547 | 0 | 3.4 | 294.3547 | 318.8637
DEER-SFAM-CZ03-V3-eSA-18-TL-s2 | 18 | CZ03 | V3 | CZ03-V3-eSA-18 | CZ03-V3-eSA-18-TL | 20.6031 | 1.5127 | 302.0074 | 0 | 3.4 | 302.0074 | 328.9355
DEER-SFAM-CZ03-V3-eSA-18-TM-s2 | 18 | CZ03 | V3 | CZ03-V3-eSA-18 | CZ03-V3-eSA-18-TM | 19.9894 | 1.5126 | 313.6848 | 0 | 3.4 | 313.6848 | 338.7533
DEER-SFAM-CZ03-V3-eSH-10-HH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-HH | 10.3928 | 2.4156 | 528.1262 | 1686.0291 | 3.4 | 2214.1552 | 700.7052
DEER-SFAM-CZ03-V3-eSH-10-HL-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-HL | 10.2588 | 2.5268 | 542.5097 | 1705.284 | 3.4 | 2247.7937 | 714.7437
DEER-SFAM-CZ03-V3-eSH-10-HM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-HM | 10.8435 | 2.4792 | 529.4457 | 1663.3582 | 3.4 | 2192.8038 | 693.3038
DEER-SFAM-CZ03-V3-eSH-10-LH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-LH | 10.4215 | 2.3744 | 533.3222 | 1783.2141 | 3.4 | 2316.5363 | 711.9362
DEER-SFAM-CZ03-V3-eSH-10-LL-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-LL | 10.5388 | 2.5209 | 540.5053 | 1670.6468 | 3.4 | 2211.1521 | 725.0021
DEER-SFAM-CZ03-V3-eSH-10-LM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-LM | 10.6403 | 2.4457 | 535.1404 | 1668.4906 | 3.4 | 2203.631 | 704.8311
DEER-SFAM-CZ03-V3-eSH-10-MH-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-MH | 10.5376 | 2.4102 | 527.4498 | 1743.678 | 3.4 | 2271.1278 | 716.9279
DEER-SFAM-CZ03-V3-eSH-10-ML-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-ML | 10.6332 | 2.5493 | 536.2215 | 1566.6958 | 3.4 | 2102.9173 | 705.8173
DEER-SFAM-CZ03-V3-eSH-10-MM-s1 | 10 | CZ03 | V3 | CZ03-V3-eSH-10 | CZ03-V3-eSH-10-MM | 10.7598 | 2.5152 | 533.1771 | 1698.0294 | 3.4 | 2231.2065 | 694.5064
DEER-SFAM-CZ03-V3-eSH-13-HH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-HH | 13.7537 | 1.934 | 409.1478 | 1618.84 | 3.4 | 2027.9878 | 566.6878
DEER-SFAM-CZ03-V3-eSH-13-HL-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-HL | 13.4484 | 1.9517 | 413.4146 | 1396.9377 | 3.9 | 1810.3522 | 570.2023
DEER-SFAM-CZ03-V3-eSH-13-HM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-HM | 13.8839 | 1.9369 | 406.8121 | 1445.4796 | 3.4 | 1852.2918 | 548.7418
DEER-SFAM-CZ03-V3-eSH-13-LH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-LH | 13.3065 | 1.8687 | 409.4893 | 1635.3993 | 3.4 | 2044.8887 | 644.7886
DEER-SFAM-CZ03-V3-eSH-13-LL-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-LL | 14.5976 | 1.8619 | 387.6922 | 1458.9209 | 3.4 | 1846.6131 | 531.1131
DEER-SFAM-CZ03-V3-eSH-13-LM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-LM | 12.9034 | 1.9595 | 427.0403 | 1306.2305 | 3.4 | 1733.2709 | 592.3709
DEER-SFAM-CZ03-V3-eSH-13-MH-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-MH | 14.4196 | 1.7814 | 385.5643 | 1618.8854 | 3.4 | 2004.4498 | 544.4998
DEER-SFAM-CZ03-V3-eSH-13-ML-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-ML | 13.2877 | 1.9717 | 419.5516 | 1498.2422 | 3.4 | 1917.7937 | 582.3937
DEER-SFAM-CZ03-V3-eSH-13-MM-s1 | 13 | CZ03 | V3 | CZ03-V3-eSH-13 | CZ03-V3-eSH-13-MM | 14.3822 | 1.9021 | 393.8766 | 1518.3883 | 3.4 | 1912.2649 | 521.9149
DEER-SFAM-CZ03-V3-eSH-14-HH-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-HH | 14.5777 | 1.8372 | 385.735 | 1475.8648 | 3.4 | 1861.5998 | 505.7498
DEER-SFAM-CZ03-V3-eSH-14-HL-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-HL | 14.6198 | 1.8586 | 383.9234 | 1434.1122 | 3.4 | 1818.0357 | 527.9357
DEER-SFAM-CZ03-V3-eSH-14-HM-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-HM | 14.4318 | 1.8272 | 387.4058 | 1422.7623 | 3.4 | 1810.1681 | 489.6682
DEER-SFAM-CZ03-V3-eSH-14-MH-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-MH | 14.0979 | 1.7484 | 384.7905 | 1484.7815 | 3.4 | 1869.572 | 540.1219
DEER-SFAM-CZ03-V3-eSH-14-ML-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-ML | 14.585 | 1.7571 | 373.1592 | 1520.8092 | 3.4 | 1893.9684 | 566.6183
DEER-SFAM-CZ03-V3-eSH-14-MM-s1 | 14 | CZ03 | V3 | CZ03-V3-eSH-14 | CZ03-V3-eSH-14-MM | 14.0565 | 1.7954 | 383.7846 | 1386.0458 | 3.4 | 1769.8304 | 519.6804
DEER-SFAM-CZ03-V3-eSH-15-HH-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-HH | 15.5876 | 1.6586 | 355.605 | 1652.2367 | 3.4 | 2007.8417 | 466.4917
DEER-SFAM-CZ03-V3-eSH-15-HL-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-HL | 15.6552 | 1.7225 | 358.9038 | 1247.6679 | 3.4 | 1606.5717 | 469.6716
DEER-SFAM-CZ03-V3-eSH-15-HM-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-HM | 16.1021 | 1.6254 | 345.2985 | 1307.1308 | 3.4 | 1652.4293 | 455.6793
DEER-SFAM-CZ03-V3-eSH-15-MH-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-MH | 15.7568 | 1.632 | 346.1555 | 1458.2859 | 3.4 | 1804.4414 | 452.2914
DEER-SFAM-CZ03-V3-eSH-15-ML-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-ML | 15.6723 | 1.6516 | 348.2588 | 1344.6779 | 3.4 | 1692.9367 | 457.7366
DEER-SFAM-CZ03-V3-eSH-15-MM-s1 | 15 | CZ03 | V3 | CZ03-V3-eSH-15 | CZ03-V3-eSH-15-MM | 16.5266 | 1.6334 | 340.3168 | 1450.1192 | 3.4 | 1790.4361 | 456.986
DEER-SFAM-CZ03-V3-eSH-16-CH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-CH | 16.8018 | 1.7611 | 375.6335 | 1375.6255 | 3.9 | 1751.259 | 464.509
DEER-SFAM-CZ03-V3-eSH-16-CL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-CL | 16.999 | 1.7656 | 371.7033 | 1283.216 | 3.9 | 1654.9193 | 465.1693
DEER-SFAM-CZ03-V3-eSH-16-LH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-LH | 16.5987 | 1.5662 | 347.813 | 1543.7241 | 3.4 | 1891.5372 | 458.1871
DEER-SFAM-CZ03-V3-eSH-16-LL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-LL | 15.9348 | 1.7018 | 370.6988 | 1385.4705 | 3.4 | 1756.1693 | 459.3693
DEER-SFAM-CZ03-V3-eSH-16-LM-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-LM | 15.8742 | 1.6462 | 366.9735 | 1537.9388 | 3.4 | 1904.9123 | 490.3123
DEER-SFAM-CZ03-V3-eSH-16-TH-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-TH | 19.3537 | 1.6225 | 324.3076 | 1697.8446 | 3.4 | 2022.1522 | 411.5522
DEER-SFAM-CZ03-V3-eSH-16-TL-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-TL | 17.797 | 1.7808 | 352.7114 | 1650.3839 | 3.4 | 2003.0954 | 430.7953
DEER-SFAM-CZ03-V3-eSH-16-TM-s2 | 16 | CZ03 | V3 | CZ03-V3-eSH-16 | CZ03-V3-eSH-16-TM | 18.0063 | 1.7569 | 348.611 | 1682.4486 | 3.4 | 2031.0596 | 428.5596
DEER-SFAM-CZ03-V3-eSH-17-CM-s2 | 17 | CZ03 | V3 | CZ03-V3-eSH-17 | CZ03-V3-eSH-17-CM | 18.0215 | 1.6669 | 350.4271 | 1398.6296 | 3.9 | 1749.0567 | 455.5568
DEER-SFAM-CZ03-V3-eSH-17-LM-s2 | 17 | CZ03 | V3 | CZ03-V3-eSH-17 | CZ03-V3-eSH-17-LM | 17.1878 | 1.5727 | 342.1614 | 1349.0904 | 3.4 | 1691.2517 | 392.1017
DEER-SFAM-CZ03-V3-eSH-17-TH-s2 | 17 | CZ03 | V3 | CZ03-V3-eSH-17 | CZ03-V3-eSH-17-TH | 20.3382 | 1.5475 | 308.0888 | 1684.9685 | 3.4 | 1993.0573 | 401.2073
DEER-SFAM-CZ03-V3-eSH-17-TL-s2 | 17 | CZ03 | V3 | CZ03-V3-eSH-17 | CZ03-V3-eSH-17-TL | 20.2499 | 1.5675 | 309.733 | 1660.0857 | 3.4 | 1969.8187 | 401.7187
DEER-SFAM-CZ03-V3-eSH-18-LH-s2 | 18 | CZ03 | V3 | CZ03-V3-eSH-18 | CZ03-V3-eSH-18-LH | 18.2245 | 1.4868 | 321.6449 | 1495.7541 | 3.4 | 1817.399 | 401.0489
DEER-SFAM-CZ03-V3-eSH-18-LL-s2 | 18 | CZ03 | V3 | CZ03-V3-eSH-18 | CZ03-V3-eSH-18-LL | 17.3398 | 1.5501 | 337.046 | 1373.8894 | 3.4 | 1710.9354 | 413.3354
DEER-SFAM-CZ03-V3-eSH-18-LM-s2 | 18 | CZ03 | V3 | CZ03-V3-eSH-18 | CZ03-V3-eSH-18-LM | 18.3491 | 1.5008 | 322.214 | 1565.8823 | 3.4 | 1888.0962 | 412.5962
DEER-SFAM-CZ03-V3-eSH-18-TM-s2 | 18 | CZ03 | V3 | CZ03-V3-eSH-18 | CZ03-V3-eSH-18-TM | 21.7102 | 1.4541 | 283.3566 | 1623.2825 | 3.4 | 1906.6391 | 418.8891
DEER-SFAM-CZ03-V4-eSA-10-HH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-HH | 10.6116 | 2.4815 | 528.7623 | 0 | 3.4 | 528.7623 | 602.3573
DEER-SFAM-CZ03-V4-eSA-10-HL-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-HL | 10.637 | 2.5751 | 529.0653 | 0 | 3.9 | 529.0653 | 602.796
DEER-SFAM-CZ03-V4-eSA-10-HM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-HM | 10.4278 | 2.5584 | 532.2119 | 0 | 3.9 | 532.2119 | 605.9338
DEER-SFAM-CZ03-V4-eSA-10-LH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-LH | 10.3535 | 2.4514 | 519.3315 | 0 | 3.9 | 519.3315 | 593.1132
DEER-SFAM-CZ03-V4-eSA-10-LL-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-LL | 10.3344 | 2.6055 | 541.605 | 0 | 3.9 | 541.605 | 615.3479
DEER-SFAM-CZ03-V4-eSA-10-LM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-LM | 10.3469 | 2.4916 | 522.7546 | 0 | 3.9 | 522.7546 | 596.5382
DEER-SFAM-CZ03-V4-eSA-10-MH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-MH | 10.2522 | 2.4423 | 527.8066 | 0 | 3.9 | 527.8066 | 601.5707
DEER-SFAM-CZ03-V4-eSA-10-ML-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-ML | 10.459 | 2.6486 | 545.3996 | 0 | 3.9 | 545.3996 | 619.1318
DEER-SFAM-CZ03-V4-eSA-10-MM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSA-10 | CZ03-V4-eSA-10-MM | 10.6527 | 2.3588 | 505.4427 | 0 | 3.4 | 505.4427 | 579.1048
DEER-SFAM-CZ03-V4-eSA-13-HH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-HH | 13.1009 | 1.9247 | 409.049 | 0 | 3.9 | 409.049 | 475.5125
DEER-SFAM-CZ03-V4-eSA-13-HL-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-HL | 13.5049 | 1.9207 | 398.3611 | 0 | 3.9 | 398.3611 | 456.5324
DEER-SFAM-CZ03-V4-eSA-13-HM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-HM | 13.585 | 1.9626 | 402.5368 | 0 | 3.9 | 402.5368 | 468.9807
DEER-SFAM-CZ03-V4-eSA-13-LH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-LH | 13.4156 | 1.8386 | 392.7939 | 0 | 3.4 | 392.7939 | 466.4663
DEER-SFAM-CZ03-V4-eSA-13-LL-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-LL | 13.5537 | 1.9524 | 408.6587 | 0 | 3.4 | 408.6587 | 482.1902
DEER-SFAM-CZ03-V4-eSA-13-LM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-LM | 13.0998 | 1.9181 | 414.3897 | 0 | 3.4 | 414.3897 | 488.0029
DEER-SFAM-CZ03-V4-eSA-13-MH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-MH | 14.5693 | 1.864 | 383.3582 | 0 | 3.9 | 383.3582 | 457.0804
DEER-SFAM-CZ03-V4-eSA-13-ML-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-ML | 13.1866 | 1.944 | 402.2661 | 0 | 3.9 | 402.2661 | 475.7651
DEER-SFAM-CZ03-V4-eSA-13-MM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSA-13 | CZ03-V4-eSA-13-MM | 14.6996 | 1.8798 | 377.3791 | 0 | 3.9 | 377.3791 | 451.0926
DEER-SFAM-CZ03-V4-eSA-14-HH-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-HH | 13.704 | 1.8614 | 387.4921 | 0 | 3.9 | 387.4921 | 449.2837
DEER-SFAM-CZ03-V4-eSA-14-HL-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-HL | 14.7939 | 1.7951 | 369.8089 | 0 | 3.9 | 369.8089 | 415.2484
DEER-SFAM-CZ03-V4-eSA-14-HM-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-HM | 14.4474 | 1.8099 | 372.8901 | 0 | 3.9 | 372.8901 | 442.5944
DEER-SFAM-CZ03-V4-eSA-14-MH-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-MH | 13.972 | 1.8067 | 392.7332 | 0 | 3.4 | 392.7332 | 441.1243
DEER-SFAM-CZ03-V4-eSA-14-ML-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-ML | 13.9215 | 1.8086 | 378.5166 | 0 | 3.9 | 378.5166 | 455.8764
DEER-SFAM-CZ03-V4-eSA-14-MM-s1 | 14 | CZ03 | V4 | CZ03-V4-eSA-14 | CZ03-V4-eSA-14-MM | 14.1102 | 1.7679 | 380.0383 | 0 | 3.4 | 380.0383 | 433.0915
DEER-SFAM-CZ03-V4-eSA-15-HH-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-HH | 15.7969 | 1.6541 | 343.2493 | 0 | 3.9 | 343.2493 | 394.7607
DEER-SFAM-CZ03-V4-eSA-15-HL-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-HL | 16.2735 | 1.6404 | 335.4404 | 0 | 3.9 | 335.4404 | 399.6436
DEER-SFAM-CZ03-V4-eSA-15-HM-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-HM | 15.5276 | 1.6608 | 348.6601 | 0 | 3.9 | 348.6601 | 400.3633
DEER-SFAM-CZ03-V4-eSA-15-MH-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-MH | 15.2861 | 1.6665 | 349.0136 | 0 | 3.9 | 349.0136 | 387.3978
DEER-SFAM-CZ03-V4-eSA-15-ML-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-ML | 16.0684 | 1.6845 | 345.3732 | 0 | 3.4 | 345.3732 | 396.9346
DEER-SFAM-CZ03-V4-eSA-15-MM-s1 | 15 | CZ03 | V4 | CZ03-V4-eSA-15 | CZ03-V4-eSA-15-MM | 15.3568 | 1.6689 | 349.1488 | 0 | 3.9 | 349.1488 | 396.215
DEER-SFAM-CZ03-V4-eSA-16-CH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-CH | 16.4279 | 1.7971 | 374.6289 | 0 | 3.9 | 374.6289 | 404.272
DEER-SFAM-CZ03-V4-eSA-16-CL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-CL | 17.0008 | 1.7127 | 353.8929 | 0 | 3.9 | 353.8929 | 391.3585
DEER-SFAM-CZ03-V4-eSA-16-CM-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-CM | 16.6015 | 1.7535 | 363.7566 | 0 | 3.9 | 363.7566 | 403.2345
DEER-SFAM-CZ03-V4-eSA-16-LH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-LH | 16.4531 | 1.5744 | 344.0534 | 0 | 3.9 | 344.0534 | 395.0961
DEER-SFAM-CZ03-V4-eSA-16-LL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-LL | 15.9008 | 1.6449 | 357.0208 | 0 | 3.9 | 357.0208 | 390.4816
DEER-SFAM-CZ03-V4-eSA-16-LM-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-LM | 15.7397 | 1.6614 | 361.9347 | 0 | 3.9 | 361.9347 | 392.259
DEER-SFAM-CZ03-V4-eSA-16-NM-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-NM | 16.9644 | 1.5407 | 348.1538 | 0 | 3.9 | 348.1538 | 377.9519
DEER-SFAM-CZ03-V4-eSA-16-TH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-TH | 17.597 | 1.713 | 354.2928 | 0 | 3.9 | 354.2928 | 373.3723
DEER-SFAM-CZ03-V4-eSA-16-TL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSA-16 | CZ03-V4-eSA-16-TL | 18.5962 | 1.6756 | 334.2872 | 0 | 3.9 | 334.2872 | 354.8524
DEER-SFAM-CZ03-V4-eSA-17-CH-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-CH | 17.5353 | 1.6602 | 346.0638 | 0 | 3.9 | 346.0638 | 383.5181
DEER-SFAM-CZ03-V4-eSA-17-CL-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-CL | 17.5785 | 1.6675 | 345.166 | 0 | 3.9 | 345.166 | 382.6107
DEER-SFAM-CZ03-V4-eSA-17-CM-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-CM | 17.724 | 1.677 | 347.4032 | 0 | 3.9 | 347.4032 | 376.9587
DEER-SFAM-CZ03-V4-eSA-17-LH-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-LH | 16.9672 | 1.5106 | 329.8331 | 0 | 3.9 | 329.8331 | 369.8291
DEER-SFAM-CZ03-V4-eSA-17-LL-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-LL | 16.9022 | 1.5675 | 338.5707 | 0 | 3.9 | 338.5707 | 360.2702
DEER-SFAM-CZ03-V4-eSA-17-LM-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-LM | 16.6079 | 1.5876 | 344.8728 | 0 | 3.9 | 344.8728 | 363.6327
DEER-SFAM-CZ03-V4-eSA-17-TH-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-TH | 20.1255 | 1.5186 | 303.6538 | 0 | 3.9 | 303.6538 | 334.1733
DEER-SFAM-CZ03-V4-eSA-17-TL-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-TL | 21.6117 | 1.4896 | 278.2344 | 0 | 3.9 | 278.2344 | 325.7592
DEER-SFAM-CZ03-V4-eSA-17-TM-s2 | 17 | CZ03 | V4 | CZ03-V4-eSA-17 | CZ03-V4-eSA-17-TM | 19.8176 | 1.6125 | 326.0251 | 0 | 3.9 | 326.0251 | 341.9053
DEER-SFAM-CZ03-V4-eSA-18-LH-s2 | 18 | CZ03 | V4 | CZ03-V4-eSA-18 | CZ03-V4-eSA-18-LH | 17.8225 | 1.467 | 320.257 | 0 | 3.9 | 320.257 | 346.4059
DEER-SFAM-CZ03-V4-eSA-18-LL-s2 | 18 | CZ03 | V4 | CZ03-V4-eSA-18 | CZ03-V4-eSA-18-LL | 18.2579 | 1.4628 | 310.425 | 0 | 3.9 | 310.425 | 344.5846
DEER-SFAM-CZ03-V4-eSA-18-TH-s2 | 18 | CZ03 | V4 | CZ03-V4-eSA-18 | CZ03-V4-eSA-18-TH | 20.6213 | 1.4439 | 296.9219 | 0 | 3.9 | 296.9219 | 317.6329
DEER-SFAM-CZ03-V4-eSA-18-TL-s2 | 18 | CZ03 | V4 | CZ03-V4-eSA-18 | CZ03-V4-eSA-18-TL | 20.4312 | 1.5033 | 301.4173 | 0 | 3.9 | 301.4173 | 324.1787
DEER-SFAM-CZ03-V4-eSA-18-TM-s2 | 18 | CZ03 | V4 | CZ03-V4-eSA-18 | CZ03-V4-eSA-18-TM | 19.6934 | 1.5021 | 309.3349 | 0 | 3.9 | 309.3349 | 330.5204
DEER-SFAM-CZ03-V4-eSH-10-HH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-HH | 10.2883 | 2.4323 | 521.36 | 1447.9095 | 3.9 | 1969.2695 | 667.8194
DEER-SFAM-CZ03-V4-eSH-10-HL-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-HL | 10.2027 | 2.5299 | 533.3738 | 1457.7144 | 3.9 | 1991.0882 | 679.4382
DEER-SFAM-CZ03-V4-eSH-10-HM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-HM | 10.765 | 2.4886 | 523.0113 | 1424.5121 | 3.9 | 1947.5233 | 662.0233
DEER-SFAM-CZ03-V4-eSH-10-LH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-LH | 10.4294 | 2.3544 | 522.0136 | 1517.0119 | 3.4 | 2039.0255 | 673.3255
DEER-SFAM-CZ03-V4-eSH-10-LL-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-LL | 10.4991 | 2.5235 | 532.1543 | 1428.8199 | 3.9 | 1960.9741 | 688.7741
DEER-SFAM-CZ03-V4-eSH-10-LM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-LM | 10.5497 | 2.4589 | 529.1753 | 1433.2431 | 3.9 | 1962.4184 | 673.2184
DEER-SFAM-CZ03-V4-eSH-10-MH-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-MH | 10.4311 | 2.4299 | 521.3742 | 1495.8214 | 3.9 | 2017.1956 | 682.1456
DEER-SFAM-CZ03-V4-eSH-10-ML-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-ML | 10.6083 | 2.5438 | 527.2461 | 1337.7169 | 3.9 | 1864.9631 | 671.2631
DEER-SFAM-CZ03-V4-eSH-10-MM-s1 | 10 | CZ03 | V4 | CZ03-V4-eSH-10 | CZ03-V4-eSH-10-MM | 10.7801 | 2.4905 | 522.0505 | 1442.1827 | 3.4 | 1964.2332 | 658.7332
DEER-SFAM-CZ03-V4-eSH-13-HH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-HH | 13.6031 | 1.9466 | 404.1936 | 1390.1266 | 3.9 | 1794.3202 | 537.9202
DEER-SFAM-CZ03-V4-eSH-13-HL-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-HL | 13.4365 | 1.913 | 398.4133 | 1186.0723 | 3.9 | 1584.4857 | 531.2857
DEER-SFAM-CZ03-V4-eSH-13-HM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-HM | 13.7798 | 1.9425 | 400.5278 | 1237.8203 | 3.9 | 1638.3482 | 520.9982
DEER-SFAM-CZ03-V4-eSH-13-LH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-LH | 13.3232 | 1.8469 | 395.41 | 1391.4138 | 3.4 | 1786.8238 | 594.7738
DEER-SFAM-CZ03-V4-eSH-13-LL-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-LL | 14.5471 | 1.8641 | 380.1973 | 1247.4693 | 3.9 | 1627.6666 | 501.9667
DEER-SFAM-CZ03-V4-eSH-13-LM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-LM | 12.9183 | 1.943 | 417.8041 | 1108.3128 | 3.4 | 1526.1169 | 557.8169
DEER-SFAM-CZ03-V4-eSH-13-MH-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-MH | 14.2359 | 1.7999 | 381.7821 | 1394.1178 | 3.9 | 1775.8999 | 516.6499
DEER-SFAM-CZ03-V4-eSH-13-ML-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-ML | 13.3019 | 1.9545 | 410.4552 | 1270.4285 | 3.4 | 1680.8837 | 548.3837
DEER-SFAM-CZ03-V4-eSH-13-MM-s1 | 13 | CZ03 | V4 | CZ03-V4-eSH-13 | CZ03-V4-eSH-13-MM | 14.2997 | 1.9039 | 387.0136 | 1298.1516 | 3.9 | 1685.1653 | 495.6153
DEER-SFAM-CZ03-V4-eSH-14-HH-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-HH | 14.4898 | 1.8444 | 378.9751 | 1264.2182 | 3.9 | 1643.1933 | 480.8433
DEER-SFAM-CZ03-V4-eSH-14-HL-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-HL | 14.5912 | 1.8504 | 375.6336 | 1221.5795 | 3.9 | 1597.2131 | 497.8631
DEER-SFAM-CZ03-V4-eSH-14-HM-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-HM | 14.3449 | 1.8328 | 380.628 | 1218.0162 | 3.9 | 1598.6443 | 467.4443
DEER-SFAM-CZ03-V4-eSH-14-MH-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-MH | 14.0943 | 1.7337 | 375.3856 | 1262.9019 | 3.4 | 1638.2875 | 507.0374
DEER-SFAM-CZ03-V4-eSH-14-ML-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-ML | 14.537 | 1.7537 | 365.6886 | 1293.3653 | 3.9 | 1659.0539 | 529.9538
DEER-SFAM-CZ03-V4-eSH-14-MM-s1 | 14 | CZ03 | V4 | CZ03-V4-eSH-14 | CZ03-V4-eSH-14-MM | 14.056 | 1.7786 | 374.6943 | 1177.4142 | 3.4 | 1552.1085 | 489.8085
DEER-SFAM-CZ03-V4-eSH-15-HH-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-HH | 15.4532 | 1.6676 | 350.2982 | 1408.9247 | 3.9 | 1759.223 | 444.473
DEER-SFAM-CZ03-V4-eSH-15-HL-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-HL | 15.597 | 1.7182 | 351.8075 | 1065.2375 | 3.9 | 1417.045 | 445.795
DEER-SFAM-CZ03-V4-eSH-15-HM-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-HM | 16.0144 | 1.6275 | 339.1574 | 1118.0068 | 3.9 | 1457.1643 | 432.8143
DEER-SFAM-CZ03-V4-eSH-15-MH-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-MH | 15.641 | 1.6402 | 339.9203 | 1244.4219 | 3.9 | 1584.3422 | 429.9922
DEER-SFAM-CZ03-V4-eSH-15-ML-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-ML | 15.6206 | 1.6484 | 340.5804 | 1145.2885 | 3.9 | 1485.8688 | 433.5188
DEER-SFAM-CZ03-V4-eSH-15-MM-s1 | 15 | CZ03 | V4 | CZ03-V4-eSH-15 | CZ03-V4-eSH-15-MM | 16.442 | 1.6309 | 334.1892 | 1237.815 | 3.9 | 1572.0042 | 433.2543
DEER-SFAM-CZ03-V4-eSH-16-CH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-CH | 16.8124 | 1.7466 | 365.2556 | 1170.7553 | 3.9 | 1536.0108 | 440.5109
DEER-SFAM-CZ03-V4-eSH-16-CL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-CL | 17.0055 | 1.7507 | 361.9092 | 1091.8725 | 3.9 | 1453.7816 | 441.0817
DEER-SFAM-CZ03-V4-eSH-16-LH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-LH | 16.2871 | 1.5525 | 345.1339 | 1328.468 | 3.9 | 1673.6019 | 438.7519
DEER-SFAM-CZ03-V4-eSH-16-LL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-LL | 15.8065 | 1.6666 | 361.6123 | 1179.5174 | 3.9 | 1541.1297 | 436.8797
DEER-SFAM-CZ03-V4-eSH-16-LM-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-LM | 15.6277 | 1.6164 | 362.9726 | 1319.2459 | 3.9 | 1682.2185 | 467.6185
DEER-SFAM-CZ03-V4-eSH-16-TH-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-TH | 19.022 | 1.5946 | 321.384 | 1457.4313 | 3.9 | 1778.8152 | 391.6652
DEER-SFAM-CZ03-V4-eSH-16-TL-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-TL | 17.8334 | 1.7606 | 348.9298 | 1397.7209 | 3.9 | 1746.6507 | 410.8007
DEER-SFAM-CZ03-V4-eSH-16-TM-s2 | 16 | CZ03 | V4 | CZ03-V4-eSH-16 | CZ03-V4-eSH-16-TM | 18.0115 | 1.7428 | 345.4798 | 1426.7776 | 3.9 | 1772.2574 | 408.7074
DEER-SFAM-CZ03-V4-eSH-17-CM-s2 | 17 | CZ03 | V4 | CZ03-V4-eSH-17 | CZ03-V4-eSH-17-CM | 18.0462 | 1.6534 | 340.841 | 1186.9318 | 3.9 | 1527.7729 | 429.6729
DEER-SFAM-CZ03-V4-eSH-17-LM-s2 | 17 | CZ03 | V4 | CZ03-V4-eSH-17 | CZ03-V4-eSH-17-LM | 17.0455 | 1.5593 | 337.1101 | 1150.2293 | 3.9 | 1487.3393 | 379.4894
DEER-SFAM-CZ03-V4-eSH-17-TH-s2 | 17 | CZ03 | V4 | CZ03-V4-eSH-17 | CZ03-V4-eSH-17-TH | 20.099 | 1.5284 | 303.3494 | 1441.9552 | 3.9 | 1745.3046 | 378.0045
DEER-SFAM-CZ03-V4-eSH-17-TL-s2 | 17 | CZ03 | V4 | CZ03-V4-eSH-17 | CZ03-V4-eSH-17-TL | 20.0108 | 1.5425 | 305.0122 | 1417.5798 | 3.9 | 1722.592 | 378.892
DEER-SFAM-CZ03-V4-eSH-18-LH-s2 | 18 | CZ03 | V4 | CZ03-V4-eSH-18 | CZ03-V4-eSH-18-LH | 18.0715 | 1.4631 | 314.3524 | 1265.9888 | 3.9 | 1580.3411 | 381.1911
DEER-SFAM-CZ03-V4-eSH-18-LL-s2 | 18 | CZ03 | V4 | CZ03-V4-eSH-18 | CZ03-V4-eSH-18-LL | 17.2058 | 1.5251 | 328.7187 | 1166.8449 | 3.9 | 1495.5636 | 393.4136
DEER-SFAM-CZ03-V4-eSH-18-LM-s2 | 18 | CZ03 | V4 | CZ03-V4-eSH-18 | CZ03-V4-eSH-18-LM | 18.1842 | 1.4667 | 315.1884 | 1323.4034 | 3.9 | 1638.5918 | 391.0917
DEER-SFAM-CZ03-V4-eSH-18-TM-s2 | 18 | CZ03 | V4 | CZ03-V4-eSH-18 | CZ03-V4-eSH-18-TM | 21.508 | 1.4426 | 284.5591 | 1387.5284 | 3.9 | 1672.0875 | 393.2876
DEER-SFAM-CZ04-V1-eSA-10-HH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-HH | 10.3791 | 3.5663 | 1272.0892 | 0 | 3.4688 | 1272.0892 | 1456.1893
DEER-SFAM-CZ04-V1-eSA-10-HL-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-HL | 10.2409 | 3.7878 | 1263.7457 | 0 | 3.4688 | 1263.7457 | 1447.9864
DEER-SFAM-CZ04-V1-eSA-10-HM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-HM | 10.2081 | 3.6413 | 1257.9797 | 0 | 3.4688 | 1257.9797 | 1442.1955
DEER-SFAM-CZ04-V1-eSA-10-LH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-LH | 10.7951 | 3.332 | 1185.7231 | 0 | 3.4688 | 1185.7231 | 1370.1057
DEER-SFAM-CZ04-V1-eSA-10-LL-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-LL | 10.1484 | 3.734 | 1267.5235 | 0 | 3.4688 | 1267.5235 | 1451.7981
DEER-SFAM-CZ04-V1-eSA-10-LM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-LM | 10.6888 | 3.4273 | 1205.4988 | 0 | 3.4688 | 1205.4988 | 1389.8877
DEER-SFAM-CZ04-V1-eSA-10-MH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-MH | 10.6797 | 3.2732 | 1205.3722 | 0 | 3.4688 | 1205.3722 | 1389.7048
DEER-SFAM-CZ04-V1-eSA-10-ML-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-ML | 10.2051 | 3.7934 | 1289.824 | 0 | 3.4688 | 1289.824 | 1474.0687
DEER-SFAM-CZ04-V1-eSA-10-MM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSA-10 | CZ04-V1-eSA-10-MM | 10.7511 | 3.4274 | 1183.3537 | 0 | 3.4688 | 1183.3537 | 1367.6134
DEER-SFAM-CZ04-V1-eSA-13-HH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-HH | 12.8795 | 2.8083 | 955.5201 | 0 | 3.4688 | 955.5201 | 1121.5964
DEER-SFAM-CZ04-V1-eSA-13-HL-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-HL | 13.623 | 2.8466 | 931.6006 | 0 | 3.4688 | 931.6006 | 1076.9489
DEER-SFAM-CZ04-V1-eSA-13-HM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-HM | 13.2562 | 2.915 | 948.374 | 0 | 3.711 | 948.374 | 1114.4656
DEER-SFAM-CZ04-V1-eSA-13-LH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-LH | 13.7727 | 2.5426 | 915.146 | 0 | 3.4688 | 915.146 | 1099.4303
DEER-SFAM-CZ04-V1-eSA-13-LL-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-LL | 13.5022 | 2.7611 | 957.2877 | 0 | 3.4688 | 957.2877 | 1141.2354
DEER-SFAM-CZ04-V1-eSA-13-LM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-LM | 13.4576 | 2.647 | 950.4046 | 0 | 3.4688 | 950.4046 | 1134.548
DEER-SFAM-CZ04-V1-eSA-13-MH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-MH | 14.1348 | 2.6319 | 915.393 | 0 | 3.4688 | 915.393 | 1099.6099
DEER-SFAM-CZ04-V1-eSA-13-ML-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-ML | 13.4379 | 2.8352 | 936.0188 | 0 | 3.4688 | 936.0188 | 1119.6708
DEER-SFAM-CZ04-V1-eSA-13-MM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSA-13 | CZ04-V1-eSA-13-MM | 14.086 | 2.7351 | 916.7407 | 0 | 3.4688 | 916.7407 | 1100.9337
DEER-SFAM-CZ04-V1-eSA-14-HH-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-HH | 13.8928 | 2.6957 | 904.2586 | 0 | 3.4688 | 904.2586 | 1058.6502
DEER-SFAM-CZ04-V1-eSA-14-HL-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-HL | 14.5777 | 2.5808 | 862.3188 | 0 | 3.4688 | 862.3188 | 975.8467
DEER-SFAM-CZ04-V1-eSA-14-HM-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-HM | 14.6949 | 2.5981 | 860.7241 | 0 | 3.4688 | 860.7241 | 1034.9043
DEER-SFAM-CZ04-V1-eSA-14-MH-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-MH | 14.3484 | 2.4715 | 905.9831 | 0 | 3.4688 | 905.9831 | 1027.0214
DEER-SFAM-CZ04-V1-eSA-14-ML-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-ML | 14.4426 | 2.5721 | 866.9362 | 0 | 3.4688 | 866.9362 | 1060.247
DEER-SFAM-CZ04-V1-eSA-14-MM-s1 | 14 | CZ04 | V1 | CZ04-V1-eSA-14 | CZ04-V1-eSA-14-MM | 14.4633 | 2.4554 | 878.8867 | 0 | 3.4688 | 878.8867 | 1011.5855
DEER-SFAM-CZ04-V1-eSA-15-HH-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-HH | 15.3016 | 2.4792 | 814.2392 | 0 | 3.711 | 814.2392 | 942.9967
DEER-SFAM-CZ04-V1-eSA-15-HL-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-HL | 15.6863 | 2.3846 | 798.7655 | 0 | 3.711 | 798.7655 | 959.2503
DEER-SFAM-CZ04-V1-eSA-15-HM-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-HM | 15.0919 | 2.5006 | 823.2427 | 0 | 3.711 | 823.2427 | 952.4777
DEER-SFAM-CZ04-V1-eSA-15-MH-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-MH | 15.5704 | 2.376 | 808.519 | 0 | 3.4688 | 808.519 | 904.42
DEER-SFAM-CZ04-V1-eSA-15-ML-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-ML | 15.7068 | 2.4339 | 824.1268 | 0 | 3.4688 | 824.1268 | 953.1032
DEER-SFAM-CZ04-V1-eSA-15-MM-s1 | 15 | CZ04 | V1 | CZ04-V1-eSA-15 | CZ04-V1-eSA-15-MM | 15.642 | 2.3826 | 808.6897 | 0 | 3.4688 | 808.6897 | 926.2858
DEER-SFAM-CZ04-V1-eSA-16-CH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-CH | 15.9125 | 2.837 | 978.652 | 0 | 3.4688 | 978.652 | 1051.8932
DEER-SFAM-CZ04-V1-eSA-16-CL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-CL | 16.2422 | 2.9446 | 934.3329 | 0 | 3.711 | 934.3329 | 1027.4989
DEER-SFAM-CZ04-V1-eSA-16-CM-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-CM | 15.9749 | 2.9428 | 955.7653 | 0 | 3.711 | 955.7653 | 1054.1256
DEER-SFAM-CZ04-V1-eSA-16-LH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-LH | 15.3678 | 2.6547 | 911.0192 | 0 | 3.4688 | 911.0192 | 1037.2237
DEER-SFAM-CZ04-V1-eSA-16-LL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-LL | 14.9897 | 2.7957 | 939.9212 | 0 | 3.4688 | 939.9212 | 1022.9164
DEER-SFAM-CZ04-V1-eSA-16-LM-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-LM | 15.1881 | 2.7167 | 933.4547 | 0 | 3.4688 | 933.4547 | 1008.675
DEER-SFAM-CZ04-V1-eSA-16-NM-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-NM | 16.678 | 2.5865 | 874.8883 | 0 | 3.4688 | 874.8883 | 948.6395
DEER-SFAM-CZ04-V1-eSA-16-TH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-TH | 15.8417 | 2.9114 | 1027.4474 | 0 | 3.4688 | 1027.4474 | 1074.1429
DEER-SFAM-CZ04-V1-eSA-16-TL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSA-16 | CZ04-V1-eSA-16-TL | 16.2572 | 2.925 | 992.3203 | 0 | 3.4688 | 992.3203 | 1042.8747
DEER-SFAM-CZ04-V1-eSA-17-CH-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-CH | 17.0067 | 2.7575 | 898.6175 | 0 | 3.711 | 898.6175 | 991.7252
DEER-SFAM-CZ04-V1-eSA-17-CL-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-CL | 16.982 | 2.804 | 900.1245 | 0 | 3.711 | 900.1245 | 993.2123
DEER-SFAM-CZ04-V1-eSA-17-CM-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-CM | 17.069 | 2.7997 | 917.3616 | 0 | 3.711 | 917.3616 | 990.449
DEER-SFAM-CZ04-V1-eSA-17-LH-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-LH | 16.084 | 2.559 | 865.0094 | 0 | 3.4688 | 865.0094 | 963.9533
DEER-SFAM-CZ04-V1-eSA-17-LL-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-LL | 15.9993 | 2.6767 | 894.8049 | 0 | 3.4688 | 894.8049 | 948.7695
DEER-SFAM-CZ04-V1-eSA-17-LM-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-LM | 15.8652 | 2.6267 | 895.153 | 0 | 3.4688 | 895.153 | 941.7402
DEER-SFAM-CZ04-V1-eSA-17-TH-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-TH | 18.0912 | 2.4629 | 865.5442 | 0 | 3.4688 | 865.5442 | 940.4657
DEER-SFAM-CZ04-V1-eSA-17-TL-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-TL | 18.3411 | 2.5126 | 842.3943 | 0 | 3.4688 | 842.3943 | 960.1448
DEER-SFAM-CZ04-V1-eSA-17-TM-s2 | 17 | CZ04 | V1 | CZ04-V1-eSA-17 | CZ04-V1-eSA-17-TM | 17.501 | 2.7443 | 979.6081 | 0 | 3.4688 | 979.6081 | 1018.5897
DEER-SFAM-CZ04-V1-eSA-18-LH-s2 | 18 | CZ04 | V1 | CZ04-V1-eSA-18 | CZ04-V1-eSA-18-LH | 16.9019 | 2.4775 | 843.1489 | 0 | 3.4688 | 843.1489 | 908.0172
DEER-SFAM-CZ04-V1-eSA-18-LL-s2 | 18 | CZ04 | V1 | CZ04-V1-eSA-18 | CZ04-V1-eSA-18-LL | 17.1983 | 2.4891 | 824.8274 | 0 | 3.4688 | 824.8274 | 909.4742
DEER-SFAM-CZ04-V1-eSA-18-TH-s2 | 18 | CZ04 | V1 | CZ04-V1-eSA-18 | CZ04-V1-eSA-18-TH | 18.5459 | 2.3546 | 845.7543 | 0 | 3.4688 | 845.7543 | 896.7332
DEER-SFAM-CZ04-V1-eSA-18-TL-s2 | 18 | CZ04 | V1 | CZ04-V1-eSA-18 | CZ04-V1-eSA-18-TL | 18.1158 | 2.5926 | 880.0641 | 0 | 3.4688 | 880.0641 | 935.948
DEER-SFAM-CZ04-V1-eSA-18-TM-s2 | 18 | CZ04 | V1 | CZ04-V1-eSA-18 | CZ04-V1-eSA-18-TM | 18.0754 | 2.4045 | 864.2993 | 0 | 3.4688 | 864.2993 | 916.3613
DEER-SFAM-CZ04-V1-eSH-10-HH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-HH | 10.4214 | 3.3564 | 1211.1346 | 4004.4357 | 3.4688 | 5215.5703 | 1624.4854
DEER-SFAM-CZ04-V1-eSH-10-HL-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-HL | 10.2599 | 3.5583 | 1248.6915 | 4044.734 | 3.4688 | 5293.4256 | 1657.2542
DEER-SFAM-CZ04-V1-eSH-10-HM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-HM | 10.5065 | 3.5069 | 1240.8783 | 3890.5218 | 3.4688 | 5131.4001 | 1632.565
DEER-SFAM-CZ04-V1-eSH-10-LH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-LH | 10.6409 | 3.2139 | 1206.8823 | 4247.8973 | 3.4688 | 5454.7796 | 1633.3036
DEER-SFAM-CZ04-V1-eSH-10-LL-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-LL | 10.3947 | 3.4782 | 1245.9139 | 4122.7458 | 3.4688 | 5368.6597 | 1689.3718
DEER-SFAM-CZ04-V1-eSH-10-LM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-LM | 10.4229 | 3.3665 | 1235.4464 | 4021.3555 | 3.4688 | 5256.8019 | 1641.0997
DEER-SFAM-CZ04-V1-eSH-10-MH-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-MH | 10.7312 | 3.3178 | 1200.2398 | 4206.6239 | 3.4688 | 5406.8637 | 1653.4818
DEER-SFAM-CZ04-V1-eSH-10-ML-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-ML | 10.4212 | 3.5842 | 1237.9244 | 3847.9841 | 3.4688 | 5085.9085 | 1646.5273
DEER-SFAM-CZ04-V1-eSH-10-MM-s1 | 10 | CZ04 | V1 | CZ04-V1-eSH-10 | CZ04-V1-eSH-10-MM | 10.4537 | 3.5819 | 1262.4776 | 4060.8169 | 3.4688 | 5323.2945 | 1645.4434
DEER-SFAM-CZ04-V1-eSH-13-HH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-HH | 13.2893 | 2.805 | 954.7179 | 3951.4887 | 3.4688 | 4906.2066 | 1330.6148
DEER-SFAM-CZ04-V1-eSH-13-HL-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-HL | 13.1321 | 2.8499 | 935.8018 | 3407.1197 | 3.711 | 4342.9215 | 1310.9336
DEER-SFAM-CZ04-V1-eSH-13-HM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-HM | 13.3826 | 2.8284 | 953.0307 | 3494.1722 | 3.4688 | 4447.2029 | 1292.0577
DEER-SFAM-CZ04-V1-eSH-13-LH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-LH | 13.762 | 2.5428 | 918.7547 | 4338.2344 | 3.4688 | 5256.9891 | 1483.8592
DEER-SFAM-CZ04-V1-eSH-13-LL-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-LL | 13.9175 | 2.6746 | 918.4445 | 3650.6316 | 3.4688 | 4569.0762 | 1262.1656
DEER-SFAM-CZ04-V1-eSH-13-LM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-LM | 13.31 | 2.6859 | 956.2356 | 3118.0022 | 3.4688 | 4074.2378 | 1348.0004
DEER-SFAM-CZ04-V1-eSH-13-MH-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-MH | 13.9358 | 2.5379 | 897.2268 | 4007.3388 | 3.4688 | 4904.5656 | 1275.6303
DEER-SFAM-CZ04-V1-eSH-13-ML-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-ML | 13.3838 | 2.8088 | 954.3347 | 3770.5395 | 3.4688 | 4724.8742 | 1343.1353
DEER-SFAM-CZ04-V1-eSH-13-MM-s1 | 13 | CZ04 | V1 | CZ04-V1-eSH-13 | CZ04-V1-eSH-13-MM | 13.8792 | 2.7446 | 926.7575 | 3662.589 | 3.4688 | 4589.3465 | 1228.38
DEER-SFAM-CZ04-V1-eSH-14-HH-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-HH | 14.0946 | 2.6935 | 900.1031 | 3617.7202 | 3.4688 | 4517.8233 | 1186.3887
DEER-SFAM-CZ04-V1-eSH-14-HL-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-HL | 14.1624 | 2.74 | 893.0089 | 3641.5378 | 3.4688 | 4534.5466 | 1238.0348
DEER-SFAM-CZ04-V1-eSH-14-HM-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-HM | 14.0547 | 2.6469 | 896.71 | 3572.9959 | 3.4688 | 4469.7059 | 1141.5139
DEER-SFAM-CZ04-V1-eSH-14-MH-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-MH | 14.5726 | 2.3854 | 863.2607 | 3923.3347 | 3.4688 | 4786.5953 | 1235.9113
DEER-SFAM-CZ04-V1-eSH-14-ML-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-ML | 14.9071 | 2.5127 | 844.2456 | 4199.0751 | 3.4688 | 5043.3207 | 1315.0903
DEER-SFAM-CZ04-V1-eSH-14-MM-s1 | 14 | CZ04 | V1 | CZ04-V1-eSH-14 | CZ04-V1-eSH-14-MM | 14.4992 | 2.5005 | 863.1783 | 3546.4324 | 3.4688 | 4409.6107 | 1187.6384
DEER-SFAM-CZ04-V1-eSH-15-HH-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-HH | 15.0049 | 2.4382 | 829.6198 | 4409.2262 | 3.4688 | 5238.846 | 1094.7687
DEER-SFAM-CZ04-V1-eSH-15-HL-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-HL | 15.1579 | 2.5129 | 833.9878 | 3063.7528 | 3.4688 | 3897.7405 | 1097.8314
DEER-SFAM-CZ04-V1-eSH-15-HM-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-HM | 15.6684 | 2.3563 | 796.6848 | 3219.6701 | 3.4688 | 4016.3549 | 1060.7425
DEER-SFAM-CZ04-V1-eSH-15-MH-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-MH | 15.9918 | 2.3792 | 788.3997 | 3877.0942 | 3.4688 | 4665.494 | 1044.7791
DEER-SFAM-CZ04-V1-eSH-15-ML-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-ML | 15.9096 | 2.3779 | 791.5397 | 3631.3126 | 3.4688 | 4422.8523 | 1057.3884
DEER-SFAM-CZ04-V1-eSH-15-MM-s1 | 15 | CZ04 | V1 | CZ04-V1-eSH-15 | CZ04-V1-eSH-15-MM | 15.8438 | 2.3708 | 796.1108 | 3792.4876 | 3.4688 | 4588.5984 | 1075.5313
DEER-SFAM-CZ04-V1-eSH-16-CH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-CH | 16.1938 | 2.8831 | 964.8365 | 3977.4969 | 3.711 | 4942.3333 | 1221.2427
DEER-SFAM-CZ04-V1-eSH-16-CL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-CL | 16.3646 | 2.9079 | 956.2044 | 3704.1145 | 3.711 | 4660.3188 | 1221.3309
DEER-SFAM-CZ04-V1-eSH-16-LH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-LH | 15.3735 | 2.5627 | 904.1212 | 4254.3788 | 3.4688 | 5158.5 | 1188.8766
DEER-SFAM-CZ04-V1-eSH-16-LL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-LL | 15.1655 | 2.762 | 932.9883 | 3957.7209 | 3.4688 | 4890.7092 | 1164.4
DEER-SFAM-CZ04-V1-eSH-16-LM-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-LM | 14.9394 | 2.667 | 932.9409 | 4304.4772 | 3.4688 | 5237.4181 | 1252.5918
DEER-SFAM-CZ04-V1-eSH-16-TH-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-TH | 16.5292 | 2.7601 | 945.9714 | 4938.9713 | 3.711 | 5884.9428 | 1226.332
DEER-SFAM-CZ04-V1-eSH-16-TL-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-TL | 16.0413 | 3.0036 | 1016.1556 | 4930.596 | 3.4688 | 5946.7516 | 1279.1881
DEER-SFAM-CZ04-V1-eSH-16-TM-s2 | 16 | CZ04 | V1 | CZ04-V1-eSH-16 | CZ04-V1-eSH-16-TM | 16.2119 | 2.9544 | 1005.4787 | 4984.5377 | 3.4688 | 5990.0164 | 1274.6947
DEER-SFAM-CZ04-V1-eSH-17-CM-s2 | 17 | CZ04 | V1 | CZ04-V1-eSH-17 | CZ04-V1-eSH-17-CM | 17.3419 | 2.7493 | 902.1646 | 4089.3022 | 3.711 | 4991.4668 | 1200.1579
DEER-SFAM-CZ04-V1-eSH-17-LM-s2 | 17 | CZ04 | V1 | CZ04-V1-eSH-17 | CZ04-V1-eSH-17-LM | 16.1706 | 2.5916 | 884.9143 | 3827.5562 | 3.4688 | 4712.4705 | 1014.7629
DEER-SFAM-CZ04-V1-eSH-17-TH-s2 | 17 | CZ04 | V1 | CZ04-V1-eSH-17 | CZ04-V1-eSH-17-TH | 17.8901 | 2.5042 | 872.3668 | 4930.7733 | 3.4688 | 5803.14 | 1175.3495
DEER-SFAM-CZ04-V1-eSH-17-TL-s2 | 17 | CZ04 | V1 | CZ04-V1-eSH-17 | CZ04-V1-eSH-17-TL | 17.7425 | 2.5626 | 878.149 | 4916.4482 | 3.4688 | 5794.5973 | 1178.3696
DEER-SFAM-CZ04-V1-eSH-18-LH-s2 | 18 | CZ04 | V1 | CZ04-V1-eSH-18 | CZ04-V1-eSH-18-LH | 17.2761 | 2.4651 | 824.9329 | 4451.2487 | 3.4688 | 5276.1816 | 1050.6123
DEER-SFAM-CZ04-V1-eSH-18-LL-s2 | 18 | CZ04 | V1 | CZ04-V1-eSH-18 | CZ04-V1-eSH-18-LL | 16.6168 | 2.5348 | 845.0914 | 4006.2144 | 3.4688 | 4851.3058 | 1046.6447
DEER-SFAM-CZ04-V1-eSH-18-LM-s2 | 18 | CZ04 | V1 | CZ04-V1-eSH-18 | CZ04-V1-eSH-18-LM | 17.1194 | 2.5157 | 834.4643 | 4691.6576 | 3.4688 | 5526.1219 | 1094.0987
DEER-SFAM-CZ04-V1-eSH-18-TM-s2 | 18 | CZ04 | V1 | CZ04-V1-eSH-18 | CZ04-V1-eSH-18-TM | 19.2161 | 2.4624 | 818.0775 | 4923.3516 | 3.4688 | 5741.4291 | 1251.2178
DEER-SFAM-CZ04-V2-eSA-10-HH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-HH | 10.2641 | 2.9523 | 773.7622 | 0 | 3.1141 | 773.7622 | 866.2243
DEER-SFAM-CZ04-V2-eSA-10-HL-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-HL | 10.1586 | 3.0995 | 765.6707 | 0 | 3.1141 | 765.6707 | 858.2009
DEER-SFAM-CZ04-V2-eSA-10-HM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-HM | 10.1295 | 2.9522 | 761.2871 | 0 | 3.1141 | 761.2871 | 853.8054
DEER-SFAM-CZ04-V2-eSA-10-LH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-LH | 10.7134 | 2.683 | 724.0435 | 0 | 3.1141 | 724.0435 | 816.6412
DEER-SFAM-CZ04-V2-eSA-10-LL-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-LL | 10.0922 | 3.0493 | 766.0518 | 0 | 3.1141 | 766.0518 | 858.597
DEER-SFAM-CZ04-V2-eSA-10-LM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-LM | 10.6128 | 2.7804 | 735.6033 | 0 | 3.1141 | 735.6033 | 828.2041
DEER-SFAM-CZ04-V2-eSA-10-MH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-MH | 10.5224 | 2.6668 | 737.1403 | 0 | 3.1141 | 737.1403 | 829.7142
DEER-SFAM-CZ04-V2-eSA-10-ML-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-ML | 10.1381 | 3.102 | 780.0485 | 0 | 3.1141 | 780.0485 | 872.5801
DEER-SFAM-CZ04-V2-eSA-10-MM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSA-10 | CZ04-V2-eSA-10-MM | 10.6738 | 2.7314 | 722.3772 | 0 | 3.1141 | 722.3772 | 814.9159
DEER-SFAM-CZ04-V2-eSA-13-HH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-HH | 12.7192 | 2.279 | 580.8691 | 0 | 3.1141 | 580.8691 | 664.2766
DEER-SFAM-CZ04-V2-eSA-13-HL-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-HL | 13.5817 | 2.2524 | 565.4975 | 0 | 3.1141 | 565.4975 | 638.4968
DEER-SFAM-CZ04-V2-eSA-13-HM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-HM | 13.237 | 2.3044 | 570.9816 | 0 | 3.1141 | 570.9816 | 654.3637
DEER-SFAM-CZ04-V2-eSA-13-LH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-LH | 13.6563 | 2.0708 | 555.9542 | 0 | 3.1141 | 555.9542 | 648.5047
DEER-SFAM-CZ04-V2-eSA-13-LL-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-LL | 13.442 | 2.2452 | 578.2252 | 0 | 3.1141 | 578.2252 | 670.6143
DEER-SFAM-CZ04-V2-eSA-13-LM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-LM | 13.3409 | 2.1571 | 577.0226 | 0 | 3.1141 | 577.0226 | 669.5052
DEER-SFAM-CZ04-V2-eSA-13-MH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-MH | 13.9598 | 2.1287 | 558.0529 | 0 | 3.1141 | 558.0529 | 650.5712
DEER-SFAM-CZ04-V2-eSA-13-ML-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-ML | 13.3687 | 2.2914 | 565.8204 | 0 | 3.1141 | 565.8204 | 658.056
DEER-SFAM-CZ04-V2-eSA-13-MM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSA-13 | CZ04-V2-eSA-13-MM | 14.0051 | 2.2147 | 555.3243 | 0 | 3.1141 | 555.3243 | 647.8312
DEER-SFAM-CZ04-V2-eSA-14-HH-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-HH | 13.779 | 2.1908 | 548.0899 | 0 | 3.1141 | 548.0899 | 625.6315
DEER-SFAM-CZ04-V2-eSA-14-HL-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-HL | 14.4896 | 2.0293 | 520.9881 | 0 | 3.1141 | 520.9881 | 578.0076
DEER-SFAM-CZ04-V2-eSA-14-HM-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-HM | 14.6472 | 2.0532 | 522.8522 | 0 | 3.1141 | 522.8522 | 610.3289
DEER-SFAM-CZ04-V2-eSA-14-MH-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-MH | 14.1823 | 2.0371 | 551.6955 | 0 | 3.1141 | 551.6955 | 612.4884
DEER-SFAM-CZ04-V2-eSA-14-ML-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-ML | 14.3899 | 2.043 | 523.6826 | 0 | 3.1141 | 523.6826 | 620.7673
DEER-SFAM-CZ04-V2-eSA-14-MM-s1 | 14 | CZ04 | V2 | CZ04-V2-eSA-14 | CZ04-V2-eSA-14-MM | 14.3197 | 2.0023 | 534.3182 | 0 | 3.1141 | 534.3182 | 600.9656
DEER-SFAM-CZ04-V2-eSA-15-HH-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-HH | 15.1905 | 1.9639 | 496.0372 | 0 | 3.1141 | 496.0372 | 560.6778
DEER-SFAM-CZ04-V2-eSA-15-HL-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-HL | 15.5955 | 1.878 | 482.4135 | 0 | 3.1141 | 482.4135 | 562.981
DEER-SFAM-CZ04-V2-eSA-15-HM-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-HM | 15.0096 | 1.9642 | 497.1813 | 0 | 3.1141 | 497.1813 | 562.062
DEER-SFAM-CZ04-V2-eSA-15-MH-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-MH | 15.4023 | 1.8778 | 494.2936 | 0 | 3.1141 | 494.2936 | 542.4599
DEER-SFAM-CZ04-V2-eSA-15-ML-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-ML | 15.6216 | 1.9548 | 497.9154 | 0 | 3.1141 | 497.9154 | 562.6977
DEER-SFAM-CZ04-V2-eSA-15-MM-s1 | 15 | CZ04 | V2 | CZ04-V2-eSA-15 | CZ04-V2-eSA-15-MM | 15.5829 | 1.8806 | 491.1224 | 0 | 3.1141 | 491.1224 | 550.1839
DEER-SFAM-CZ04-V2-eSA-16-CH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-CH | 15.8365 | 2.3125 | 589.4319 | 0 | 3.1141 | 589.4319 | 626.8859
DEER-SFAM-CZ04-V2-eSA-16-CL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-CL | 16.1576 | 2.2952 | 561.8605 | 0 | 3.1141 | 561.8605 | 609.2802
DEER-SFAM-CZ04-V2-eSA-16-CM-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-CM | 15.8815 | 2.3078 | 575.3564 | 0 | 3.1141 | 575.3564 | 625.4184
DEER-SFAM-CZ04-V2-eSA-16-LH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-LH | 14.9515 | 2.1216 | 560.0892 | 0 | 3.1141 | 560.0892 | 624.1536
DEER-SFAM-CZ04-V2-eSA-16-LL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-LL | 14.7035 | 2.2371 | 574.1384 | 0 | 3.1141 | 574.1384 | 616.1836
DEER-SFAM-CZ04-V2-eSA-16-LM-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-LM | 14.9053 | 2.185 | 568.7123 | 0 | 3.1141 | 568.7123 | 606.8269
DEER-SFAM-CZ04-V2-eSA-16-NM-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-NM | 16.5064 | 2.0268 | 523.2499 | 0 | 3.1141 | 523.2499 | 560.6799
DEER-SFAM-CZ04-V2-eSA-16-TH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-TH | 15.3989 | 2.3842 | 630.4081 | 0 | 3.1141 | 630.4081 | 654.4197
DEER-SFAM-CZ04-V2-eSA-16-TL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSA-16 | CZ04-V2-eSA-16-TL | 16.0525 | 2.3724 | 598.5718 | 0 | 3.1141 | 598.5718 | 624.4572
DEER-SFAM-CZ04-V2-eSA-17-CH-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-CH | 16.9369 | 2.1666 | 539.3505 | 0 | 3.1141 | 539.3505 | 586.7505
DEER-SFAM-CZ04-V2-eSA-17-CL-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-CL | 16.9236 | 2.1975 | 539.9439 | 0 | 3.1141 | 539.9439 | 587.3331
DEER-SFAM-CZ04-V2-eSA-17-CM-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-CM | 17.003 | 2.1974 | 549.2754 | 0 | 3.1141 | 549.2754 | 586.616
DEER-SFAM-CZ04-V2-eSA-17-LH-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-LH | 15.7072 | 2.0454 | 530.1489 | 0 | 3.1141 | 530.1489 | 580.3412
DEER-SFAM-CZ04-V2-eSA-17-LL-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-LL | 15.7248 | 2.1424 | 544.6371 | 0 | 3.1141 | 544.6371 | 571.946
DEER-SFAM-CZ04-V2-eSA-17-LM-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-LM | 15.587 | 2.0869 | 544.684 | 0 | 3.1141 | 544.684 | 568.274
DEER-SFAM-CZ04-V2-eSA-17-TH-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-TH | 17.4453 | 2.0134 | 535.1208 | 0 | 3.1141 | 535.1208 | 573.4912
DEER-SFAM-CZ04-V2-eSA-17-TL-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-TL | 18.2016 | 2.0343 | 510.514 | 0 | 3.1141 | 510.514 | 570.7133
DEER-SFAM-CZ04-V2-eSA-17-TM-s2 | 17 | CZ04 | V2 | CZ04-V2-eSA-17 | CZ04-V2-eSA-17-TM | 17.1605 | 2.2562 | 586.4781 | 0 | 3.1141 | 586.4781 | 606.4881
DEER-SFAM-CZ04-V2-eSA-18-LH-s2 | 18 | CZ04 | V2 | CZ04-V2-eSA-18 | CZ04-V2-eSA-18-LH | 16.5228 | 1.9856 | 515.4491 | 0 | 3.1141 | 515.4491 | 548.3182
DEER-SFAM-CZ04-V2-eSA-18-LL-s2 | 18 | CZ04 | V2 | CZ04-V2-eSA-18 | CZ04-V2-eSA-18-LL | 16.9268 | 1.9818 | 500.2544 | 0 | 3.1141 | 500.2544 | 543.174
DEER-SFAM-CZ04-V2-eSA-18-TH-s2 | 18 | CZ04 | V2 | CZ04-V2-eSA-18 | CZ04-V2-eSA-18-TH | 17.8626 | 1.929 | 523.2467 | 0 | 3.1141 | 523.2467 | 549.308
DEER-SFAM-CZ04-V2-eSA-18-TL-s2 | 18 | CZ04 | V2 | CZ04-V2-eSA-18 | CZ04-V2-eSA-18-TL | 17.673 | 2.123 | 538.3629 | 0 | 3.1141 | 538.3629 | 567.0398
DEER-SFAM-CZ04-V2-eSA-18-TM-s2 | 18 | CZ04 | V2 | CZ04-V2-eSA-18 | CZ04-V2-eSA-18-TM | 17.5176 | 1.959 | 531.5886 | 0 | 3.1141 | 531.5886 | 558.2338
DEER-SFAM-CZ04-V2-eSH-10-HH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-HH | 10.2621 | 2.7072 | 739.6929 | 2007.033 | 3.1141 | 2746.7259 | 946.5453
DEER-SFAM-CZ04-V2-eSH-10-HL-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-HL | 10.1577 | 2.8694 | 758.5896 | 2025.1589 | 3.1141 | 2783.7485 | 962.4581
DEER-SFAM-CZ04-V2-eSH-10-HM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-HM | 10.3993 | 2.8452 | 754.3485 | 1967.0664 | 3.1141 | 2721.4149 | 949.8216
DEER-SFAM-CZ04-V2-eSH-10-LH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-LH | 10.4861 | 2.6379 | 737.4486 | 2108.1562 | 3.1141 | 2845.6049 | 950.9496
DEER-SFAM-CZ04-V2-eSH-10-LL-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-LL | 10.2992 | 2.8137 | 755.6506 | 2041.2841 | 3.1141 | 2796.9347 | 977.864
DEER-SFAM-CZ04-V2-eSH-10-LM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-LM | 10.281 | 2.7201 | 752.4256 | 2019.0399 | 3.1141 | 2771.4654 | 955.9032
DEER-SFAM-CZ04-V2-eSH-10-MH-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-MH | 10.6125 | 2.7124 | 731.1357 | 2084.8733 | 3.1141 | 2816.009 | 957.8763
DEER-SFAM-CZ04-V2-eSH-10-ML-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-ML | 10.3424 | 2.8618 | 749.4497 | 1920.5297 | 3.1141 | 2669.9795 | 954.73
DEER-SFAM-CZ04-V2-eSH-10-MM-s1 | 10 | CZ04 | V2 | CZ04-V2-eSH-10 | CZ04-V2-eSH-10-MM | 10.3653 | 2.9369 | 766.338 | 2028.1598 | 3.1141 | 2794.4979 | 958.1328
DEER-SFAM-CZ04-V2-eSH-13-HH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-HH | 13.1107 | 2.2973 | 581.9528 | 1928.8747 | 3.1141 | 2510.8275 | 770.7836
DEER-SFAM-CZ04-V2-eSH-13-HL-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-HL | 13.0837 | 2.2398 | 563.7462 | 1673.4803 | 3.1141 | 2237.2265 | 751.5237
DEER-SFAM-CZ04-V2-eSH-13-HM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-HM | 13.2474 | 2.3129 | 578.9307 | 1725.1118 | 3.1141 | 2304.0424 | 748.9832
DEER-SFAM-CZ04-V2-eSH-13-LH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-LH | 13.602 | 2.0643 | 560.0456 | 2020.7742 | 3.1141 | 2580.8198 | 844.8789
DEER-SFAM-CZ04-V2-eSH-13-LL-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-LL | 13.7792 | 2.1327 | 557.6044 | 1762.1079 | 3.1141 | 2319.7123 | 730.263
DEER-SFAM-CZ04-V2-eSH-13-LM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-LM | 13.2067 | 2.1789 | 580.0944 | 1542.0553 | 3.1141 | 2122.1497 | 775.9048
DEER-SFAM-CZ04-V2-eSH-13-MH-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-MH | 13.6571 | 2.0258 | 549.6025 | 1952.7817 | 3.1141 | 2502.3842 | 739.222
DEER-SFAM-CZ04-V2-eSH-13-ML-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-ML | 13.3251 | 2.2562 | 576.464 | 1807.039 | 3.1141 | 2383.503 | 770.703
DEER-SFAM-CZ04-V2-eSH-13-MM-s1 | 13 | CZ04 | V2 | CZ04-V2-eSH-13 | CZ04-V2-eSH-13-MM | 13.7709 | 2.1991 | 561.6264 | 1812.6558 | 3.1141 | 2374.2823 | 712.599
DEER-SFAM-CZ04-V2-eSH-14-HH-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-HH | 13.9364 | 2.1949 | 547.2919 | 1764.7166 | 3.1141 | 2312.0085 | 691.0056
DEER-SFAM-CZ04-V2-eSH-14-HL-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-HL | 14.1155 | 2.2192 | 538.8489 | 1737.2572 | 3.1141 | 2276.1061 | 711.7667
DEER-SFAM-CZ04-V2-eSH-14-HM-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-HM | 13.9358 | 2.1457 | 543.5667 | 1726.4397 | 3.1141 | 2270.0063 | 666.5654
DEER-SFAM-CZ04-V2-eSH-14-MH-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-MH | 14.4255 | 1.9387 | 525.2009 | 1837.4861 | 3.1141 | 2362.687 | 713.3081
DEER-SFAM-CZ04-V2-eSH-14-ML-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-ML | 14.8986 | 1.9734 | 511.6116 | 1915.4516 | 3.1141 | 2427.0632 | 748.0491
DEER-SFAM-CZ04-V2-eSH-14-MM-s1 | 14 | CZ04 | V2 | CZ04-V2-eSH-14 | CZ04-V2-eSH-14-MM | 14.4516 | 2.0042 | 521.5685 | 1691.1324 | 3.1141 | 2212.7008 | 684.1121
DEER-SFAM-CZ04-V2-eSH-15-HH-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-HH | 14.8137 | 1.9673 | 504.949 | 2031.4886 | 3.1141 | 2536.4376 | 639.6092
DEER-SFAM-CZ04-V2-eSH-15-HL-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-HL | 15.0736 | 2.0395 | 504.1853 | 1497.6719 | 3.1141 | 2001.8572 | 636.239
DEER-SFAM-CZ04-V2-eSH-15-HM-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-HM | 15.4809 | 1.8655 | 483.8234 | 1556.6507 | 3.1141 | 2040.4741 | 615.846
DEER-SFAM-CZ04-V2-eSH-15-MH-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-MH | 15.8892 | 1.877 | 480.3595 | 1786.7072 | 3.1141 | 2267.0667 | 608.6047
DEER-SFAM-CZ04-V2-eSH-15-ML-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-ML | 15.9048 | 1.8657 | 479.176 | 1681.8076 | 3.1141 | 2160.9837 | 612.2598
DEER-SFAM-CZ04-V2-eSH-15-MM-s1 | 15 | CZ04 | V2 | CZ04-V2-eSH-15 | CZ04-V2-eSH-15-MM | 15.6714 | 1.8793 | 483.5214 | 1787.2414 | 3.1141 | 2270.7629 | 624.3178
DEER-SFAM-CZ04-V2-eSH-16-CH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-CH | 16.0475 | 2.2635 | 581.0391 | 1908.5931 | 3.1141 | 2489.6322 | 704.5971
DEER-SFAM-CZ04-V2-eSH-16-CL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-CL | 16.2598 | 2.2897 | 573.8633 | 1769.6778 | 3.1141 | 2343.5411 | 701.3272
DEER-SFAM-CZ04-V2-eSH-16-LH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-LH | 14.8564 | 2.0473 | 559.7537 | 1998.1162 | 3.1141 | 2557.8699 | 695.9389
DEER-SFAM-CZ04-V2-eSH-16-LL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-LL | 14.9072 | 2.1943 | 568.1144 | 1817.2078 | 3.1141 | 2385.3222 | 677.2393
DEER-SFAM-CZ04-V2-eSH-16-LM-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-LM | 14.5081 | 2.1304 | 575.1682 | 2003.5613 | 3.1141 | 2578.7295 | 727.5182
DEER-SFAM-CZ04-V2-eSH-16-TH-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-TH | 16.1149 | 2.1541 | 576.0484 | 2425.712 | 3.1141 | 3001.7604 | 707.5587
DEER-SFAM-CZ04-V2-eSH-16-TL-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-TL | 15.9078 | 2.4588 | 611.513 | 2378.9274 | 3.1141 | 2990.4404 | 730.4149
DEER-SFAM-CZ04-V2-eSH-16-TM-s2 | 16 | CZ04 | V2 | CZ04-V2-eSH-16 | CZ04-V2-eSH-16-TM | 16.0502 | 2.4235 | 606.0873 | 2413.4293 | 3.1141 | 3019.5167 | 728.4249
DEER-SFAM-CZ04-V2-eSH-17-CM-s2 | 17 | CZ04 | V2 | CZ04-V2-eSH-17 | CZ04-V2-eSH-17-CM | 17.2422 | 2.1648 | 541.0541 | 1917.427 | 3.1141 | 2458.4811 | 680.1531
DEER-SFAM-CZ04-V2-eSH-17-LM-s2 | 17 | CZ04 | V2 | CZ04-V2-eSH-17 | CZ04-V2-eSH-17-LM | 15.825 | 2.104 | 539.5865 | 1760.5221 | 3.1141 | 2300.1086 | 600.8763
DEER-SFAM-CZ04-V2-eSH-17-TH-s2 | 17 | CZ04 | V2 | CZ04-V2-eSH-17 | CZ04-V2-eSH-17-TH | 17.3904 | 2.0325 | 535.3088 | 2421.1387 | 3.1141 | 2956.4475 | 677.1628
DEER-SFAM-CZ04-V2-eSH-17-TL-s2 | 17 | CZ04 | V2 | CZ04-V2-eSH-17 | CZ04-V2-eSH-17-TL | 17.2931 | 2.0692 | 537.3756 | 2402.5538 | 3.1141 | 2939.9294 | 677.3644
DEER-SFAM-CZ04-V2-eSH-18-LH-s2 | 18 | CZ04 | V2 | CZ04-V2-eSH-18 | CZ04-V2-eSH-18-LH | 16.9294 | 1.9637 | 503.4251 | 2069.2333 | 3.1141 | 2572.6584 | 606.1275
DEER-SFAM-CZ04-V2-eSH-18-LL-s2 | 18 | CZ04 | V2 | CZ04-V2-eSH-18 | CZ04-V2-eSH-18-LL | 16.3219 | 2.0191 | 515.0376 | 1827.6079 | 3.1141 | 2342.6455 | 609.5147
DEER-SFAM-CZ04-V2-eSH-18-LM-s2 | 18 | CZ04 | V2 | CZ04-V2-eSH-18 | CZ04-V2-eSH-18-LM | 16.7818 | 2.0147 | 509.3188 | 2191.5321 | 3.1141 | 2700.851 | 627.9116
DEER-SFAM-CZ04-V2-eSH-18-TM-s2 | 18 | CZ04 | V2 | CZ04-V2-eSH-18 | CZ04-V2-eSH-18-TM | 18.6291 | 1.972 | 504.2377 | 2415.7157 | 3.1141 | 2919.9535 | 712.7801
DEER-SFAM-CZ04-V3-eSA-10-HH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-HH | 10.4179 | 3.3988 | 1627.4604 | 0 | 3.4 | 1627.4604 | 1714.0488
DEER-SFAM-CZ04-V3-eSA-10-HL-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-HL | 10.2787 | 3.6526 | 1640.0695 | 0 | 3.4 | 1640.0695 | 1726.7274
DEER-SFAM-CZ04-V3-eSA-10-HM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-HM | 10.2426 | 3.455 | 1634.678 | 0 | 3.4 | 1634.678 | 1721.3232
DEER-SFAM-CZ04-V3-eSA-10-LH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-LH | 10.7208 | 3.2374 | 1552.7451 | 0 | 3.4 | 1552.7451 | 1639.4721
DEER-SFAM-CZ04-V3-eSA-10-LL-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-LL | 10.1547 | 3.6054 | 1653.5043 | 0 | 3.4 | 1653.5043 | 1740.178
DEER-SFAM-CZ04-V3-eSA-10-LM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-LM | 10.6226 | 3.3123 | 1573.2416 | 0 | 3.4 | 1573.2416 | 1659.9716
DEER-SFAM-CZ04-V3-eSA-10-MH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-MH | 10.6461 | 3.1803 | 1568.8915 | 0 | 3.4 | 1568.8915 | 1655.5941
DEER-SFAM-CZ04-V3-eSA-10-ML-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-ML | 10.2145 | 3.6488 | 1671.4684 | 0 | 3.4 | 1671.4684 | 1758.1279
DEER-SFAM-CZ04-V3-eSA-10-MM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSA-10 | CZ04-V3-eSA-10-MM | 10.8458 | 3.2862 | 1523.5617 | 0 | 3.4 | 1523.5617 | 1610.2286
DEER-SFAM-CZ04-V3-eSA-13-HH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-HH | 12.9586 | 2.7439 | 1253.6262 | 0 | 3.4 | 1253.6262 | 1331.7424
DEER-SFAM-CZ04-V3-eSA-13-HL-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-HL | 13.6053 | 2.7763 | 1210.0518 | 0 | 3.4 | 1210.0518 | 1278.4205
DEER-SFAM-CZ04-V3-eSA-13-HM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-HM | 13.2953 | 2.819 | 1242.0958 | 0 | 3.4 | 1242.0958 | 1320.1858
DEER-SFAM-CZ04-V3-eSA-13-LH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-LH | 13.6931 | 2.4816 | 1199.9969 | 0 | 3.4 | 1199.9969 | 1286.6753
DEER-SFAM-CZ04-V3-eSA-13-LL-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-LL | 13.4186 | 2.6883 | 1246.0791 | 0 | 3.4 | 1246.0791 | 1332.5941
DEER-SFAM-CZ04-V3-eSA-13-LM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-LM | 13.3702 | 2.5842 | 1243.138 | 0 | 3.4 | 1243.138 | 1329.748
DEER-SFAM-CZ04-V3-eSA-13-MH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-MH | 14.2502 | 2.5852 | 1182.013 | 0 | 3.4 | 1182.013 | 1268.659
DEER-SFAM-CZ04-V3-eSA-13-ML-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-ML | 13.3383 | 2.7628 | 1223.6301 | 0 | 3.4 | 1223.6301 | 1310.0088
DEER-SFAM-CZ04-V3-eSA-13-MM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSA-13 | CZ04-V3-eSA-13-MM | 14.1839 | 2.6641 | 1183.5506 | 0 | 3.4 | 1183.5506 | 1270.1841
DEER-SFAM-CZ04-V3-eSA-14-HH-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-HH | 13.7549 | 2.6449 | 1186.1135 | 0 | 3.4 | 1186.1135 | 1258.734
DEER-SFAM-CZ04-V3-eSA-14-HL-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-HL | 14.6296 | 2.5539 | 1129.1526 | 0 | 3.4 | 1129.1526 | 1182.5558
DEER-SFAM-CZ04-V3-eSA-14-HM-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-HM | 14.586 | 2.572 | 1128.6186 | 0 | 3.4 | 1128.6186 | 1210.5458
DEER-SFAM-CZ04-V3-eSA-14-MH-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-MH | 14.2118 | 2.4072 | 1183.5521 | 0 | 3.4 | 1183.5521 | 1240.4865
DEER-SFAM-CZ04-V3-eSA-14-ML-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-ML | 14.2751 | 2.5255 | 1140.2222 | 0 | 3.4 | 1140.2222 | 1231.1442
DEER-SFAM-CZ04-V3-eSA-14-MM-s1 | 14 | CZ04 | V3 | CZ04-V3-eSA-14 | CZ04-V3-eSA-14-MM | 14.3433 | 2.4051 | 1152.0378 | 0 | 3.4 | 1152.0378 | 1214.4569
DEER-SFAM-CZ04-V3-eSA-15-HH-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-HH | 15.4357 | 2.3965 | 1061.5683 | 0 | 3.4 | 1061.5683 | 1122.1103
DEER-SFAM-CZ04-V3-eSA-15-HL-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-HL | 15.8617 | 2.3678 | 1038.1916 | 0 | 3.4 | 1038.1916 | 1113.6445
DEER-SFAM-CZ04-V3-eSA-15-HM-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-HM | 15.2274 | 2.3822 | 1072.6555 | 0 | 3.4 | 1072.6555 | 1133.4214
DEER-SFAM-CZ04-V3-eSA-15-MH-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-MH | 15.4848 | 2.3573 | 1054.7876 | 0 | 3.4 | 1054.7876 | 1099.9014
DEER-SFAM-CZ04-V3-eSA-15-ML-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-ML | 15.6606 | 2.3789 | 1070.1463 | 0 | 3.4 | 1070.1463 | 1130.812
DEER-SFAM-CZ04-V3-eSA-15-MM-s1 | 15 | CZ04 | V3 | CZ04-V3-eSA-15 | CZ04-V3-eSA-15-MM | 15.5285 | 2.3519 | 1056.3576 | 0 | 3.4 | 1056.3576 | 1111.6748
DEER-SFAM-CZ04-V3-eSA-16-CH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-CH | 15.6542 | 2.6724 | 1205.2739 | 0 | 3.4 | 1205.2739 | 1240.1276
DEER-SFAM-CZ04-V3-eSA-16-CL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-CL | 16.1233 | 2.6759 | 1149.6336 | 0 | 3.4 | 1149.6336 | 1193.7082
DEER-SFAM-CZ04-V3-eSA-16-CM-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-CM | 15.7935 | 2.6828 | 1177.3371 | 0 | 3.4 | 1177.3371 | 1223.7907
DEER-SFAM-CZ04-V3-eSA-16-LH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-LH | 15.7386 | 2.4556 | 1110.7916 | 0 | 3.4 | 1110.7916 | 1170.7607
DEER-SFAM-CZ04-V3-eSA-16-LL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-LL | 15.1826 | 2.6004 | 1158.7102 | 0 | 3.4 | 1158.7102 | 1198.0393
DEER-SFAM-CZ04-V3-eSA-16-LM-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-LM | 15.2483 | 2.5354 | 1155.3218 | 0 | 3.4 | 1155.3218 | 1190.9661
DEER-SFAM-CZ04-V3-eSA-16-NM-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-NM | 16.5786 | 2.3361 | 1087.9595 | 0 | 3.4 | 1087.9595 | 1122.9685
DEER-SFAM-CZ04-V3-eSA-16-TH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-TH | 16.1434 | 2.7224 | 1191.1112 | 0 | 3.4 | 1191.1112 | 1213.5344
DEER-SFAM-CZ04-V3-eSA-16-TL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSA-16 | CZ04-V3-eSA-16-TL | 16.6787 | 2.686 | 1148.9321 | 0 | 3.4 | 1148.9321 | 1173.1131
DEER-SFAM-CZ04-V3-eSA-17-CH-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-CH | 16.7552 | 2.5143 | 1112.3514 | 0 | 3.4 | 1112.3514 | 1156.4024
DEER-SFAM-CZ04-V3-eSA-17-CL-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-CL | 16.7246 | 2.5542 | 1114.512 | 0 | 3.4 | 1114.512 | 1158.553
DEER-SFAM-CZ04-V3-eSA-17-CM-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-CM | 16.8103 | 2.5492 | 1121.159 | 0 | 3.4 | 1121.159 | 1155.9106
DEER-SFAM-CZ04-V3-eSA-17-LH-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-LH | 16.3388 | 2.3773 | 1064.2874 | 0 | 3.4 | 1064.2874 | 1111.2789
DEER-SFAM-CZ04-V3-eSA-17-LL-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-LL | 16.1253 | 2.485 | 1102.162 | 0 | 3.4 | 1102.162 | 1127.6912
DEER-SFAM-CZ04-V3-eSA-17-LM-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-LM | 15.9183 | 2.4507 | 1110.4221 | 0 | 3.4 | 1110.4221 | 1132.4787
DEER-SFAM-CZ04-V3-eSA-17-TH-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-TH | 18.3492 | 2.3376 | 1026.998 | 0 | 3.4 | 1026.998 | 1062.8591
DEER-SFAM-CZ04-V3-eSA-17-TL-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-TL | 18.7166 | 2.3385 | 993.4177 | 0 | 3.4 | 993.4177 | 1049.3094
DEER-SFAM-CZ04-V3-eSA-17-TM-s2 | 17 | CZ04 | V3 | CZ04-V3-eSA-17 | CZ04-V3-eSA-17-TM | 17.8999 | 2.5307 | 1111.3567 | 0 | 3.4 | 1111.3567 | 1130.053
DEER-SFAM-CZ04-V3-eSA-18-LH-s2 | 18 | CZ04 | V3 | CZ04-V3-eSA-18 | CZ04-V3-eSA-18-LH | 17.0914 | 2.3022 | 1033.849 | 0 | 3.4 | 1033.849 | 1064.5863
DEER-SFAM-CZ04-V3-eSA-18-LL-s2 | 18 | CZ04 | V3 | CZ04-V3-eSA-18 | CZ04-V3-eSA-18-LL | 17.3844 | 2.3047 | 1010.9942 | 0 | 3.4 | 1010.9942 | 1051.1392
DEER-SFAM-CZ04-V3-eSA-18-TH-s2 | 18 | CZ04 | V3 | CZ04-V3-eSA-18 | CZ04-V3-eSA-18-TH | 18.9378 | 2.2254 | 997.2829 | 0 | 3.4 | 997.2829 | 1021.6306
DEER-SFAM-CZ04-V3-eSA-18-TL-s2 | 18 | CZ04 | V3 | CZ04-V3-eSA-18 | CZ04-V3-eSA-18-TL | 18.4398 | 2.4275 | 1033.3326 | 0 | 3.4 | 1033.3326 | 1060.0864
DEER-SFAM-CZ04-V3-eSA-18-TM-s2 | 18 | CZ04 | V3 | CZ04-V3-eSA-18 | CZ04-V3-eSA-18-TM | 18.2848 | 2.2785 | 1028.5211 | 0 | 3.4 | 1028.5211 | 1053.4179
DEER-SFAM-CZ04-V3-eSH-10-HH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-HH | 10.4659 | 3.2814 | 1574.6736 | 1808.9596 | 3.4 | 3383.6332 | 1759.2332
DEER-SFAM-CZ04-V3-eSH-10-HL-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-HL | 10.2607 | 3.429 | 1625.4672 | 1826.1936 | 3.4 | 3451.6609 | 1807.5109
DEER-SFAM-CZ04-V3-eSH-10-HM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-HM | 10.6297 | 3.388 | 1591.9845 | 1796.9931 | 3.4 | 3388.9776 | 1766.1776
DEER-SFAM-CZ04-V3-eSH-10-LH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-LH | 10.6611 | 3.1173 | 1567.147 | 1892.9081 | 3.4 | 3460.055 | 1757.505
DEER-SFAM-CZ04-V3-eSH-10-LL-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-LL | 10.4772 | 3.3479 | 1608.7659 | 1833.5816 | 3.4 | 3442.3475 | 1806.7475
DEER-SFAM-CZ04-V3-eSH-10-LM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-LM | 10.5467 | 3.2635 | 1592.6967 | 1821.064 | 3.4 | 3413.7607 | 1774.7607
DEER-SFAM-CZ04-V3-eSH-10-MH-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-MH | 10.73 | 3.2119 | 1560.335 | 1869.1874 | 3.4 | 3429.5225 | 1762.2225
DEER-SFAM-CZ04-V3-eSH-10-ML-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-ML | 10.4699 | 3.5023 | 1608.0745 | 1735.0096 | 3.4 | 3343.0841 | 1791.6841
DEER-SFAM-CZ04-V3-eSH-10-MM-s1 | 10 | CZ04 | V3 | CZ04-V3-eSH-10 | CZ04-V3-eSH-10-MM | 10.5599 | 3.3872 | 1609.8196 | 1829.2789 | 3.4 | 3439.0986 | 1781.7486
DEER-SFAM-CZ04-V3-eSH-13-HH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-HH | 13.3008 | 2.754 | 1247.7678 | 1744.9886 | 3.4 | 2992.7564 | 1416.2565
DEER-SFAM-CZ04-V3-eSH-13-HL-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-HL | 13.1797 | 2.8005 | 1228.452 | 1512.3383 | 3.4 | 2740.7903 | 1396.0902
DEER-SFAM-CZ04-V3-eSH-13-HM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-HM | 13.4264 | 2.7654 | 1240.8582 | 1565.4198 | 3.4 | 2806.278 | 1393.078
DEER-SFAM-CZ04-V3-eSH-13-LH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-LH | 13.6563 | 2.4926 | 1205.7671 | 1778.8759 | 3.4 | 2984.6431 | 1456.593
DEER-SFAM-CZ04-V3-eSH-13-LL-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-LL | 14.1595 | 2.6164 | 1179.6956 | 1582.576 | 3.4 | 2762.2716 | 1333.7216
DEER-SFAM-CZ04-V3-eSH-13-LM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-LM | 13.1977 | 2.6298 | 1253.882 | 1387.3876 | 3.4 | 2641.2696 | 1429.1696
DEER-SFAM-CZ04-V3-eSH-13-MH-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-MH | 14.1401 | 2.5312 | 1164.0856 | 1751.8983 | 3.4 | 2915.9839 | 1332.734
DEER-SFAM-CZ04-V3-eSH-13-ML-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-ML | 13.3156 | 2.7433 | 1246.2264 | 1609.5124 | 3.4 | 2855.7388 | 1419.1388
DEER-SFAM-CZ04-V3-eSH-13-MM-s1 | 13 | CZ04 | V3 | CZ04-V3-eSH-13 | CZ04-V3-eSH-13-MM | 13.9378 | 2.6917 | 1200.9071 | 1642.1102 | 3.4 | 2843.0173 | 1336.4173
DEER-SFAM-CZ04-V3-eSH-14-HH-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-HH | 14.0773 | 2.636 | 1178.6641 | 1599.3914 | 3.4 | 2778.0554 | 1307.0555
DEER-SFAM-CZ04-V3-eSH-14-HL-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-HL | 14.1372 | 2.6656 | 1171.6076 | 1566.9227 | 3.4 | 2738.5303 | 1325.3803
DEER-SFAM-CZ04-V3-eSH-14-HM-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-HM | 14.0319 | 2.572 | 1175.9911 | 1558.1444 | 3.4 | 2734.1355 | 1285.7855
DEER-SFAM-CZ04-V3-eSH-14-MH-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-MH | 14.4625 | 2.3346 | 1134.1753 | 1628.0904 | 3.4 | 2762.2657 | 1300.9157
DEER-SFAM-CZ04-V3-eSH-14-ML-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-ML | 14.8071 | 2.4718 | 1104.1811 | 1668.5538 | 3.4 | 2772.7349 | 1311.3349
DEER-SFAM-CZ04-V3-eSH-14-MM-s1 | 14 | CZ04 | V3 | CZ04-V3-eSH-14 | CZ04-V3-eSH-14-MM | 14.2796 | 2.4644 | 1141.4137 | 1512.8194 | 3.4 | 2654.2331 | 1285.9831
DEER-SFAM-CZ04-V3-eSH-15-HH-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-HH | 15.082 | 2.3607 | 1083.8155 | 1787.4957 | 3.4 | 2871.3111 | 1202.4111
DEER-SFAM-CZ04-V3-eSH-15-HL-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-HL | 15.1578 | 2.4754 | 1092.2989 | 1361.0645 | 3.4 | 2453.3634 | 1210.4134
DEER-SFAM-CZ04-V3-eSH-15-HM-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-HM | 15.7395 | 2.3409 | 1043.9035 | 1426.2818 | 3.4 | 2470.1852 | 1161.1852
DEER-SFAM-CZ04-V3-eSH-15-MH-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-MH | 15.9199 | 2.3426 | 1032.0999 | 1568.5044 | 3.4 | 2600.6043 | 1144.9543
DEER-SFAM-CZ04-V3-eSH-15-ML-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-ML | 15.7794 | 2.3533 | 1039.4078 | 1479.3264 | 3.4 | 2518.7341 | 1156.6341
DEER-SFAM-CZ04-V3-eSH-15-MM-s1 | 15 | CZ04 | V3 | CZ04-V3-eSH-15 | CZ04-V3-eSH-15-MM | 15.9701 | 2.3588 | 1036.3968 | 1598.5553 | 3.4 | 2634.952 | 1161.652
DEER-SFAM-CZ04-V3-eSH-16-CH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-CH | 16.0274 | 2.6257 | 1175.7916 | 1567.9738 | 3.4 | 2743.7654 | 1281.0153
DEER-SFAM-CZ04-V3-eSH-16-CL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-CL | 16.1225 | 2.6574 | 1170.1166 | 1467.6451 | 3.4 | 2637.7617 | 1279.5617
DEER-SFAM-CZ04-V3-eSH-16-LH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-LH | 15.7132 | 2.3929 | 1105.3058 | 1672.6509 | 3.4 | 2777.9567 | 1224.0567
DEER-SFAM-CZ04-V3-eSH-16-LL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-LL | 15.219 | 2.5827 | 1158.6842 | 1526.1059 | 3.4 | 2684.7901 | 1254.1901
DEER-SFAM-CZ04-V3-eSH-16-LM-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-LM | 15.1461 | 2.4918 | 1153.8936 | 1671.2791 | 3.4 | 2825.1727 | 1286.5727
DEER-SFAM-CZ04-V3-eSH-16-TH-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-TH | 17.1762 | 2.5321 | 1096.2994 | 1932.6645 | 3.4 | 3028.9639 | 1202.8139
DEER-SFAM-CZ04-V3-eSH-16-TL-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-TL | 16.1791 | 2.8035 | 1192.2722 | 1890.7731 | 3.4 | 3083.0453 | 1289.3453
DEER-SFAM-CZ04-V3-eSH-16-TM-s2 | 16 | CZ04 | V3 | CZ04-V3-eSH-16 | CZ04-V3-eSH-16-TM | 16.3402 | 2.7597 | 1180.5206 | 1920.2772 | 3.4 | 3100.7978 | 1280.2478
DEER-SFAM-CZ04-V3-eSH-17-CM-s2 | 17 | CZ04 | V3 | CZ04-V3-eSH-17 | CZ04-V3-eSH-17-CM | 17.0769 | 2.516 | 1104.1337 | 1549.4251 | 3.4 | 2653.5588 | 1221.0088
DEER-SFAM-CZ04-V3-eSH-17-LM-s2 | 17 | CZ04 | V3 | CZ04-V3-eSH-17 | CZ04-V3-eSH-17-LM | 16.2732 | 2.4249 | 1093.389 | 1482.3945 | 3.4 | 2575.7834 | 1147.0834
DEER-SFAM-CZ04-V3-eSH-17-TH-s2 | 17 | CZ04 | V3 | CZ04-V3-eSH-17 | CZ04-V3-eSH-17-TH | 18.2199 | 2.3697 | 1034.2135 | 1925.352 | 3.4 | 2959.5656 | 1148.9156
DEER-SFAM-CZ04-V3-eSH-17-TL-s2 | 17 | CZ04 | V3 | CZ04-V3-eSH-17 | CZ04-V3-eSH-17-TL | 18.0904 | 2.427 | 1040.8658 | 1903.3133 | 3.4 | 2944.1791 | 1153.8791
DEER-SFAM-CZ04-V3-eSH-18-LH-s2 | 18 | CZ04 | V3 | CZ04-V3-eSH-18 | CZ04-V3-eSH-18-LH | 17.3523 | 2.2997 | 1014.6698 | 1668.9827 | 3.4 | 2683.6526 | 1102.2026
DEER-SFAM-CZ04-V3-eSH-18-LL-s2 | 18 | CZ04 | V3 | CZ04-V3-eSH-18 | CZ04-V3-eSH-18-LL | 16.5942 | 2.3733 | 1055.0191 | 1520.8972 | 3.4 | 2575.9163 | 1137.3663
DEER-SFAM-CZ04-V3-eSH-18-LM-s2 | 18 | CZ04 | V3 | CZ04-V3-eSH-18 | CZ04-V3-eSH-18-LM | 17.2741 | 2.3456 | 1024.2617 | 1750.0153 | 3.4 | 2774.277 | 1124.277
DEER-SFAM-CZ04-V3-eSH-18-TM-s2 | 18 | CZ04 | V3 | CZ04-V3-eSH-18 | CZ04-V3-eSH-18-TM | 19.5564 | 2.3304 | 969.6635 | 1885.3656 | 3.4 | 2855.0291 | 1137.6791
DEER-SFAM-CZ04-V4-eSA-10-HH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-HH | 10.429 | 3.4013 | 1603.0849 | 0 | 3.4 | 1603.0849 | 1677.5211
DEER-SFAM-CZ04-V4-eSA-10-HL-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-HL | 10.3036 | 3.6463 | 1610.677 | 0 | 3.4 | 1610.677 | 1685.1735
DEER-SFAM-CZ04-V4-eSA-10-HM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-HM | 10.2659 | 3.4487 | 1605.0106 | 0 | 3.4 | 1605.0106 | 1679.496
DEER-SFAM-CZ04-V4-eSA-10-LH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-LH | 10.7363 | 3.2377 | 1521.5563 | 0 | 3.4 | 1521.5563 | 1596.1124
DEER-SFAM-CZ04-V4-eSA-10-LL-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-LL | 10.1074 | 3.8874 | 1639.0789 | 0 | 3.9 | 1639.0789 | 1713.666
DEER-SFAM-CZ04-V4-eSA-10-LM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-LM | 10.6354 | 3.3133 | 1542.3611 | 0 | 3.4 | 1542.3611 | 1616.9201
DEER-SFAM-CZ04-V4-eSA-10-MH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-MH | 10.6558 | 3.1806 | 1538.5384 | 0 | 3.4 | 1538.5384 | 1613.0745
DEER-SFAM-CZ04-V4-eSA-10-ML-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-ML | 10.2321 | 3.6429 | 1640.1655 | 0 | 3.4 | 1640.1655 | 1714.6636
DEER-SFAM-CZ04-V4-eSA-10-MM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSA-10 | CZ04-V4-eSA-10-MM | 10.856 | 3.2858 | 1494.902 | 0 | 3.4 | 1494.902 | 1569.4062
DEER-SFAM-CZ04-V4-eSA-13-HH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-HH | 12.8311 | 2.9579 | 1246.5406 | 0 | 3.9 | 1246.5406 | 1313.7647
DEER-SFAM-CZ04-V4-eSA-13-HL-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-HL | 13.567 | 2.8855 | 1197.4971 | 0 | 3.9 | 1197.4971 | 1256.3338
DEER-SFAM-CZ04-V4-eSA-13-HM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-HM | 13.222 | 3.0184 | 1230.1267 | 0 | 3.9 | 1230.1267 | 1297.3308
DEER-SFAM-CZ04-V4-eSA-13-LH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-LH | 13.7093 | 2.4819 | 1173.6934 | 0 | 3.4 | 1173.6934 | 1248.2084
DEER-SFAM-CZ04-V4-eSA-13-LL-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-LL | 13.4371 | 2.6889 | 1225.5435 | 0 | 3.4 | 1225.5435 | 1299.9143
DEER-SFAM-CZ04-V4-eSA-13-LM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-LM | 13.3856 | 2.5852 | 1216.6028 | 0 | 3.4 | 1216.6028 | 1291.0572
DEER-SFAM-CZ04-V4-eSA-13-MH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-MH | 14.2729 | 2.5819 | 1158.4604 | 0 | 3.4 | 1158.4604 | 1232.9463
DEER-SFAM-CZ04-V4-eSA-13-ML-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-ML | 13.3552 | 2.7636 | 1199.5023 | 0 | 3.4 | 1199.5023 | 1273.7579
DEER-SFAM-CZ04-V4-eSA-13-MM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSA-13 | CZ04-V4-eSA-13-MM | 14.0933 | 2.864 | 1174.1594 | 0 | 3.9 | 1174.1594 | 1248.7164
DEER-SFAM-CZ04-V4-eSA-14-HH-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-HH | 13.7785 | 2.6431 | 1162.115 | 0 | 3.4 | 1162.115 | 1224.5436
DEER-SFAM-CZ04-V4-eSA-14-HL-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-HL | 14.5572 | 2.6573 | 1119.6539 | 0 | 3.9 | 1119.6539 | 1165.6128
DEER-SFAM-CZ04-V4-eSA-14-HM-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-HM | 14.6198 | 2.5657 | 1104.9159 | 0 | 3.4 | 1104.9159 | 1175.3464
DEER-SFAM-CZ04-V4-eSA-14-MH-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-MH | 14.2281 | 2.4078 | 1162.9122 | 0 | 3.4 | 1162.9122 | 1211.8559
DEER-SFAM-CZ04-V4-eSA-14-ML-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-ML | 14.3002 | 2.525 | 1117.0824 | 0 | 3.4 | 1117.0824 | 1195.2443
DEER-SFAM-CZ04-V4-eSA-14-MM-s1 | 14 | CZ04 | V4 | CZ04-V4-eSA-14 | CZ04-V4-eSA-14-MM | 14.3661 | 2.4053 | 1126.8665 | 0 | 3.4 | 1126.8665 | 1180.5255
DEER-SFAM-CZ04-V4-eSA-15-HH-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-HH | 15.286 | 2.5675 | 1055.9887 | 0 | 3.9 | 1055.9887 | 1108.0896
DEER-SFAM-CZ04-V4-eSA-15-HL-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-HL | 15.7647 | 2.475 | 1029.8382 | 0 | 3.9 | 1029.8382 | 1094.7755
DEER-SFAM-CZ04-V4-eSA-15-HM-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-HM | 15.0984 | 2.5378 | 1065.472 | 0 | 3.9 | 1065.472 | 1117.7667
DEER-SFAM-CZ04-V4-eSA-15-MH-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-MH | 15.512 | 2.351 | 1033.6321 | 0 | 3.4 | 1033.6321 | 1072.4151
DEER-SFAM-CZ04-V4-eSA-15-ML-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-ML | 15.6864 | 2.379 | 1048.6185 | 0 | 3.4 | 1048.6185 | 1100.7682
DEER-SFAM-CZ04-V4-eSA-15-MM-s1 | 15 | CZ04 | V4 | CZ04-V4-eSA-15 | CZ04-V4-eSA-15-MM | 15.5554 | 2.3451 | 1036.9497 | 0 | 3.4 | 1036.9497 | 1084.5038
DEER-SFAM-CZ04-V4-eSA-16-CH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-CH | 15.7413 | 2.8918 | 1192.3933 | 0 | 3.9 | 1192.3933 | 1222.4313
DEER-SFAM-CZ04-V4-eSA-16-CL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-CL | 16.1973 | 2.8538 | 1136.1472 | 0 | 3.9 | 1136.1472 | 1174.1199
DEER-SFAM-CZ04-V4-eSA-16-CM-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-CM | 15.8471 | 2.8818 | 1166.467 | 0 | 3.9 | 1166.467 | 1206.4941
DEER-SFAM-CZ04-V4-eSA-16-LH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-LH | 15.7466 | 2.4575 | 1093.1627 | 0 | 3.4 | 1093.1627 | 1144.734
DEER-SFAM-CZ04-V4-eSA-16-LL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-LL | 15.1921 | 2.601 | 1141.6185 | 0 | 3.4 | 1141.6185 | 1175.4372
DEER-SFAM-CZ04-V4-eSA-16-LM-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-LM | 15.2637 | 2.5364 | 1136.8318 | 0 | 3.4 | 1136.8318 | 1167.4814
DEER-SFAM-CZ04-V4-eSA-16-NM-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-NM | 16.603 | 2.3335 | 1064.4822 | 0 | 3.4 | 1064.4822 | 1094.5879
DEER-SFAM-CZ04-V4-eSA-16-TH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-TH | 16.1889 | 2.7241 | 1172.7263 | 0 | 3.4 | 1172.7263 | 1192.017
DEER-SFAM-CZ04-V4-eSA-16-TL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSA-16 | CZ04-V4-eSA-16-TL | 16.7398 | 2.8733 | 1138.1968 | 0 | 3.9 | 1138.1968 | 1159.0276
DEER-SFAM-CZ04-V4-eSA-17-CH-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-CH | 16.8406 | 2.7138 | 1099.0247 | 0 | 3.9 | 1099.0247 | 1136.9841
DEER-SFAM-CZ04-V4-eSA-17-CL-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-CL | 16.845 | 2.751 | 1098.9374 | 0 | 3.9 | 1098.9374 | 1136.8876
DEER-SFAM-CZ04-V4-eSA-17-CM-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-CM | 16.928 | 2.7493 | 1108.8095 | 0 | 3.9 | 1108.8095 | 1138.7585
DEER-SFAM-CZ04-V4-eSA-17-LH-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-LH | 16.3518 | 2.3788 | 1047.5133 | 0 | 3.4 | 1047.5133 | 1087.9237
DEER-SFAM-CZ04-V4-eSA-17-LL-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-LL | 16.1471 | 2.4851 | 1083.715 | 0 | 3.4 | 1083.715 | 1105.6628
DEER-SFAM-CZ04-V4-eSA-17-LM-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-LM | 15.943 | 2.4505 | 1093.018 | 0 | 3.4 | 1093.018 | 1111.983
DEER-SFAM-CZ04-V4-eSA-17-TH-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-TH | 18.397 | 2.3371 | 1008.1207 | 0 | 3.4 | 1008.1207 | 1038.9685
DEER-SFAM-CZ04-V4-eSA-17-TL-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-TL | 18.7476 | 2.3325 | 972.0875 | 0 | 3.4 | 972.0875 | 1020.1755
DEER-SFAM-CZ04-V4-eSA-17-TM-s2 | 17 | CZ04 | V4 | CZ04-V4-eSA-17 | CZ04-V4-eSA-17-TM | 17.896 | 2.7329 | 1103.0238 | 0 | 3.9 | 1103.0238 | 1119.1255
DEER-SFAM-CZ04-V4-eSA-18-LH-s2 | 18 | CZ04 | V4 | CZ04-V4-eSA-18 | CZ04-V4-eSA-18-LH | 17.1189 | 2.3037 | 1017.8454 | 0 | 3.4 | 1017.8454 | 1044.2757
DEER-SFAM-CZ04-V4-eSA-18-LL-s2 | 18 | CZ04 | V4 | CZ04-V4-eSA-18 | CZ04-V4-eSA-18-LL | 17.4043 | 2.3064 | 993.8029 | 0 | 3.4 | 993.8029 | 1028.3242
DEER-SFAM-CZ04-V4-eSA-18-TH-s2 | 18 | CZ04 | V4 | CZ04-V4-eSA-18 | CZ04-V4-eSA-18-TH | 18.7227 | 2.4017 | 1001.3423 | 0 | 3.9 | 1001.3423 | 1022.3153
DEER-SFAM-CZ04-V4-eSA-18-TL-s2 | 18 | CZ04 | V4 | CZ04-V4-eSA-18 | CZ04-V4-eSA-18-TL | 18.4769 | 2.4282 | 1015.6475 | 0 | 3.4 | 1015.6475 | 1038.6631
DEER-SFAM-CZ04-V4-eSA-18-TM-s2 | 18 | CZ04 | V4 | CZ04-V4-eSA-18 | CZ04-V4-eSA-18-TM | 18.3197 | 2.2786 | 1009.6341 | 0 | 3.4 | 1009.6341 | 1031.0494
DEER-SFAM-CZ04-V4-eSH-10-HH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-HH | 10.3221 | 3.4926 | 1574.61 | 1584.3038 | 3.9 | 3158.9138 | 1734.4137
DEER-SFAM-CZ04-V4-eSH-10-HL-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-HL | 10.1664 | 3.6671 | 1616.159 | 1593.3357 | 3.9 | 3209.4947 | 1773.6447
DEER-SFAM-CZ04-V4-eSH-10-HM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-HM | 10.6392 | 3.3851 | 1561.8138 | 1558.8756 | 3.4 | 3120.6894 | 1712.3894
DEER-SFAM-CZ04-V4-eSH-10-LH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-LH | 10.6655 | 3.1181 | 1539.5273 | 1642.3403 | 3.4 | 3181.8676 | 1704.1176
DEER-SFAM-CZ04-V4-eSH-10-LL-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-LL | 10.4728 | 3.3558 | 1579.1124 | 1592.0238 | 3.4 | 3171.1361 | 1750.3861
DEER-SFAM-CZ04-V4-eSH-10-LM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-LM | 10.5537 | 3.2675 | 1559.2729 | 1581.8464 | 3.4 | 3141.1193 | 1716.7693
DEER-SFAM-CZ04-V4-eSH-10-MH-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-MH | 10.7407 | 3.2142 | 1527.394 | 1621.3575 | 3.4 | 3148.7515 | 1701.9515
DEER-SFAM-CZ04-V4-eSH-10-ML-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-ML | 10.4796 | 3.5046 | 1576.502 | 1506.0437 | 3.4 | 3082.5456 | 1735.4456
DEER-SFAM-CZ04-V4-eSH-10-MM-s1 | 10 | CZ04 | V4 | CZ04-V4-eSH-10 | CZ04-V4-eSH-10-MM | 10.5689 | 3.393 | 1585.4571 | 1585.9476 | 3.4 | 3171.4048 | 1734.1047
DEER-SFAM-CZ04-V4-eSH-13-HH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-HH | 13.1547 | 2.9765 | 1241.289 | 1525.1916 | 3.9 | 2766.4806 | 1387.2305
DEER-SFAM-CZ04-V4-eSH-13-HL-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-HL | 13.1162 | 2.9625 | 1217.3599 | 1314.3735 | 3.9 | 2531.7333 | 1362.5333
DEER-SFAM-CZ04-V4-eSH-13-HM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-HM | 13.3106 | 2.9846 | 1231.5131 | 1366.3898 | 3.9 | 2597.903 | 1363.3529
DEER-SFAM-CZ04-V4-eSH-13-LH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-LH | 13.676 | 2.4915 | 1179.5298 | 1542.0183 | 3.4 | 2721.5481 | 1396.4481
DEER-SFAM-CZ04-V4-eSH-13-LL-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-LL | 14.1664 | 2.6109 | 1158.6498 | 1371.6554 | 3.4 | 2530.3052 | 1291.9052
DEER-SFAM-CZ04-V4-eSH-13-LM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-LM | 13.2106 | 2.6295 | 1227.2901 | 1202.1901 | 3.4 | 2429.4801 | 1378.7802
DEER-SFAM-CZ04-V4-eSH-13-MH-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-MH | 13.925 | 2.694 | 1165.0539 | 1536.85 | 3.9 | 2701.9039 | 1311.0539
DEER-SFAM-CZ04-V4-eSH-13-ML-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-ML | 13.3401 | 2.742 | 1220.9702 | 1392.8584 | 3.4 | 2613.8286 | 1370.4286
DEER-SFAM-CZ04-V4-eSH-13-MM-s1 | 13 | CZ04 | V4 | CZ04-V4-eSH-13 | CZ04-V4-eSH-13-MM | 13.9623 | 2.6921 | 1176.4712 | 1423.8483 | 3.4 | 2600.3195 | 1293.5695
DEER-SFAM-CZ04-V4-eSH-14-HH-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-HH | 13.9599 | 2.8413 | 1171.738 | 1395.051 | 3.9 | 2566.789 | 1282.939
DEER-SFAM-CZ04-V4-eSH-14-HL-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-HL | 14.0905 | 2.8617 | 1158.8633 | 1357.768 | 3.9 | 2516.6313 | 1292.0313
DEER-SFAM-CZ04-V4-eSH-14-HM-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-HM | 13.9215 | 2.7602 | 1168.0715 | 1357.8718 | 3.9 | 2525.9433 | 1263.1933
DEER-SFAM-CZ04-V4-eSH-14-MH-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-MH | 14.4802 | 2.3347 | 1109.2266 | 1411.9718 | 3.4 | 2521.1984 | 1253.4984
DEER-SFAM-CZ04-V4-eSH-14-ML-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-ML | 14.7491 | 2.5559 | 1094.039 | 1438.3108 | 3.9 | 2532.3497 | 1273.5497
DEER-SFAM-CZ04-V4-eSH-14-MM-s1 | 14 | CZ04 | V4 | CZ04-V4-eSH-14 | CZ04-V4-eSH-14-MM | 14.3072 | 2.4634 | 1115.8869 | 1311.4865 | 3.4 | 2427.3733 | 1240.8734
DEER-SFAM-CZ04-V4-eSH-15-HH-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-HH | 14.9235 | 2.5285 | 1078.4241 | 1539.5678 | 3.9 | 2617.9918 | 1181.2919
DEER-SFAM-CZ04-V4-eSH-15-HL-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-HL | 15.0743 | 2.6612 | 1082.1834 | 1184.1527 | 3.9 | 2266.3362 | 1184.4361
DEER-SFAM-CZ04-V4-eSH-15-HM-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-HM | 15.6238 | 2.4623 | 1036.6083 | 1241.5721 | 3.9 | 2278.1804 | 1138.1304
DEER-SFAM-CZ04-V4-eSH-15-MH-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-MH | 15.9571 | 2.3356 | 1010.5755 | 1357.6687 | 3.4 | 2368.2441 | 1108.1442
DEER-SFAM-CZ04-V4-eSH-15-ML-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-ML | 15.7308 | 2.4291 | 1027.7909 | 1279.745 | 3.9 | 2307.5359 | 1129.3359
DEER-SFAM-CZ04-V4-eSH-15-MM-s1 | 15 | CZ04 | V4 | CZ04-V4-eSH-15 | CZ04-V4-eSH-15-MM | 15.8722 | 2.4661 | 1029.0848 | 1384.9064 | 3.9 | 2413.9913 | 1137.6413
DEER-SFAM-CZ04-V4-eSH-16-CH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-CH | 16.065 | 2.8257 | 1166.5015 | 1351.7887 | 3.9 | 2518.2902 | 1254.0902
DEER-SFAM-CZ04-V4-eSH-16-CL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-CL | 16.2089 | 2.8714 | 1157.7437 | 1263.3934 | 3.9 | 2421.137 | 1249.187
DEER-SFAM-CZ04-V4-eSH-16-LH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-LH | 15.7219 | 2.3918 | 1087.8613 | 1450.7205 | 3.4 | 2538.5818 | 1190.4318
DEER-SFAM-CZ04-V4-eSH-16-LL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-LL | 15.2419 | 2.5824 | 1140.6859 | 1321.8953 | 3.4 | 2462.5811 | 1223.1811
DEER-SFAM-CZ04-V4-eSH-16-LM-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-LM | 15.1556 | 2.4921 | 1136.1665 | 1448.5483 | 3.4 | 2584.7148 | 1250.7648
DEER-SFAM-CZ04-V4-eSH-16-TH-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-TH | 17.0373 | 2.6984 | 1097.182 | 1677.3465 | 3.9 | 2774.5285 | 1181.8785
DEER-SFAM-CZ04-V4-eSH-16-TL-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-TL | 16.2242 | 2.806 | 1171.0403 | 1641.6146 | 3.4 | 2812.6548 | 1253.6048
DEER-SFAM-CZ04-V4-eSH-16-TM-s2 | 16 | CZ04 | V4 | CZ04-V4-eSH-16 | CZ04-V4-eSH-16-TM | 16.3816 | 2.7616 | 1159.7885 | 1667.4226 | 3.4 | 2827.2111 | 1244.6111
DEER-SFAM-CZ04-V4-eSH-17-CM-s2 | 17 | CZ04 | V4 | CZ04-V4-eSH-17 | CZ04-V4-eSH-17-CM | 17.1711 | 2.7166 | 1092.2171 | 1328.4236 | 3.9 | 2420.6408 | 1189.4908
DEER-SFAM-CZ04-V4-eSH-17-LM-s2 | 17 | CZ04 | V4 | CZ04-V4-eSH-17 | CZ04-V4-eSH-17-LM | 16.1195 | 2.6079 | 1088.065 | 1277.5131 | 3.9 | 2365.5781 | 1134.2281
DEER-SFAM-CZ04-V4-eSH-17-TH-s2 | 17 | CZ04 | V4 | CZ04-V4-eSH-17 | CZ04-V4-eSH-17-TH | 18.1334 | 2.5383 | 1031.4568 | 1668.7894 | 3.9 | 2700.2462 | 1122.5962
DEER-SFAM-CZ04-V4-eSH-17-TL-s2 | 17 | CZ04 | V4 | CZ04-V4-eSH-17 | CZ04-V4-eSH-17-TL | 18.0322 | 2.5918 | 1037.1316 | 1646.8354 | 3.9 | 2683.9669 | 1126.9669
DEER-SFAM-CZ04-V4-eSH-18-LH-s2 | 18 | CZ04 | V4 | CZ04-V4-eSH-18 | CZ04-V4-eSH-18-LH | 17.3889 | 2.2992 | 1000.3932 | 1443.4986 | 3.4 | 2443.8918 | 1075.7919
DEER-SFAM-CZ04-V4-eSH-18-LL-s2 | 18 | CZ04 | V4 | CZ04-V4-eSH-18 | CZ04-V4-eSH-18-LL | 16.6262 | 2.3738 | 1038.2333 | 1316.4472 | 3.4 | 2354.6806 | 1109.3305
DEER-SFAM-CZ04-V4-eSH-18-LM-s2 | 18 | CZ04 | V4 | CZ04-V4-eSH-18 | CZ04-V4-eSH-18-LM | 17.3046 | 2.3461 | 1009.9238 | 1512.4731 | 3.4 | 2522.3969 | 1096.0469
DEER-SFAM-CZ04-V4-eSH-18-TM-s2 | 18 | CZ04 | V4 | CZ04-V4-eSH-18 | CZ04-V4-eSH-18-TM | 19.6175 | 2.3289 | 952.2046 | 1639.6104 | 3.4 | 2591.8149 | 1095.965
DEER-SFAM-CZ05-V1-eSA-10-HH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-HH | 10.5068 | 2.3881 | 275.7985 | 0 | 3.4688 | 275.7985 | 436.5611
DEER-SFAM-CZ05-V1-eSA-10-HL-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-HL | 10.6563 | 2.4878 | 270.9298 | 0 | 3.711 | 270.9298 | 431.8957
DEER-SFAM-CZ05-V1-eSA-10-HM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-HM | 10.4567 | 2.4596 | 272.9857 | 0 | 3.711 | 272.9857 | 433.9294
DEER-SFAM-CZ05-V1-eSA-10-LH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-LH | 10.24 | 2.3393 | 264.4612 | 0 | 3.4688 | 264.4612 | 425.4926
DEER-SFAM-CZ05-V1-eSA-10-LL-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-LL | 10.3185 | 2.5116 | 277.796 | 0 | 3.711 | 277.796 | 438.7909
DEER-SFAM-CZ05-V1-eSA-10-LM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-LM | 10.2624 | 2.3662 | 266.5307 | 0 | 3.4688 | 266.5307 | 427.5676
DEER-SFAM-CZ05-V1-eSA-10-MH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-MH | 10.1186 | 2.323 | 270.6153 | 0 | 3.4688 | 270.6153 | 431.6001
DEER-SFAM-CZ05-V1-eSA-10-ML-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-ML | 10.5042 | 2.5383 | 280.4493 | 0 | 3.711 | 280.4493 | 441.4187
DEER-SFAM-CZ05-V1-eSA-10-MM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSA-10 | CZ05-V1-eSA-10-MM | 10.4889 | 2.3225 | 261.3752 | 0 | 3.4688 | 261.3752 | 422.2898
DEER-SFAM-CZ05-V1-eSA-13-HH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-HH | 12.941 | 1.8653 | 207.3156 | 0 | 3.711 | 207.3156 | 352.412
DEER-SFAM-CZ05-V1-eSA-13-HL-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-HL | 13.4773 | 1.8625 | 204.2712 | 0 | 3.711 | 204.2712 | 331.2579
DEER-SFAM-CZ05-V1-eSA-13-HM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-HM | 13.5267 | 1.8876 | 204.9691 | 0 | 3.711 | 204.9691 | 350.017
DEER-SFAM-CZ05-V1-eSA-13-LH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-LH | 13.1464 | 1.7796 | 204.0946 | 0 | 3.4688 | 204.0946 | 365.0323
DEER-SFAM-CZ05-V1-eSA-13-LL-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-LL | 13.4829 | 1.8883 | 209.7602 | 0 | 3.4688 | 209.7602 | 370.3758
DEER-SFAM-CZ05-V1-eSA-13-LM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-LM | 12.8718 | 1.8678 | 214.1354 | 0 | 3.4688 | 214.1354 | 374.9388
DEER-SFAM-CZ05-V1-eSA-13-MH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-MH | 14.4315 | 1.7918 | 196.1431 | 0 | 3.4688 | 196.1431 | 357.0173
DEER-SFAM-CZ05-V1-eSA-13-ML-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-ML | 13.2235 | 1.8578 | 204.3437 | 0 | 3.4688 | 204.3437 | 364.7187
DEER-SFAM-CZ05-V1-eSA-13-MM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSA-13 | CZ05-V1-eSA-13-MM | 14.5619 | 1.7908 | 194.3674 | 0 | 3.711 | 194.3674 | 355.2886
DEER-SFAM-CZ05-V1-eSA-14-HH-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-HH | 13.769 | 1.7863 | 196.5376 | 0 | 3.4688 | 196.5376 | 331.3632
DEER-SFAM-CZ05-V1-eSA-14-HL-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-HL | 14.6891 | 1.7542 | 187.761 | 0 | 3.711 | 187.761 | 286.9472
DEER-SFAM-CZ05-V1-eSA-14-HM-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-HM | 14.4974 | 1.7651 | 189.2031 | 0 | 3.4688 | 189.2031 | 341.3172
DEER-SFAM-CZ05-V1-eSA-14-MH-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-MH | 13.7295 | 1.7673 | 203.388 | 0 | 3.4688 | 203.388 | 309.0839
DEER-SFAM-CZ05-V1-eSA-14-ML-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-ML | 13.9227 | 1.7357 | 192.3687 | 0 | 3.4688 | 192.3687 | 361.1848
DEER-SFAM-CZ05-V1-eSA-14-MM-s1 | 14 | CZ05 | V1 | CZ05-V1-eSA-14 | CZ05-V1-eSA-14-MM | 13.8734 | 1.721 | 195.9186 | 0 | 3.4688 | 195.9186 | 311.8011
DEER-SFAM-CZ05-V1-eSA-15-HH-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-HH | 15.7166 | 1.5921 | 174.3688 | 0 | 3.711 | 174.3688 | 286.8155
DEER-SFAM-CZ05-V1-eSA-15-HL-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-HL | 16.1946 | 1.5843 | 170.1077 | 0 | 3.711 | 170.1077 | 310.2557
DEER-SFAM-CZ05-V1-eSA-15-HM-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-HM | 15.4517 | 1.6015 | 177.0136 | 0 | 3.711 | 177.0136 | 289.8766
DEER-SFAM-CZ05-V1-eSA-15-MH-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-MH | 15.251 | 1.6162 | 178.389 | 0 | 3.4688 | 178.389 | 262.1413
DEER-SFAM-CZ05-V1-eSA-15-ML-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-ML | 16.0433 | 1.6366 | 177.2719 | 0 | 3.4688 | 177.2719 | 289.8876
DEER-SFAM-CZ05-V1-eSA-15-MM-s1 | 15 | CZ05 | V1 | CZ05-V1-eSA-15 | CZ05-V1-eSA-15-MM | 15.363 | 1.6063 | 178.2737 | 0 | 3.4688 | 178.2737 | 280.9708
DEER-SFAM-CZ05-V1-eSA-16-CH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-CH | 16.6245 | 1.7353 | 198.4206 | 0 | 3.711 | 198.4206 | 262.4107
DEER-SFAM-CZ05-V1-eSA-16-CL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-CL | 17.1198 | 1.6276 | 185.5417 | 0 | 3.711 | 185.5417 | 266.8281
DEER-SFAM-CZ05-V1-eSA-16-CM-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-CM | 16.7769 | 1.6756 | 189.9504 | 0 | 3.711 | 189.9504 | 275.7559
DEER-SFAM-CZ05-V1-eSA-16-LH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-LH | 16.3853 | 1.4705 | 181.9781 | 0 | 3.711 | 181.9781 | 292.2213
DEER-SFAM-CZ05-V1-eSA-16-LL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-LL | 15.9797 | 1.5617 | 187.8564 | 0 | 3.711 | 187.8564 | 260.432
DEER-SFAM-CZ05-V1-eSA-16-LM-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-LM | 15.8534 | 1.5831 | 189.9486 | 0 | 3.4688 | 189.9486 | 255.6892
DEER-SFAM-CZ05-V1-eSA-16-NM-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-NM | 16.9612 | 1.4894 | 186.7001 | 0 | 3.4688 | 186.7001 | 251.1535
DEER-SFAM-CZ05-V1-eSA-16-TH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-TH | 17.5125 | 1.6228 | 195.3423 | 0 | 3.4688 | 195.3423 | 236.1634
DEER-SFAM-CZ05-V1-eSA-16-TL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSA-16 | CZ05-V1-eSA-16-TL | 18.4814 | 1.5639 | 186.0584 | 0 | 3.711 | 186.0584 | 230.3204
DEER-SFAM-CZ05-V1-eSA-17-CH-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-CH | 17.7552 | 1.5969 | 181.5715 | 0 | 3.711 | 181.5715 | 262.8078
DEER-SFAM-CZ05-V1-eSA-17-CL-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-CL | 17.7612 | 1.5979 | 181.465 | 0 | 3.711 | 181.465 | 262.6835
DEER-SFAM-CZ05-V1-eSA-17-CM-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-CM | 17.9425 | 1.6146 | 184.0176 | 0 | 3.711 | 184.0176 | 247.8167
DEER-SFAM-CZ05-V1-eSA-17-LH-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-LH | 17.0246 | 1.4343 | 172.2424 | 0 | 3.4688 | 172.2424 | 258.6456
DEER-SFAM-CZ05-V1-eSA-17-LL-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-LL | 17.0132 | 1.5076 | 179.0419 | 0 | 3.711 | 179.0419 | 226.2203
DEER-SFAM-CZ05-V1-eSA-17-LM-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-LM | 16.6946 | 1.5239 | 182.4923 | 0 | 3.711 | 182.4923 | 223.2299
DEER-SFAM-CZ05-V1-eSA-17-TH-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-TH | 20.1925 | 1.4372 | 165.4602 | 0 | 3.711 | 165.4602 | 231.0166
DEER-SFAM-CZ05-V1-eSA-17-TL-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-TL | 21.7702 | 1.3458 | 148.5531 | 0 | 3.711 | 148.5531 | 251.4141
DEER-SFAM-CZ05-V1-eSA-17-TM-s2 | 17 | CZ05 | V1 | CZ05-V1-eSA-17 | CZ05-V1-eSA-17-TM | 19.5548 | 1.5377 | 186.3257 | 0 | 3.711 | 186.3257 | 220.4581
DEER-SFAM-CZ05-V1-eSA-18-LH-s2 | 18 | CZ05 | V1 | CZ05-V1-eSA-18 | CZ05-V1-eSA-18-LH | 17.8639 | 1.4033 | 169.8832 | 0 | 3.711 | 169.8832 | 226.6106
DEER-SFAM-CZ05-V1-eSA-18-LL-s2 | 18 | CZ05 | V1 | CZ05-V1-eSA-18 | CZ05-V1-eSA-18-LL | 18.3622 | 1.382 | 163.5691 | 0 | 3.711 | 163.5691 | 237.5933
DEER-SFAM-CZ05-V1-eSA-18-TH-s2 | 18 | CZ05 | V1 | CZ05-V1-eSA-18 | CZ05-V1-eSA-18-TH | 20.4985 | 1.3627 | 163.0096 | 0 | 3.711 | 163.0096 | 207.626
DEER-SFAM-CZ05-V1-eSA-18-TL-s2 | 18 | CZ05 | V1 | CZ05-V1-eSA-18 | CZ05-V1-eSA-18-TL | 20.4179 | 1.4213 | 164.7647 | 0 | 3.711 | 164.7647 | 213.6168
DEER-SFAM-CZ05-V1-eSA-18-TM-s2 | 18 | CZ05 | V1 | CZ05-V1-eSA-18 | CZ05-V1-eSA-18-TM | 19.8725 | 1.4204 | 167.1957 | 0 | 3.4688 | 167.1957 | 212.716
DEER-SFAM-CZ05-V1-eSH-10-HH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-HH | 10.117 | 2.3445 | 266.4205 | 3421.5494 | 3.711 | 3687.9698 | 618.6522
DEER-SFAM-CZ05-V1-eSH-10-HL-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-HL | 10.095 | 2.4452 | 272.8591 | 3460.8648 | 3.711 | 3733.7239 | 621.9996
DEER-SFAM-CZ05-V1-eSH-10-HM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-HM | 10.6829 | 2.3957 | 269.0926 | 3313.0657 | 3.4688 | 3582.1583 | 602.9892
DEER-SFAM-CZ05-V1-eSH-10-LH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-LH | 10.1256 | 2.2919 | 272.1276 | 3626.6582 | 3.4688 | 3898.7858 | 635.9994
DEER-SFAM-CZ05-V1-eSH-10-LL-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-LL | 10.3597 | 2.4306 | 273.4812 | 3484.1846 | 3.4688 | 3757.6657 | 650.8409
DEER-SFAM-CZ05-V1-eSH-10-LM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-LM | 10.3661 | 2.3621 | 273.1099 | 3407.4499 | 3.4688 | 3680.5598 | 618.3518
DEER-SFAM-CZ05-V1-eSH-10-MH-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-MH | 10.3062 | 2.318 | 266.3648 | 3579.988 | 3.4688 | 3846.3529 | 652.9964
DEER-SFAM-CZ05-V1-eSH-10-ML-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-ML | 10.4697 | 2.4746 | 270.1816 | 3253.8042 | 3.711 | 3523.9858 | 617.333
DEER-SFAM-CZ05-V1-eSH-10-MM-s1 | 10 | CZ05 | V1 | CZ05-V1-eSH-10 | CZ05-V1-eSH-10-MM | 10.6663 | 2.4125 | 271.2317 | 3455.7394 | 3.4688 | 3726.9711 | 597.6767
DEER-SFAM-CZ05-V1-eSH-13-HH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-HH | 13.5236 | 1.8919 | 206.6272 | 3342.3045 | 3.711 | 3548.9317 | 527.5454
DEER-SFAM-CZ05-V1-eSH-13-HL-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-HL | 13.4015 | 1.854 | 200.7774 | 2892.2121 | 3.711 | 3092.9895 | 520.206
DEER-SFAM-CZ05-V1-eSH-13-HM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-HM | 13.7057 | 1.8767 | 205.0204 | 2961.3751 | 3.711 | 3166.3955 | 493.8928
DEER-SFAM-CZ05-V1-eSH-13-LH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-LH | 13.0011 | 1.8029 | 206.4899 | 3672.8828 | 3.4688 | 3879.3727 | 689.6822
DEER-SFAM-CZ05-V1-eSH-13-LL-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-LL | 14.3158 | 1.7881 | 196.2388 | 3072.2514 | 3.711 | 3268.4903 | 489.1444
DEER-SFAM-CZ05-V1-eSH-13-LM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-LM | 12.7038 | 1.894 | 215.52 | 2657.4462 | 3.4688 | 2872.9662 | 550.0427
DEER-SFAM-CZ05-V1-eSH-13-MH-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-MH | 14.0163 | 1.7463 | 194.8346 | 3383.0307 | 3.711 | 3577.8653 | 518.4246
DEER-SFAM-CZ05-V1-eSH-13-ML-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-ML | 13.2243 | 1.9112 | 210.8846 | 3203.1953 | 3.4688 | 3414.0799 | 542.8037
DEER-SFAM-CZ05-V1-eSH-13-MM-s1 | 13 | CZ05 | V1 | CZ05-V1-eSH-13 | CZ05-V1-eSH-13-MM | 14.2973 | 1.8316 | 197.5028 | 3111.6911 | 3.4688 | 3309.1939 | 455.2449
DEER-SFAM-CZ05-V1-eSH-14-HH-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-HH | 14.4388 | 1.793 | 193.4333 | 3054.931 | 3.711 | 3248.3643 | 437.721
DEER-SFAM-CZ05-V1-eSH-14-HL-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-HL | 14.5955 | 1.7856 | 190.6861 | 3051.8264 | 3.711 | 3242.5125 | 485.2218
DEER-SFAM-CZ05-V1-eSH-14-HM-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-HM | 14.279 | 1.767 | 194.1659 | 3001.557 | 3.711 | 3195.7229 | 402.9083
DEER-SFAM-CZ05-V1-eSH-14-MH-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-MH | 13.801 | 1.6833 | 193.5364 | 3314.0333 | 3.4688 | 3507.5697 | 511.6141
DEER-SFAM-CZ05-V1-eSH-14-ML-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-ML | 14.513 | 1.6855 | 186.0003 | 3484.6037 | 3.711 | 3670.6041 | 588.1736
DEER-SFAM-CZ05-V1-eSH-14-MM-s1 | 14 | CZ05 | V1 | CZ05-V1-eSH-14 | CZ05-V1-eSH-14-MM | 13.9425 | 1.7085 | 190.7293 | 2996.1479 | 3.4688 | 3186.8772 | 467.8519
DEER-SFAM-CZ05-V1-eSH-15-HH-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-HH | 15.3786 | 1.6039 | 178.1506 | 3690.0974 | 3.711 | 3868.248 | 405.6508
DEER-SFAM-CZ05-V1-eSH-15-HL-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-HL | 15.5424 | 1.6616 | 179.3554 | 2586.1162 | 3.711 | 2765.4716 | 404.4547
DEER-SFAM-CZ05-V1-eSH-15-HM-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-HM | 15.9623 | 1.5776 | 171.7307 | 2706.2409 | 3.711 | 2877.9716 | 397.3378
DEER-SFAM-CZ05-V1-eSH-15-MH-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-MH | 15.6706 | 1.5926 | 172.6957 | 3285.0405 | 3.4688 | 3457.7362 | 391.7106
DEER-SFAM-CZ05-V1-eSH-15-ML-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-ML | 15.6627 | 1.5783 | 173.1927 | 3018.4468 | 3.711 | 3191.6396 | 399.9829
DEER-SFAM-CZ05-V1-eSH-15-MM-s1 | 15 | CZ05 | V1 | CZ05-V1-eSH-15 | CZ05-V1-eSH-15-MM | 16.4151 | 1.5767 | 169.1508 | 3162.7577 | 3.711 | 3331.9084 | 407.727
DEER-SFAM-CZ05-V1-eSH-16-CH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-CH | 16.9057 | 1.6732 | 194.5678 | 3376.5466 | 3.711 | 3571.1145 | 408.2991
DEER-SFAM-CZ05-V1-eSH-16-CL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-CL | 17.2008 | 1.694 | 191.5828 | 3141.4997 | 3.711 | 3333.0825 | 412.7526
DEER-SFAM-CZ05-V1-eSH-16-LH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-LH | 16.1787 | 1.4686 | 183.0854 | 3600.0012 | 3.711 | 3783.0866 | 421.427
DEER-SFAM-CZ05-V1-eSH-16-LL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-LL | 15.9288 | 1.5848 | 190.1778 | 3359.2679 | 3.4688 | 3549.4457 | 385.029
DEER-SFAM-CZ05-V1-eSH-16-LM-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-LM | 15.692 | 1.5356 | 190.0232 | 3672.6153 | 3.4688 | 3862.6385 | 460.0954
DEER-SFAM-CZ05-V1-eSH-16-TH-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-TH | 18.8874 | 1.4911 | 176.5937 | 4201.7898 | 3.711 | 4378.3835 | 408.4391
DEER-SFAM-CZ05-V1-eSH-16-TL-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-TL | 17.9704 | 1.6734 | 190.7497 | 4169.8058 | 3.711 | 4360.5555 | 402.2211
DEER-SFAM-CZ05-V1-eSH-16-TM-s2 | 16 | CZ05 | V1 | CZ05-V1-eSH-16 | CZ05-V1-eSH-16-TM | 18.1812 | 1.6548 | 188.5377 | 4222.0338 | 3.711 | 4410.5715 | 405.2368
DEER-SFAM-CZ05-V1-eSH-17-CM-s2 | 17 | CZ05 | V1 | CZ05-V1-eSH-17 | CZ05-V1-eSH-17-CM | 18.2191 | 1.5987 | 180.813 | 3491.4729 | 3.711 | 3672.2859 | 431.5021
DEER-SFAM-CZ05-V1-eSH-17-LM-s2 | 17 | CZ05 | V1 | CZ05-V1-eSH-17 | CZ05-V1-eSH-17-LM | 17.1595 | 1.4938 | 178.1717 | 3208.1927 | 3.711 | 3386.3644 | 286.2066
DEER-SFAM-CZ05-V1-eSH-17-TH-s2 | 17 | CZ05 | V1 | CZ05-V1-eSH-17 | CZ05-V1-eSH-17-TH | 20.2139 | 1.44 | 164.9171 | 4189.7202 | 3.711 | 4354.6373 | 411.4507
DEER-SFAM-CZ05-V1-eSH-17-TL-s2 | 17 | CZ05 | V1 | CZ05-V1-eSH-17 | CZ05-V1-eSH-17-TL | 20.1314 | 1.4532 | 165.4944 | 4170.5345 | 3.711 | 4336.029 | 409.6318
DEER-SFAM-CZ05-V1-eSH-18-LH-s2 | 18 | CZ05 | V1 | CZ05-V1-eSH-18 | CZ05-V1-eSH-18-LH | 18.1942 | 1.4191 | 166.1758 | 3750.6538 | 3.711 | 3916.8295 | 351.4974
DEER-SFAM-CZ05-V1-eSH-18-LL-s2 | 18 | CZ05 | V1 | CZ05-V1-eSH-18 | CZ05-V1-eSH-18-LL | 17.3788 | 1.4779 | 171.6851 | 3400.4508 | 3.4688 | 3572.1359 | 341.3361
DEER-SFAM-CZ05-V1-eSH-18-LM-s2 | 18 | CZ05 | V1 | CZ05-V1-eSH-18 | CZ05-V1-eSH-18-LM | 18.332 | 1.4088 | 166.2875 | 3959.573 | 3.711 | 4125.8605 | 379.9259
DEER-SFAM-CZ05-V1-eSH-18-TM-s2 | 18 | CZ05 | V1 | CZ05-V1-eSH-18 | CZ05-V1-eSH-18-TM | 21.6269 | 1.3848 | 153.0734 | 4167.3843 | 3.4688 | 4320.4577 | 511.7566
DEER-SFAM-CZ05-V2-eSA-10-HH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-HH | 10.2269 | 1.8409 | 121.5227 | 0 | 3.1141 | 121.5227 | 193.377
DEER-SFAM-CZ05-V2-eSA-10-HL-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-HL | 10.4817 | 1.9031 | 118.9136 | 0 | 3.1141 | 118.9136 | 190.8266
DEER-SFAM-CZ05-V2-eSA-10-HM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-HM | 10.297 | 1.8834 | 119.782 | 0 | 3.1141 | 119.782 | 191.6845
DEER-SFAM-CZ05-V2-eSA-10-LH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-LH | 10.0982 | 1.809 | 116.8835 | 0 | 3.1141 | 116.8835 | 188.8548
DEER-SFAM-CZ05-V2-eSA-10-LL-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-LL | 10.2162 | 1.9223 | 121.2991 | 0 | 3.1141 | 121.2991 | 193.2257
DEER-SFAM-CZ05-V2-eSA-10-LM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-LM | 10.0853 | 1.8259 | 117.8685 | 0 | 3.1141 | 117.8685 | 189.8423
DEER-SFAM-CZ05-V2-eSA-10-MH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-MH | 9.8791 | 1.8092 | 120.4291 | 0 | 3.1141 | 120.4291 | 192.3796
DEER-SFAM-CZ05-V2-eSA-10-ML-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-ML | 10.3676 | 1.9405 | 122.5477 | 0 | 3.1141 | 122.5477 | 194.4624
DEER-SFAM-CZ05-V2-eSA-10-MM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSA-10 | CZ05-V2-eSA-10-MM | 10.2555 | 1.7863 | 115.7438 | 0 | 3.1141 | 115.7438 | 187.6646
DEER-SFAM-CZ05-V2-eSA-13-HH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-HH | 12.7574 | 1.4317 | 91.4754 | 0 | 3.1141 | 91.4754 | 156.2996
DEER-SFAM-CZ05-V2-eSA-13-HL-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-HL | 13.2644 | 1.4234 | 89.4603 | 0 | 3.1141 | 89.4603 | 146.1938
DEER-SFAM-CZ05-V2-eSA-13-HM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-HM | 13.3641 | 1.453 | 90.297 | 0 | 3.2676 | 90.297 | 155.118
DEER-SFAM-CZ05-V2-eSA-13-LH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-LH | 12.9336 | 1.378 | 90.0207 | 0 | 3.1141 | 90.0207 | 161.9515
DEER-SFAM-CZ05-V2-eSA-13-LL-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-LL | 13.246 | 1.4515 | 91.7789 | 0 | 3.1141 | 91.7789 | 163.5697
DEER-SFAM-CZ05-V2-eSA-13-LM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-LM | 12.6117 | 1.4441 | 94.3746 | 0 | 3.1141 | 94.3746 | 166.2463
DEER-SFAM-CZ05-V2-eSA-13-MH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-MH | 14.0648 | 1.3902 | 87.1285 | 0 | 3.1141 | 87.1285 | 159.0311
DEER-SFAM-CZ05-V2-eSA-13-ML-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-ML | 12.9264 | 1.4251 | 90.157 | 0 | 3.1141 | 90.157 | 161.8374
DEER-SFAM-CZ05-V2-eSA-13-MM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSA-13 | CZ05-V2-eSA-13-MM | 14.3459 | 1.3687 | 85.0812 | 0 | 3.1141 | 85.0812 | 156.974
DEER-SFAM-CZ05-V2-eSA-14-HH-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-HH | 13.4176 | 1.3748 | 86.95 | 0 | 3.1141 | 86.95 | 147.2119
DEER-SFAM-CZ05-V2-eSA-14-HL-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-HL | 14.4542 | 1.346 | 82.719 | 0 | 3.1141 | 82.719 | 127.0326
DEER-SFAM-CZ05-V2-eSA-14-HM-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-HM | 14.1882 | 1.3546 | 83.7014 | 0 | 3.1141 | 83.7014 | 151.6888
DEER-SFAM-CZ05-V2-eSA-14-MH-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-MH | 13.418 | 1.3733 | 90.0729 | 0 | 3.1141 | 90.0729 | 137.3167
DEER-SFAM-CZ05-V2-eSA-14-ML-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-ML | 13.6654 | 1.3342 | 84.6375 | 0 | 3.1141 | 84.6375 | 160.0895
DEER-SFAM-CZ05-V2-eSA-14-MM-s1 | 14 | CZ05 | V2 | CZ05-V2-eSA-14 | CZ05-V2-eSA-14-MM | 13.5455 | 1.3319 | 86.8852 | 0 | 3.1141 | 86.8852 | 138.6812
DEER-SFAM-CZ05-V2-eSA-15-HH-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-HH | 15.4103 | 1.2314 | 77.4704 | 0 | 3.2676 | 77.4704 | 127.7235
DEER-SFAM-CZ05-V2-eSA-15-HL-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-HL | 15.8455 | 1.215 | 75.2432 | 0 | 3.1141 | 75.2432 | 137.8552
DEER-SFAM-CZ05-V2-eSA-15-HM-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-HM | 15.1317 | 1.2386 | 78.5761 | 0 | 3.2676 | 78.5761 | 129.0149
DEER-SFAM-CZ05-V2-eSA-15-MH-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-MH | 14.7151 | 1.2495 | 79.5909 | 0 | 3.1141 | 79.5909 | 117.0258
DEER-SFAM-CZ05-V2-eSA-15-ML-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-ML | 15.6739 | 1.2576 | 77.9964 | 0 | 3.1141 | 77.9964 | 128.3347
DEER-SFAM-CZ05-V2-eSA-15-MM-s1 | 15 | CZ05 | V2 | CZ05-V2-eSA-15 | CZ05-V2-eSA-15-MM | 15.0038 | 1.2364 | 78.6226 | 0 | 3.1141 | 78.6226 | 124.5246
DEER-SFAM-CZ05-V2-eSA-16-CH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-CH | 16.2847 | 1.3013 | 88.9493 | 0 | 3.2676 | 88.9493 | 118.0507
DEER-SFAM-CZ05-V2-eSA-16-CL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-CL | 16.7736 | 1.2177 | 83.9417 | 0 | 3.2676 | 83.9417 | 120.7762
DEER-SFAM-CZ05-V2-eSA-16-CM-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-CM | 16.3925 | 1.259 | 86.2286 | 0 | 3.2676 | 86.2286 | 125.1113
DEER-SFAM-CZ05-V2-eSA-16-LH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-LH | 15.9364 | 1.1232 | 82.3808 | 0 | 3.1141 | 82.3808 | 132.1424
DEER-SFAM-CZ05-V2-eSA-16-LL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-LL | 15.6331 | 1.1839 | 84.6217 | 0 | 3.1141 | 84.6217 | 117.3014
DEER-SFAM-CZ05-V2-eSA-16-LM-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-LM | 15.4901 | 1.2062 | 85.6096 | 0 | 3.1141 | 85.6096 | 115.2344
DEER-SFAM-CZ05-V2-eSA-16-NM-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-NM | 16.7438 | 1.1207 | 82.9879 | 0 | 3.1141 | 82.9879 | 112.0756
DEER-SFAM-CZ05-V2-eSA-16-TH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-TH | 16.4797 | 1.2267 | 88.6962 | 0 | 3.1141 | 88.6962 | 107.3551
DEER-SFAM-CZ05-V2-eSA-16-TL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSA-16 | CZ05-V2-eSA-16-TL | 17.9042 | 1.1679 | 82.2646 | 0 | 3.1141 | 82.2646 | 102.3917
DEER-SFAM-CZ05-V2-eSA-17-CH-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-CH | 17.3785 | 1.1962 | 81.8536 | 0 | 3.2676 | 81.8536 | 118.6735
DEER-SFAM-CZ05-V2-eSA-17-CL-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-CL | 17.4362 | 1.1933 | 81.576 | 0 | 3.2676 | 81.576 | 118.3871
DEER-SFAM-CZ05-V2-eSA-17-CM-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-CM | 17.624 | 1.2067 | 82.2458 | 0 | 3.2676 | 82.2458 | 111.2595
DEER-SFAM-CZ05-V2-eSA-17-LH-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-LH | 16.5373 | 1.0938 | 78.3827 | 0 | 3.1141 | 78.3827 | 117.3741
DEER-SFAM-CZ05-V2-eSA-17-LL-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-LL | 16.5577 | 1.1366 | 79.5114 | 0 | 3.1141 | 79.5114 | 100.7343
DEER-SFAM-CZ05-V2-eSA-17-LM-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-LM | 16.3459 | 1.1519 | 80.5479 | 0 | 3.1141 | 80.5479 | 98.8834
DEER-SFAM-CZ05-V2-eSA-17-TH-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-TH | 19.0802 | 1.089 | 74.8758 | 0 | 3.1141 | 74.8758 | 104.6992
DEER-SFAM-CZ05-V2-eSA-17-TL-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-TL | 20.7519 | 1.0032 | 68.0444 | 0 | 3.1141 | 68.0444 | 114.7879
DEER-SFAM-CZ05-V2-eSA-17-TM-s2 | 17 | CZ05 | V2 | CZ05-V2-eSA-17 | CZ05-V2-eSA-17-TM | 18.9237 | 1.1537 | 81.8299 | 0 | 3.1141 | 81.8299 | 97.3854
DEER-SFAM-CZ05-V2-eSA-18-LH-s2 | 18 | CZ05 | V2 | CZ05-V2-eSA-18 | CZ05-V2-eSA-18-LH | 17.401 | 1.0656 | 76.4882 | 0 | 3.1141 | 76.4882 | 102.0359
DEER-SFAM-CZ05-V2-eSA-18-LL-s2 | 18 | CZ05 | V2 | CZ05-V2-eSA-18 | CZ05-V2-eSA-18-LL | 18.0056 | 1.0461 | 73.2998 | 0 | 3.1141 | 73.2998 | 106.6571
DEER-SFAM-CZ05-V2-eSA-18-TH-s2 | 18 | CZ05 | V2 | CZ05-V2-eSA-18 | CZ05-V2-eSA-18-TH | 19.4814 | 1.0342 | 73.5173 | 0 | 3.1141 | 73.5173 | 93.7767
DEER-SFAM-CZ05-V2-eSA-18-TL-s2 | 18 | CZ05 | V2 | CZ05-V2-eSA-18 | CZ05-V2-eSA-18-TL | 19.4447 | 1.0698 | 73.9454 | 0 | 3.1141 | 73.9454 | 96.2225
DEER-SFAM-CZ05-V2-eSA-18-TM-s2 | 18 | CZ05 | V2 | CZ05-V2-eSA-18 | CZ05-V2-eSA-18-TM | 18.7332 | 1.0835 | 76.0247 | 0 | 3.1141 | 76.0247 | 96.7351
DEER-SFAM-CZ05-V2-eSH-10-HH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-HH | 10.0153 | 1.8076 | 117.3693 | 1549.9221 | 3.1141 | 1667.2914 | 275.0029
DEER-SFAM-CZ05-V2-eSH-10-HL-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-HL | 10.0057 | 1.8769 | 119.8045 | 1563.4081 | 3.1141 | 1683.2127 | 275.5424
DEER-SFAM-CZ05-V2-eSH-10-HM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-HM | 10.4543 | 1.8491 | 118.7749 | 1515.6774 | 3.1141 | 1634.4523 | 267.9004
DEER-SFAM-CZ05-V2-eSH-10-LH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-LH | 9.9028 | 1.7875 | 120.5592 | 1631.2865 | 3.1141 | 1751.8457 | 283.3852
DEER-SFAM-CZ05-V2-eSH-10-LL-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-LL | 10.2224 | 1.8777 | 120.0109 | 1565.2238 | 3.1141 | 1685.2347 | 289.2096
DEER-SFAM-CZ05-V2-eSH-10-LM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-LM | 10.2019 | 1.836 | 120.0591 | 1552.3978 | 3.1141 | 1672.4569 | 275.0148
DEER-SFAM-CZ05-V2-eSH-10-MH-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-MH | 10.1389 | 1.798 | 117.7757 | 1608.9017 | 3.1141 | 1726.6774 | 290.7043
DEER-SFAM-CZ05-V2-eSH-10-ML-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-ML | 10.3494 | 1.898 | 118.3971 | 1471.3862 | 3.1141 | 1589.7833 | 274.4694
DEER-SFAM-CZ05-V2-eSH-10-MM-s1 | 10 | CZ05 | V2 | CZ05-V2-eSH-10 | CZ05-V2-eSH-10-MM | 10.4286 | 1.8551 | 119.5337 | 1562.3973 | 3.1141 | 1681.931 | 265.8002
DEER-SFAM-CZ05-V2-eSH-13-HH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-HH | 13.2391 | 1.4577 | 91.4847 | 1484.1051 | 3.1141 | 1575.5898 | 235.3675
DEER-SFAM-CZ05-V2-eSH-13-HL-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-HL | 13.2166 | 1.4238 | 88.5244 | 1287.2489 | 3.2676 | 1375.7733 | 231.6455
DEER-SFAM-CZ05-V2-eSH-13-HM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-HM | 13.5208 | 1.4423 | 90.0172 | 1328.2495 | 3.1141 | 1418.2668 | 219.5417
DEER-SFAM-CZ05-V2-eSH-13-LH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-LH | 12.7047 | 1.3982 | 91.8304 | 1538.2353 | 3.1141 | 1630.0656 | 309.0025
DEER-SFAM-CZ05-V2-eSH-13-LL-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-LL | 14.0966 | 1.3724 | 86.3377 | 1352.4758 | 3.1141 | 1438.8135 | 217.7773
DEER-SFAM-CZ05-V2-eSH-13-LM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-LM | 12.4832 | 1.463 | 94.7112 | 1192.1854 | 3.1141 | 1286.8965 | 244.2351
DEER-SFAM-CZ05-V2-eSH-13-MH-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-MH | 13.6447 | 1.346 | 86.8334 | 1502.0262 | 3.1141 | 1588.8597 | 231.519
DEER-SFAM-CZ05-V2-eSH-13-ML-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-ML | 12.9413 | 1.4698 | 92.862 | 1390.7303 | 3.1141 | 1483.5922 | 241.0912
DEER-SFAM-CZ05-V2-eSH-13-MM-s1 | 13 | CZ05 | V2 | CZ05-V2-eSH-13 | CZ05-V2-eSH-13-MM | 13.9416 | 1.4154 | 87.5347 | 1395.8582 | 3.1141 | 1483.3929 | 202.8424
DEER-SFAM-CZ05-V2-eSH-14-HH-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-HH | 14.172 | 1.379 | 85.4132 | 1356.333 | 3.1141 | 1441.7462 | 194.9197
DEER-SFAM-CZ05-V2-eSH-14-HL-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-HL | 14.3916 | 1.3679 | 83.9148 | 1329.4853 | 3.1141 | 1413.4 | 215.706
DEER-SFAM-CZ05-V2-eSH-14-HM-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-HM | 14.0753 | 1.3593 | 85.437 | 1323.0686 | 3.1141 | 1408.5056 | 179.0918
DEER-SFAM-CZ05-V2-eSH-14-MH-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-MH | 13.5625 | 1.304 | 85.5618 | 1399.1334 | 3.1141 | 1484.6952 | 228.8125
DEER-SFAM-CZ05-V2-eSH-14-ML-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-ML | 14.2927 | 1.2861 | 81.6794 | 1453.5381 | 3.1141 | 1535.2175 | 261.7432
DEER-SFAM-CZ05-V2-eSH-14-MM-s1 | 14 | CZ05 | V2 | CZ05-V2-eSH-14 | CZ05-V2-eSH-14-MM | 13.7357 | 1.314 | 83.9086 | 1295.5846 | 3.1141 | 1379.4932 | 207.9006
DEER-SFAM-CZ05-V2-eSH-15-HH-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-HH | 15.0353 | 1.236 | 79.055 | 1541.4881 | 3.1141 | 1620.5431 | 181.6983
DEER-SFAM-CZ05-V2-eSH-15-HL-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-HL | 15.367 | 1.2741 | 78.687 | 1151.3941 | 3.1141 | 1230.0811 | 179.3886
DEER-SFAM-CZ05-V2-eSH-15-HM-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-HM | 15.5585 | 1.2109 | 76.2494 | 1195.1645 | 3.1141 | 1271.4139 | 176.9748
DEER-SFAM-CZ05-V2-eSH-15-MH-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-MH | 15.2554 | 1.2272 | 79.2407 | 1369.085 | 3.1141 | 1448.3257 | 177.0528
DEER-SFAM-CZ05-V2-eSH-15-ML-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-ML | 15.471 | 1.2051 | 75.7172 | 1281.9633 | 3.1141 | 1357.6804 | 177.0752
DEER-SFAM-CZ05-V2-eSH-15-MM-s1 | 15 | CZ05 | V2 | CZ05-V2-eSH-15 | CZ05-V2-eSH-15-MM | 15.9659 | 1.2143 | 75.3624 | 1363.939 | 3.2676 | 1439.3013 | 182.62
DEER-SFAM-CZ05-V2-eSH-16-CH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-CH | 16.5059 | 1.2573 | 87.6095 | 1448.002 | 3.2676 | 1535.6115 | 178.5331
DEER-SFAM-CZ05-V2-eSH-16-CL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-CL | 16.8289 | 1.268 | 85.9868 | 1340.7419 | 3.2676 | 1426.7287 | 179.9799
DEER-SFAM-CZ05-V2-eSH-16-LH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-LH | 15.6954 | 1.1271 | 83.0344 | 1518.7752 | 3.1141 | 1601.8096 | 186.1466
DEER-SFAM-CZ05-V2-eSH-16-LL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-LL | 15.6156 | 1.2049 | 85.496 | 1374.3038 | 3.1141 | 1459.7998 | 168.0327
DEER-SFAM-CZ05-V2-eSH-16-LM-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-LM | 15.1227 | 1.1816 | 87.0833 | 1519.6887 | 3.1141 | 1606.772 | 202.4076
DEER-SFAM-CZ05-V2-eSH-16-TH-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-TH | 18.0088 | 1.1282 | 80.5342 | 1853.7887 | 3.2676 | 1934.3228 | 174.6189
DEER-SFAM-CZ05-V2-eSH-16-TL-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-TL | 17.3149 | 1.2525 | 84.3543 | 1813.0846 | 3.1141 | 1897.4389 | 170.6477
DEER-SFAM-CZ05-V2-eSH-16-TM-s2 | 16 | CZ05 | V2 | CZ05-V2-eSH-16 | CZ05-V2-eSH-16-TM | 17.5874 | 1.2412 | 83.0471 | 1840.7074 | 3.1141 | 1923.7545 | 171.8928
DEER-SFAM-CZ05-V2-eSH-17-CM-s2 | 17 | CZ05 | V2 | CZ05-V2-eSH-17 | CZ05-V2-eSH-17-CM | 17.8016 | 1.198 | 81.2213 | 1460.7426 | 3.2676 | 1541.9639 | 184.8292
DEER-SFAM-CZ05-V2-eSH-17-LM-s2 | 17 | CZ05 | V2 | CZ05-V2-eSH-17 | CZ05-V2-eSH-17-LM | 16.7263 | 1.1315 | 78.9932 | 1333.8423 | 3.1141 | 1412.8356 | 125.3797
DEER-SFAM-CZ05-V2-eSH-17-TH-s2 | 17 | CZ05 | V2 | CZ05-V2-eSH-17 | CZ05-V2-eSH-17-TH | 19.1817 | 1.0863 | 74.5412 | 1851.4803 | 3.1141 | 1926.0215 | 178.2344
DEER-SFAM-CZ05-V2-eSH-17-TL-s2 | 17 | CZ05 | V2 | CZ05-V2-eSH-17 | CZ05-V2-eSH-17-TL | 19.2691 | 1.0933 | 74.2237 | 1834.872 | 3.1141 | 1909.0957 | 176.4931
DEER-SFAM-CZ05-V2-eSH-18-LH-s2 | 18 | CZ05 | V2 | CZ05-V2-eSH-18 | CZ05-V2-eSH-18-LH | 17.6954 | 1.0717 | 73.8089 | 1557.8965 | 3.1141 | 1631.7054 | 150.32
DEER-SFAM-CZ05-V2-eSH-18-LL-s2 | 18 | CZ05 | V2 | CZ05-V2-eSH-18 | CZ05-V2-eSH-18-LL | 16.8766 | 1.1233 | 77.92 | 1376.1032 | 3.1141 | 1454.0232 | 149.2476
DEER-SFAM-CZ05-V2-eSH-18-LM-s2 | 18 | CZ05 | V2 | CZ05-V2-eSH-18 | CZ05-V2-eSH-18-LM | 17.8813 | 1.0635 | 73.6856 | 1652.1589 | 3.1141 | 1725.8444 | 161.8491
DEER-SFAM-CZ05-V2-eSH-18-TM-s2 | 18 | CZ05 | V2 | CZ05-V2-eSH-18 | CZ05-V2-eSH-18-TM | 20.2209 | 1.0407 | 70.6279 | 1849.151 | 3.1141 | 1919.7789 | 224.2694
DEER-SFAM-CZ05-V3-eSA-10-HH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-HH | 10.6861 | 2.7418 | 511.329 | 0 | 3.4 | 511.329 | 575.0391
DEER-SFAM-CZ05-V3-eSA-10-HL-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-HL | 10.911 | 2.872 | 505.1596 | 0 | 3.4 | 505.1596 | 568.9283
DEER-SFAM-CZ05-V3-eSA-10-HM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-HM | 10.662 | 2.8264 | 511.3675 | 0 | 3.4 | 511.3675 | 575.1257
DEER-SFAM-CZ05-V3-eSA-10-LH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-LH | 10.3425 | 2.7176 | 502.7976 | 0 | 3.4 | 502.7976 | 566.625
DEER-SFAM-CZ05-V3-eSA-10-LL-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-LL | 10.5096 | 2.918 | 521.3937 | 0 | 3.4 | 521.3937 | 585.1761
DEER-SFAM-CZ05-V3-eSA-10-LM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-LM | 10.3609 | 2.7427 | 505.8893 | 0 | 3.4 | 505.8893 | 569.7191
DEER-SFAM-CZ05-V3-eSA-10-MH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-MH | 10.2824 | 2.6692 | 510.0804 | 0 | 3.4 | 510.0804 | 573.8868
DEER-SFAM-CZ05-V3-eSA-10-ML-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-ML | 10.6814 | 2.9337 | 523.2156 | 0 | 3.4 | 523.2156 | 586.9859
DEER-SFAM-CZ05-V3-eSA-10-MM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSA-10 | CZ05-V3-eSA-10-MM | 10.5866 | 2.7041 | 495.0785 | 0 | 3.4 | 495.0785 | 558.8545
DEER-SFAM-CZ05-V3-eSA-13-HH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-HH | 13.1871 | 2.1439 | 394.1833 | 0 | 3.4 | 394.1833 | 451.6676
DEER-SFAM-CZ05-V3-eSA-13-HL-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-HL | 13.5754 | 2.1831 | 386.7599 | 0 | 3.4 | 386.7599 | 437.0693
DEER-SFAM-CZ05-V3-eSA-13-HM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-HM | 13.7567 | 2.1898 | 388.0318 | 0 | 3.4 | 388.0318 | 445.4936
DEER-SFAM-CZ05-V3-eSA-13-LH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-LH | 13.2987 | 2.0595 | 386.92 | 0 | 3.4 | 386.92 | 450.7057
DEER-SFAM-CZ05-V3-eSA-13-LL-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-LL | 13.595 | 2.206 | 394.7801 | 0 | 3.4 | 394.7801 | 458.4271
DEER-SFAM-CZ05-V3-eSA-13-LM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-LM | 13.0124 | 2.162 | 404.3646 | 0 | 3.4 | 404.3646 | 468.0922
DEER-SFAM-CZ05-V3-eSA-13-MH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-MH | 14.7688 | 2.0751 | 366.4355 | 0 | 3.4 | 366.4355 | 430.1943
DEER-SFAM-CZ05-V3-eSA-13-ML-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-ML | 13.3077 | 2.1749 | 388.7552 | 0 | 3.4 | 388.7552 | 452.3139
DEER-SFAM-CZ05-V3-eSA-13-MM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSA-13 | CZ05-V3-eSA-13-MM | 14.9708 | 2.0657 | 361.3317 | 0 | 3.4 | 361.3317 | 425.0799
DEER-SFAM-CZ05-V3-eSA-14-HH-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-HH | 13.9148 | 2.0772 | 372.508 | 0 | 3.4 | 372.508 | 425.9438
DEER-SFAM-CZ05-V3-eSA-14-HL-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-HL | 14.8964 | 2.0433 | 356.8184 | 0 | 3.4 | 356.8184 | 396.1148
DEER-SFAM-CZ05-V3-eSA-14-HM-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-HM | 14.5728 | 2.0767 | 360.4434 | 0 | 3.4 | 360.4434 | 420.7332
DEER-SFAM-CZ05-V3-eSA-14-MH-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-MH | 13.8586 | 2.0346 | 383.5925 | 0 | 3.4 | 383.5925 | 425.4837
DEER-SFAM-CZ05-V3-eSA-14-ML-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-ML | 13.9959 | 2.037 | 366.7531 | 0 | 3.4 | 366.7531 | 433.6585
DEER-SFAM-CZ05-V3-eSA-14-MM-s1 | 14 | CZ05 | V3 | CZ05-V3-eSA-14 | CZ05-V3-eSA-14-MM | 14.0502 | 1.9901 | 370.2704 | 0 | 3.4 | 370.2704 | 416.2004
DEER-SFAM-CZ05-V3-eSA-15-HH-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-HH | 16.1314 | 1.8216 | 327.8225 | 0 | 3.4 | 327.8225 | 372.3736
DEER-SFAM-CZ05-V3-eSA-15-HL-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-HL | 16.5302 | 1.8262 | 320.8761 | 0 | 3.4 | 320.8761 | 376.3942
DEER-SFAM-CZ05-V3-eSA-15-HM-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-HM | 15.5975 | 1.8827 | 334.1941 | 0 | 3.9 | 334.1941 | 378.9627
DEER-SFAM-CZ05-V3-eSA-15-MH-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-MH | 15.5325 | 1.8789 | 335.7415 | 0 | 3.4 | 335.7415 | 368.94
DEER-SFAM-CZ05-V3-eSA-15-ML-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-ML | 16.2406 | 1.9129 | 333.0553 | 0 | 3.4 | 333.0553 | 377.6844
DEER-SFAM-CZ05-V3-eSA-15-MM-s1 | 15 | CZ05 | V3 | CZ05-V3-eSA-15 | CZ05-V3-eSA-15-MM | 15.5202 | 1.8792 | 337.7676 | 0 | 3.4 | 337.7676 | 378.474
DEER-SFAM-CZ05-V3-eSA-16-CH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-CH | 16.7283 | 1.9587 | 350.3537 | 0 | 3.4 | 350.3537 | 375.9803
DEER-SFAM-CZ05-V3-eSA-16-CL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-CL | 17.2682 | 1.843 | 334.9925 | 0 | 3.9 | 334.9925 | 367.4493
DEER-SFAM-CZ05-V3-eSA-16-CM-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-CM | 16.8873 | 1.8901 | 343.7603 | 0 | 3.9 | 343.7603 | 377.9678
DEER-SFAM-CZ05-V3-eSA-16-LH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-LH | 16.9135 | 1.6809 | 321.5716 | 0 | 3.4 | 321.5716 | 365.674
DEER-SFAM-CZ05-V3-eSA-16-LL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-LL | 16.2685 | 1.7853 | 334.7072 | 0 | 3.4 | 334.7072 | 363.6449
DEER-SFAM-CZ05-V3-eSA-16-LM-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-LM | 16.0417 | 1.8094 | 340.9103 | 0 | 3.4 | 340.9103 | 367.1375
DEER-SFAM-CZ05-V3-eSA-16-NM-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-NM | 17.1419 | 1.7259 | 332.127 | 0 | 3.4 | 332.127 | 357.8779
DEER-SFAM-CZ05-V3-eSA-16-TH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-TH | 18.3556 | 1.8353 | 322.8823 | 0 | 3.4 | 322.8823 | 339.3759
DEER-SFAM-CZ05-V3-eSA-16-TL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSA-16 | CZ05-V3-eSA-16-TL | 19.4 | 1.7572 | 306.1813 | 0 | 3.4 | 306.1813 | 323.9782
DEER-SFAM-CZ05-V3-eSA-17-CH-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-CH | 17.8547 | 1.8219 | 324.2837 | 0 | 3.4 | 324.2837 | 356.6672
DEER-SFAM-CZ05-V3-eSA-17-CL-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-CL | 17.8871 | 1.8352 | 323.7203 | 0 | 3.4 | 323.7203 | 356.0965
DEER-SFAM-CZ05-V3-eSA-17-CM-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-CM | 18.0262 | 1.8389 | 325.4023 | 0 | 3.4 | 325.4023 | 350.9542
DEER-SFAM-CZ05-V3-eSA-17-LH-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-LH | 17.3676 | 1.6534 | 309.2919 | 0 | 3.4 | 309.2919 | 343.8515
DEER-SFAM-CZ05-V3-eSA-17-LL-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-LL | 17.3112 | 1.7057 | 317.7495 | 0 | 3.4 | 317.7495 | 336.5346
DEER-SFAM-CZ05-V3-eSA-17-LM-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-LM | 16.9978 | 1.7147 | 324.0712 | 0 | 3.4 | 324.0712 | 340.3018
DEER-SFAM-CZ05-V3-eSA-17-TH-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-TH | 21.086 | 1.6288 | 276.007 | 0 | 3.4 | 276.007 | 302.3874
DEER-SFAM-CZ05-V3-eSA-17-TL-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-TL | 22.7491 | 1.585 | 252.123 | 0 | 3.4 | 252.123 | 293.215
DEER-SFAM-CZ05-V3-eSA-17-TM-s2 | 17 | CZ05 | V3 | CZ05-V3-eSA-17 | CZ05-V3-eSA-17-TM | 20.6533 | 1.6788 | 298.1938 | 0 | 3.4 | 298.1938 | 311.9491
DEER-SFAM-CZ05-V3-eSA-18-LH-s2 | 18 | CZ05 | V3 | CZ05-V3-eSA-18 | CZ05-V3-eSA-18-LH | 18.2903 | 1.5866 | 300.2676 | 0 | 3.4 | 300.2676 | 322.8843
DEER-SFAM-CZ05-V3-eSA-18-LL-s2 | 18 | CZ05 | V3 | CZ05-V3-eSA-18 | CZ05-V3-eSA-18-LL | 18.7191 | 1.5942 | 290.6758 | 0 | 3.4 | 290.6758 | 320.2108
DEER-SFAM-CZ05-V3-eSA-18-TH-s2 | 18 | CZ05 | V3 | CZ05-V3-eSA-18 | CZ05-V3-eSA-18-TH | 21.6193 | 1.516 | 269.888 | 0 | 3.4 | 269.888 | 287.8032
DEER-SFAM-CZ05-V3-eSA-18-TL-s2 | 18 | CZ05 | V3 | CZ05-V3-eSA-18 | CZ05-V3-eSA-18-TL | 21.4087 | 1.6046 | 273.7903 | 0 | 3.4 | 273.7903 | 293.4661
DEER-SFAM-CZ05-V3-eSA-18-TM-s2 | 18 | CZ05 | V3 | CZ05-V3-eSA-18 | CZ05-V3-eSA-18-TM | 20.5379 | 1.6056 | 283.2282 | 0 | 3.4 | 283.2282 | 301.5432
DEER-SFAM-CZ05-V3-eSH-10-HH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-HH | 10.335 | 2.6692 | 502.637 | 1328.6869 | 3.4 | 1831.3238 | 636.2739
DEER-SFAM-CZ05-V3-eSH-10-HL-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-HL | 10.2415 | 2.7977 | 515.4209 | 1341.005 | 3.4 | 1856.426 | 647.5259
DEER-SFAM-CZ05-V3-eSH-10-HM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-HM | 10.8749 | 2.7568 | 502.8116 | 1316.7484 | 3.4 | 1819.5601 | 629.0601
DEER-SFAM-CZ05-V3-eSH-10-LH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-LH | 10.2951 | 2.6326 | 502.7926 | 1394.1984 | 3.4 | 1896.991 | 640.741
DEER-SFAM-CZ05-V3-eSH-10-LL-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-LL | 10.5147 | 2.8133 | 515.477 | 1338.3077 | 3.4 | 1853.7848 | 658.7347
DEER-SFAM-CZ05-V3-eSH-10-LM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-LM | 10.5606 | 2.7205 | 512.1559 | 1332.6881 | 3.4 | 1844.844 | 643.894
DEER-SFAM-CZ05-V3-eSH-10-MH-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-MH | 10.4394 | 2.6684 | 503.179 | 1373.1174 | 3.4 | 1876.2965 | 649.4964
DEER-SFAM-CZ05-V3-eSH-10-ML-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-ML | 10.6514 | 2.8632 | 509.3447 | 1265.5727 | 3.4 | 1774.9174 | 642.0175
DEER-SFAM-CZ05-V3-eSH-10-MM-s1 | 10 | CZ05 | V3 | CZ05-V3-eSH-10 | CZ05-V3-eSH-10-MM | 10.8406 | 2.7744 | 504.66 | 1340.1553 | 3.4 | 1844.8153 | 629.2153
DEER-SFAM-CZ05-V3-eSH-13-HH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-HH | 13.8606 | 2.1754 | 386.3526 | 1278.8441 | 3.4 | 1665.1967 | 508.3467
DEER-SFAM-CZ05-V3-eSH-13-HL-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-HL | 13.5185 | 2.1827 | 380.6529 | 1110.8405 | 3.9 | 1491.4934 | 502.1934
DEER-SFAM-CZ05-V3-eSH-13-HM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-HM | 14.009 | 2.1667 | 383.6635 | 1146.5601 | 3.4 | 1530.2235 | 493.8235
DEER-SFAM-CZ05-V3-eSH-13-LH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-LH | 13.1894 | 2.0833 | 390.8085 | 1297.6291 | 3.4 | 1688.4376 | 572.5875
DEER-SFAM-CZ05-V3-eSH-13-LL-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-LL | 14.672 | 2.0487 | 366.2434 | 1156.3773 | 3.4 | 1522.6207 | 477.6707
DEER-SFAM-CZ05-V3-eSH-13-LM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-LM | 12.8228 | 2.198 | 408.0739 | 1021.0057 | 3.4 | 1429.0796 | 535.2296
DEER-SFAM-CZ05-V3-eSH-13-MH-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-MH | 14.497 | 1.959 | 363.2949 | 1283.727 | 3.4 | 1647.022 | 485.572
DEER-SFAM-CZ05-V3-eSH-13-ML-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-ML | 13.3447 | 2.237 | 398.4174 | 1180.0175 | 3.4 | 1578.4349 | 523.7849
DEER-SFAM-CZ05-V3-eSH-13-MM-s1 | 13 | CZ05 | V3 | CZ05-V3-eSH-13 | CZ05-V3-eSH-13-MM | 14.5298 | 2.1362 | 370.904 | 1202.4035 | 3.4 | 1573.3075 | 469.2076
DEER-SFAM-CZ05-V3-eSH-14-HH-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-HH | 14.7463 | 2.0713 | 362.8845 | 1170.6089 | 3.4 | 1533.4934 | 455.8435
DEER-SFAM-CZ05-V3-eSH-14-HL-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-HL | 14.7808 | 2.0878 | 361.4155 | 1142.223 | 3.4 | 1503.6385 | 472.7885
DEER-SFAM-CZ05-V3-eSH-14-HM-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-HM | 14.5411 | 2.0414 | 365.8774 | 1138.1473 | 3.4 | 1504.0248 | 445.3247
DEER-SFAM-CZ05-V3-eSH-14-MH-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-MH | 13.9686 | 1.9458 | 367.3791 | 1186.9007 | 3.4 | 1554.2797 | 488.0797
DEER-SFAM-CZ05-V3-eSH-14-ML-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-ML | 14.6256 | 1.9708 | 354.0048 | 1213.938 | 3.4 | 1567.9427 | 503.9928
DEER-SFAM-CZ05-V3-eSH-14-MM-s1 | 14 | CZ05 | V3 | CZ05-V3-eSH-14 | CZ05-V3-eSH-14-MM | 14.023 | 1.997 | 364.4776 | 1105.1022 | 3.4 | 1469.5798 | 469.2797
DEER-SFAM-CZ05-V3-eSH-15-HH-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-HH | 15.7014 | 1.8432 | 335.7414 | 1302.9898 | 3.4 | 1638.7313 | 421.6313
DEER-SFAM-CZ05-V3-eSH-15-HL-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-HL | 15.8049 | 1.9379 | 338.2554 | 995.6204 | 3.4 | 1333.8758 | 423.8258
DEER-SFAM-CZ05-V3-eSH-15-HM-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-HM | 16.302 | 1.8044 | 323.997 | 1041.9729 | 3.4 | 1365.9699 | 409.0199
DEER-SFAM-CZ05-V3-eSH-15-MH-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-MH | 15.8173 | 1.8655 | 327.7865 | 1148.6171 | 3.4 | 1476.4036 | 409.6037
DEER-SFAM-CZ05-V3-eSH-15-ML-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-ML | 15.7325 | 1.8482 | 330.543 | 1077.9765 | 3.4 | 1408.5195 | 415.4195
DEER-SFAM-CZ05-V3-eSH-15-MM-s1 | 15 | CZ05 | V3 | CZ05-V3-eSH-15 | CZ05-V3-eSH-15-MM | 16.7914 | 1.8073 | 318.2998 | 1163.7481 | 3.4 | 1482.0479 | 408.9479
DEER-SFAM-CZ05-V3-eSH-16-CH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-CH | 17.058 | 1.8827 | 345.9948 | 1131.8015 | 3.9 | 1477.7963 | 418.0963
DEER-SFAM-CZ05-V3-eSH-16-CL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-CL | 17.2883 | 1.9059 | 341.7033 | 1057.9923 | 3.9 | 1399.6956 | 417.0956
DEER-SFAM-CZ05-V3-eSH-16-LH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-LH | 16.7956 | 1.6467 | 321.7951 | 1224.7732 | 3.4 | 1546.5684 | 407.5183
DEER-SFAM-CZ05-V3-eSH-16-LL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-LL | 16.1478 | 1.8219 | 339.8972 | 1110.9127 | 3.4 | 1450.8099 | 408.8099
DEER-SFAM-CZ05-V3-eSH-16-LM-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-LM | 16.0427 | 1.7572 | 339.6732 | 1221.7332 | 3.4 | 1561.4063 | 435.4563
DEER-SFAM-CZ05-V3-eSH-16-TH-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-TH | 19.9718 | 1.6812 | 291.9583 | 1407.8497 | 3.4 | 1699.8081 | 365.7581
DEER-SFAM-CZ05-V3-eSH-16-TL-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-TL | 18.5008 | 1.9046 | 319.8596 | 1371.4155 | 3.4 | 1691.2751 | 386.7751
DEER-SFAM-CZ05-V3-eSH-16-TM-s2 | 16 | CZ05 | V3 | CZ05-V3-eSH-16 | CZ05-V3-eSH-16-TM | 18.7028 | 1.8714 | 316.4054 | 1393.4211 | 3.4 | 1709.8265 | 385.1265
DEER-SFAM-CZ05-V3-eSH-17-CM-s2 | 17 | CZ05 | V3 | CZ05-V3-eSH-17 | CZ05-V3-eSH-17-CM | 18.3384 | 1.8004 | 321.9416 | 1121.4607 | 3.9 | 1443.4023 | 403.3023
DEER-SFAM-CZ05-V3-eSH-17-LM-s2 | 17 | CZ05 | V3 | CZ05-V3-eSH-17 | CZ05-V3-eSH-17-LM | 17.5102 | 1.6678 | 315.5405 | 1080.1539 | 3.4 | 1395.6943 | 354.2944
DEER-SFAM-CZ05-V3-eSH-17-TH-s2 | 17 | CZ05 | V3 | CZ05-V3-eSH-17 | CZ05-V3-eSH-17-TH | 21.0454 | 1.622 | 276.7634 | 1398.7522 | 3.4 | 1675.5157 | 356.2656
DEER-SFAM-CZ05-V3-eSH-17-TL-s2 | 17 | CZ05 | V3 | CZ05-V3-eSH-17 | CZ05-V3-eSH-17-TL | 21.0014 | 1.6462 | 277.4182 | 1382.5346 | 3.4 | 1659.9527 | 355.7527
DEER-SFAM-CZ05-V3-eSH-18-LH-s2 | 18 | CZ05 | V3 | CZ05-V3-eSH-18 | CZ05-V3-eSH-18-LH | 18.5206 | 1.6134 | 294.4316 | 1209.1572 | 3.4 | 1503.5887 | 356.9887
DEER-SFAM-CZ05-V3-eSH-18-LL-s2 | 18 | CZ05 | V3 | CZ05-V3-eSH-18 | CZ05-V3-eSH-18-LL | 17.5871 | 1.6921 | 308.8628 | 1104.8021 | 3.4 | 1413.6649 | 368.2149
DEER-SFAM-CZ05-V3-eSH-18-LM-s2 | 18 | CZ05 | V3 | CZ05-V3-eSH-18 | CZ05-V3-eSH-18-LM | 18.7067 | 1.6023 | 294.5609 | 1266.4146 | 3.4 | 1560.9756 | 365.9255
DEER-SFAM-CZ05-V3-eSH-18-TM-s2 | 18 | CZ05 | V3 | CZ05-V3-eSH-18 | CZ05-V3-eSH-18-TM | 22.5438 | 1.6195 | 257.2174 | 1368.2042 | 3.4 | 1625.4216 | 374.1716
DEER-SFAM-CZ05-V4-eSA-10-HH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-HH | 10.6794 | 2.7173 | 494.6119 | 0 | 3.4 | 494.6119 | 546.3547
DEER-SFAM-CZ05-V4-eSA-10-HL-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-HL | 10.8644 | 2.8815 | 493.0122 | 0 | 3.9 | 493.0122 | 544.8677
DEER-SFAM-CZ05-V4-eSA-10-HM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-HM | 10.6065 | 2.8424 | 499.5818 | 0 | 3.9 | 499.5818 | 551.4298
DEER-SFAM-CZ05-V4-eSA-10-LH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-LH | 10.264 | 2.7397 | 492.0494 | 0 | 3.9 | 492.0494 | 543.947
DEER-SFAM-CZ05-V4-eSA-10-LL-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-LL | 10.482 | 2.9209 | 508.0125 | 0 | 3.9 | 508.0125 | 559.878
DEER-SFAM-CZ05-V4-eSA-10-LM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-LM | 10.2845 | 2.7616 | 494.9449 | 0 | 3.9 | 494.9449 | 546.8439
DEER-SFAM-CZ05-V4-eSA-10-MH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-MH | 10.1532 | 2.7098 | 501.6127 | 0 | 3.9 | 501.6127 | 553.4954
DEER-SFAM-CZ05-V4-eSA-10-ML-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-ML | 10.6452 | 2.9394 | 510.3954 | 0 | 3.9 | 510.3954 | 562.252
DEER-SFAM-CZ05-V4-eSA-10-MM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSA-10 | CZ05-V4-eSA-10-MM | 10.5856 | 2.6782 | 477.7445 | 0 | 3.4 | 477.7445 | 529.5418
DEER-SFAM-CZ05-V4-eSA-13-HH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-HH | 13.1142 | 2.1644 | 384.7306 | 0 | 3.9 | 384.7306 | 431.4749
DEER-SFAM-CZ05-V4-eSA-13-HL-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-HL | 13.5296 | 2.1797 | 376.6497 | 0 | 3.9 | 376.6497 | 417.5613
DEER-SFAM-CZ05-V4-eSA-13-HM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-HM | 13.7249 | 2.1928 | 377.6418 | 0 | 3.9 | 377.6418 | 424.3698
DEER-SFAM-CZ05-V4-eSA-13-LH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-LH | 13.3051 | 2.0413 | 373.5227 | 0 | 3.4 | 373.5227 | 425.3282
DEER-SFAM-CZ05-V4-eSA-13-LL-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-LL | 13.6077 | 2.1853 | 381.0632 | 0 | 3.4 | 381.0632 | 432.7527
DEER-SFAM-CZ05-V4-eSA-13-LM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-LM | 12.994 | 2.1423 | 390.6614 | 0 | 3.4 | 390.6614 | 442.4189
DEER-SFAM-CZ05-V4-eSA-13-MH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-MH | 14.6683 | 2.0939 | 358.4525 | 0 | 3.9 | 358.4525 | 410.3005
DEER-SFAM-CZ05-V4-eSA-13-ML-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-ML | 13.2472 | 2.1744 | 379.0027 | 0 | 3.9 | 379.0027 | 430.6905
DEER-SFAM-CZ05-V4-eSA-13-MM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSA-13 | CZ05-V4-eSA-13-MM | 14.879 | 2.0709 | 353.1116 | 0 | 3.9 | 353.1116 | 404.9523
DEER-SFAM-CZ05-V4-eSA-14-HH-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-HH | 13.8314 | 2.0859 | 363.687 | 0 | 3.9 | 363.687 | 407.1418
DEER-SFAM-CZ05-V4-eSA-14-HL-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-HL | 14.8643 | 2.0446 | 347.3003 | 0 | 3.9 | 347.3003 | 379.256
DEER-SFAM-CZ05-V4-eSA-14-HM-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-HM | 14.5282 | 2.0799 | 351.0537 | 0 | 3.9 | 351.0537 | 400.0792
DEER-SFAM-CZ05-V4-eSA-14-MH-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-MH | 13.8592 | 2.0177 | 370.5369 | 0 | 3.4 | 370.5369 | 404.5588
DEER-SFAM-CZ05-V4-eSA-14-ML-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-ML | 13.9396 | 2.0404 | 357.3565 | 0 | 3.9 | 357.3565 | 411.7636
DEER-SFAM-CZ05-V4-eSA-14-MM-s1 | 14 | CZ05 | V4 | CZ05-V4-eSA-14 | CZ05-V4-eSA-14-MM | 14.0508 | 1.9728 | 357.5605 | 0 | 3.4 | 357.5605 | 394.8626
DEER-SFAM-CZ05-V4-eSA-15-HH-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-HH | 16.0164 | 1.8361 | 320.5648 | 0 | 3.9 | 320.5648 | 356.7926
DEER-SFAM-CZ05-V4-eSA-15-HL-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-HL | 16.4966 | 1.8316 | 312.795 | 0 | 3.9 | 312.795 | 357.9445
DEER-SFAM-CZ05-V4-eSA-15-HM-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-HM | 15.63 | 1.8637 | 327.3758 | 0 | 3.9 | 327.3758 | 363.7371
DEER-SFAM-CZ05-V4-eSA-15-MH-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-MH | 15.406 | 1.8929 | 328.5189 | 0 | 3.9 | 328.5189 | 355.5147
DEER-SFAM-CZ05-V4-eSA-15-ML-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-ML | 16.2174 | 1.8938 | 321.8761 | 0 | 3.4 | 321.8761 | 358.1196
DEER-SFAM-CZ05-V4-eSA-15-MM-s1 | 15 | CZ05 | V4 | CZ05-V4-eSA-15 | CZ05-V4-eSA-15-MM | 15.4368 | 1.8825 | 329.6315 | 0 | 3.9 | 329.6315 | 362.7328
DEER-SFAM-CZ05-V4-eSA-16-CH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-CH | 16.7463 | 1.9308 | 346.6457 | 0 | 3.9 | 346.6457 | 367.5111
DEER-SFAM-CZ05-V4-eSA-16-CL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-CL | 17.3022 | 1.8205 | 328.1755 | 0 | 3.9 | 328.1755 | 354.5521
DEER-SFAM-CZ05-V4-eSA-16-CM-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-CM | 16.9219 | 1.8687 | 336.769 | 0 | 3.9 | 336.769 | 364.5704
DEER-SFAM-CZ05-V4-eSA-16-LH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-LH | 16.743 | 1.6491 | 321.802 | 0 | 3.9 | 321.802 | 357.6812
DEER-SFAM-CZ05-V4-eSA-16-LL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-LL | 16.2249 | 1.7436 | 332.2539 | 0 | 3.9 | 332.2539 | 355.7935
DEER-SFAM-CZ05-V4-eSA-16-LM-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-LM | 15.9982 | 1.7784 | 338.4646 | 0 | 3.9 | 338.4646 | 359.8021
DEER-SFAM-CZ05-V4-eSA-16-NM-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-NM | 17.1454 | 1.652 | 328.2553 | 0 | 3.9 | 328.2553 | 349.2088
DEER-SFAM-CZ05-V4-eSA-16-TH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-TH | 18.1352 | 1.7919 | 322.5113 | 0 | 3.9 | 322.5113 | 335.9393
DEER-SFAM-CZ05-V4-eSA-16-TL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSA-16 | CZ05-V4-eSA-16-TL | 19.3109 | 1.7041 | 304.4797 | 0 | 3.9 | 304.4797 | 318.9669
DEER-SFAM-CZ05-V4-eSA-17-CH-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-CH | 17.8813 | 1.7855 | 320.6375 | 0 | 3.9 | 320.6375 | 347.0022
DEER-SFAM-CZ05-V4-eSA-17-CL-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-CL | 17.8982 | 1.7894 | 320.4162 | 0 | 3.9 | 320.4162 | 346.7747
DEER-SFAM-CZ05-V4-eSA-17-CM-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-CM | 18.0589 | 1.797 | 321.5935 | 0 | 3.9 | 321.5935 | 342.3974
DEER-SFAM-CZ05-V4-eSA-17-LH-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-LH | 17.2661 | 1.6202 | 308.2903 | 0 | 3.9 | 308.2903 | 336.4037
DEER-SFAM-CZ05-V4-eSA-17-LL-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-LL | 17.2928 | 1.6744 | 314.3302 | 0 | 3.9 | 314.3302 | 329.6168
DEER-SFAM-CZ05-V4-eSA-17-LM-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-LM | 16.9557 | 1.6914 | 321.3106 | 0 | 3.9 | 321.3106 | 334.5156
DEER-SFAM-CZ05-V4-eSA-17-TH-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-TH | 20.9044 | 1.6039 | 275.2144 | 0 | 3.9 | 275.2144 | 296.6878
DEER-SFAM-CZ05-V4-eSA-17-TL-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-TL | 22.7276 | 1.5173 | 250.4178 | 0 | 3.9 | 250.4178 | 283.8844
DEER-SFAM-CZ05-V4-eSA-17-TM-s2 | 17 | CZ05 | V4 | CZ05-V4-eSA-17 | CZ05-V4-eSA-17-TM | 20.5116 | 1.649 | 294.1346 | 0 | 3.9 | 294.1346 | 305.3465
DEER-SFAM-CZ05-V4-eSA-18-LH-s2 | 18 | CZ05 | V4 | CZ05-V4-eSA-18 | CZ05-V4-eSA-18-LH | 18.2258 | 1.5606 | 297.7332 | 0 | 3.9 | 297.7332 | 316.1328
DEER-SFAM-CZ05-V4-eSA-18-LL-s2 | 18 | CZ05 | V4 | CZ05-V4-eSA-18 | CZ05-V4-eSA-18-LL | 18.6718 | 1.553 | 288.5546 | 0 | 3.9 | 288.5546 | 312.5827
DEER-SFAM-CZ05-V4-eSA-18-TH-s2 | 18 | CZ05 | V4 | CZ05-V4-eSA-18 | CZ05-V4-eSA-18-TH | 21.3169 | 1.5015 | 270.2062 | 0 | 3.9 | 270.2062 | 284.7862
DEER-SFAM-CZ05-V4-eSA-18-TL-s2 | 18 | CZ05 | V4 | CZ05-V4-eSA-18 | CZ05-V4-eSA-18-TL | 21.2453 | 1.571 | 272.2231 | 0 | 3.9 | 272.2231 | 288.2418
DEER-SFAM-CZ05-V4-eSA-18-TM-s2 | 18 | CZ05 | V4 | CZ05-V4-eSA-18 | CZ05-V4-eSA-18-TM | 20.356 | 1.5884 | 281.9745 | 0 | 3.9 | 281.9745 | 296.8814
DEER-SFAM-CZ05-V4-eSH-10-HH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-HH | 10.2535 | 2.6977 | 492.7583 | 1102.8813 | 3.9 | 1595.6396 | 602.2396
DEER-SFAM-CZ05-V4-eSH-10-HL-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-HL | 10.1936 | 2.8122 | 503.8444 | 1107.8573 | 3.9 | 1611.7017 | 611.9517
DEER-SFAM-CZ05-V4-eSH-10-HM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-HM | 10.7988 | 2.7783 | 491.9934 | 1090.3684 | 3.9 | 1582.3619 | 595.3619
DEER-SFAM-CZ05-V4-eSH-10-LH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-LH | 10.298 | 2.604 | 493.1696 | 1145.7582 | 3.4 | 1638.9278 | 605.9778
DEER-SFAM-CZ05-V4-eSH-10-LL-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-LL | 10.4607 | 2.8257 | 504.321 | 1106.6575 | 3.9 | 1610.9785 | 621.7285
DEER-SFAM-CZ05-V4-eSH-10-LM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-LM | 10.4809 | 2.746 | 502.7127 | 1105.9564 | 3.9 | 1608.6691 | 610.6691
DEER-SFAM-CZ05-V4-eSH-10-MH-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-MH | 10.3383 | 2.6995 | 493.9645 | 1139.0939 | 3.9 | 1633.0584 | 613.8084
DEER-SFAM-CZ05-V4-eSH-10-ML-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-ML | 10.6174 | 2.8658 | 496.4586 | 1045.3543 | 3.9 | 1541.8128 | 605.2628
DEER-SFAM-CZ05-V4-eSH-10-MM-s1 | 10 | CZ05 | V4 | CZ05-V4-eSH-10 | CZ05-V4-eSH-10-MM | 10.8459 | 2.7499 | 487.7283 | 1099.9473 | 3.4 | 1587.6757 | 589.5757
DEER-SFAM-CZ05-V4-eSH-13-HH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-HH | 13.7549 | 2.1976 | 378.0052 | 1061.3157 | 3.9 | 1439.3209 | 477.9709
DEER-SFAM-CZ05-V4-eSH-13-HL-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-HL | 13.5433 | 2.1598 | 373.2008 | 911.187 | 3.9 | 1284.3878 | 472.6377
DEER-SFAM-CZ05-V4-eSH-13-HM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-HM | 13.9038 | 2.1806 | 375.3417 | 948.923 | 3.9 | 1324.2647 | 465.6146
DEER-SFAM-CZ05-V4-eSH-13-LH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-LH | 13.1957 | 2.0657 | 377.2704 | 1065.9915 | 3.4 | 1443.262 | 525.962
DEER-SFAM-CZ05-V4-eSH-13-LL-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-LL | 14.6084 | 2.0585 | 357.3087 | 955.8357 | 3.9 | 1313.1445 | 448.6445
DEER-SFAM-CZ05-V4-eSH-13-LM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-LM | 12.822 | 2.1774 | 393.6939 | 837.1263 | 3.4 | 1230.8202 | 497.6202
DEER-SFAM-CZ05-V4-eSH-13-MH-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-MH | 14.3581 | 2.0004 | 356.3718 | 1069.3849 | 3.9 | 1425.7567 | 456.5067
DEER-SFAM-CZ05-V4-eSH-13-ML-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-ML | 13.3205 | 2.2159 | 385.197 | 966.8849 | 3.4 | 1352.0819 | 487.6819
DEER-SFAM-CZ05-V4-eSH-13-MM-s1 | 13 | CZ05 | V4 | CZ05-V4-eSH-13 | CZ05-V4-eSH-13-MM | 14.4516 | 2.1478 | 362.1332 | 993.7599 | 3.9 | 1355.893 | 442.5931
DEER-SFAM-CZ05-V4-eSH-14-HH-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-HH | 14.6474 | 2.0864 | 354.7082 | 968.9705 | 3.9 | 1323.6787 | 430.8787
DEER-SFAM-CZ05-V4-eSH-14-HL-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-HL | 14.7558 | 2.0855 | 351.4817 | 940.1493 | 3.9 | 1291.6309 | 442.731
DEER-SFAM-CZ05-V4-eSH-14-HM-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-HM | 14.4589 | 2.053 | 357.1583 | 941.8208 | 3.9 | 1298.979 | 422.279
DEER-SFAM-CZ05-V4-eSH-14-MH-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-MH | 13.9577 | 1.9292 | 355.0422 | 975.885 | 3.4 | 1330.9272 | 453.8272
DEER-SFAM-CZ05-V4-eSH-14-ML-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-ML | 14.5536 | 1.9708 | 345.3709 | 996.5648 | 3.9 | 1341.9357 | 468.3357
DEER-SFAM-CZ05-V4-eSH-14-MM-s1 | 14 | CZ05 | V4 | CZ05-V4-eSH-14 | CZ05-V4-eSH-14-MM | 14.0213 | 1.9789 | 351.9284 | 907.2909 | 3.4 | 1259.2193 | 437.6193
DEER-SFAM-CZ05-V4-eSH-15-HH-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-HH | 15.5966 | 1.8577 | 328.0115 | 1069.5492 | 3.9 | 1397.5606 | 398.4606
DEER-SFAM-CZ05-V4-eSH-15-HL-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-HL | 15.7479 | 1.9416 | 329.6015 | 821.1851 | 3.9 | 1150.7866 | 399.6866
DEER-SFAM-CZ05-V4-eSH-15-HM-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-HM | 16.2208 | 1.8193 | 316.2827 | 861.4289 | 3.9 | 1177.7116 | 385.9117
DEER-SFAM-CZ05-V4-eSH-15-MH-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-MH | 15.7384 | 1.8715 | 319.5088 | 946.9234 | 3.9 | 1266.4322 | 386.5322
DEER-SFAM-CZ05-V4-eSH-15-ML-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-ML | 15.6834 | 1.8461 | 321.8949 | 886.668 | 3.9 | 1208.563 | 391.4629
DEER-SFAM-CZ05-V4-eSH-15-MM-s1 | 15 | CZ05 | V4 | CZ05-V4-eSH-15 | CZ05-V4-eSH-15-MM | 16.704 | 1.8127 | 310.7996 | 959.0174 | 3.9 | 1269.8169 | 385.1169
DEER-SFAM-CZ05-V4-eSH-16-CH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-CH | 17.0998 | 1.8608 | 338.7634 | 930.9552 | 3.9 | 1269.7186 | 397.6186
DEER-SFAM-CZ05-V4-eSH-16-CL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-CL | 17.3434 | 1.883 | 334.4047 | 869.5434 | 3.9 | 1203.9481 | 395.9982
DEER-SFAM-CZ05-V4-eSH-16-LH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-LH | 16.5841 | 1.6402 | 321.8834 | 1011.8632 | 3.9 | 1333.7466 | 391.8465
DEER-SFAM-CZ05-V4-eSH-16-LL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-LL | 16.112 | 1.7827 | 337.2169 | 908.9881 | 3.9 | 1246.205 | 393.505
DEER-SFAM-CZ05-V4-eSH-16-LM-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-LM | 15.874 | 1.7319 | 340.0958 | 1005.0429 | 3.9 | 1345.1387 | 418.2887
DEER-SFAM-CZ05-V4-eSH-16-TH-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-TH | 19.736 | 1.6459 | 291.762 | 1157.9779 | 3.9 | 1449.7399 | 347.6399
DEER-SFAM-CZ05-V4-eSH-16-TL-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-TL | 18.5135 | 1.8557 | 315.5892 | 1119.0476 | 3.9 | 1434.6368 | 365.4368
DEER-SFAM-CZ05-V4-eSH-16-TM-s2 | 16 | CZ05 | V4 | CZ05-V4-eSH-16 | CZ05-V4-eSH-16-TM | 18.7274 | 1.832 | 311.9864 | 1140.0456 | 3.9 | 1452.0319 | 363.1319
DEER-SFAM-CZ05-V4-eSH-17-CM-s2 | 17 | CZ05 | V4 | CZ05-V4-eSH-17 | CZ05-V4-eSH-17-CM | 18.3903 | 1.7796 | 315.151 | 917.6185 | 3.9 | 1232.7695 | 381.4195
DEER-SFAM-CZ05-V4-eSH-17-LM-s2 | 17 | CZ05 | V4 | CZ05-V4-eSH-17 | CZ05-V4-eSH-17-LM | 17.4506 | 1.6576 | 312.9766 | 886.101 | 3.9 | 1199.0776 | 344.6277
DEER-SFAM-CZ05-V4-eSH-17-TH-s2 | 17 | CZ05 | V4 | CZ05-V4-eSH-17 | CZ05-V4-eSH-17-TH | 20.8711 | 1.5986 | 275.6782 | 1150.0897 | 3.9 | 1425.7679 | 335.618
DEER-SFAM-CZ05-V4-eSH-17-TL-s2 | 17 | CZ05 | V4 | CZ05-V4-eSH-17 | CZ05-V4-eSH-17-TL | 20.8398 | 1.6141 | 276.1766 | 1133.8007 | 3.9 | 1409.9773 | 335.3273
DEER-SFAM-CZ05-V4-eSH-18-LH-s2 | 18 | CZ05 | V4 | CZ05-V4-eSH-18 | CZ05-V4-eSH-18-LH | 18.4843 | 1.5874 | 292.2145 | 980.95 | 3.9 | 1273.1645 | 342.5145
DEER-SFAM-CZ05-V4-eSH-18-LL-s2 | 18 | CZ05 | V4 | CZ05-V4-eSH-18 | CZ05-V4-eSH-18-LL | 17.581 | 1.6638 | 305.9694 | 900.9903 | 3.9 | 1206.9597 | 354.3597
DEER-SFAM-CZ05-V4-eSH-18-LM-s2 | 18 | CZ05 | V4 | CZ05-V4-eSH-18 | CZ05-V4-eSH-18-LM | 18.6552 | 1.569 | 291.8983 | 1023.7157 | 3.9 | 1315.614 | 349.0641
DEER-SFAM-CZ05-V4-eSH-18-TM-s2 | 18 | CZ05 | V4 | CZ05-V4-eSH-18 | CZ05-V4-eSH-18-TM | 22.3434 | 1.5966 | 257.1074 | 1123.5549 | 3.9 | 1380.6624 | 345.9624
DEER-SFAM-CZ06-V1-eSA-10-HH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-HH | 10.8742 | 1.7951 | 780.6359 | 0 | 3.0988 | 780.6359 | 860.7323
DEER-SFAM-CZ06-V1-eSA-10-HL-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-HL | 10.908 | 1.8221 | 763.8354 | 0 | 3.0988 | 763.8354 | 844.0091
DEER-SFAM-CZ06-V1-eSA-10-HM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-HM | 10.7266 | 1.8241 | 769.6439 | 0 | 3.0988 | 769.6439 | 849.8043
DEER-SFAM-CZ06-V1-eSA-10-LH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-LH | 10.5714 | 1.7466 | 743.9819 | 0 | 3.0988 | 743.9819 | 824.2334
DEER-SFAM-CZ06-V1-eSA-10-LL-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-LL | 10.5204 | 1.8806 | 785.1407 | 0 | 3.0988 | 785.1407 | 865.333
DEER-SFAM-CZ06-V1-eSA-10-LM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-LM | 10.5809 | 1.7798 | 754.7057 | 0 | 3.0988 | 754.7057 | 834.9605
DEER-SFAM-CZ06-V1-eSA-10-MH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-MH | 10.5266 | 1.7311 | 759.2968 | 0 | 3.0988 | 759.2968 | 839.5215
DEER-SFAM-CZ06-V1-eSA-10-ML-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-ML | 10.8108 | 1.8967 | 789.6776 | 0 | 3.0988 | 789.6776 | 869.8533
DEER-SFAM-CZ06-V1-eSA-10-MM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSA-10 | CZ06-V1-eSA-10-MM | 10.8365 | 1.7256 | 736.7782 | 0 | 3.0988 | 736.7782 | 816.9619
DEER-SFAM-CZ06-V1-eSA-13-HH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-HH | 13.2552 | 1.3643 | 584.4557 | 0 | 3.0988 | 584.4557 | 656.727
DEER-SFAM-CZ06-V1-eSA-13-HL-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-HL | 14.0037 | 1.3859 | 574.6102 | 0 | 3.0988 | 574.6102 | 637.8591
DEER-SFAM-CZ06-V1-eSA-13-HM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-HM | 13.6999 | 1.3808 | 579.8595 | 0 | 3.0988 | 579.8595 | 652.1016
DEER-SFAM-CZ06-V1-eSA-13-LH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-LH | 13.5877 | 1.3336 | 574.0382 | 0 | 3.0988 | 574.0382 | 654.2355
DEER-SFAM-CZ06-V1-eSA-13-LL-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-LL | 13.8901 | 1.4044 | 593.3608 | 0 | 3.0988 | 593.3608 | 673.3725
DEER-SFAM-CZ06-V1-eSA-13-LM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-LM | 13.415 | 1.3915 | 599.4992 | 0 | 3.0988 | 599.4992 | 679.6189
DEER-SFAM-CZ06-V1-eSA-13-MH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-MH | 14.7558 | 1.2979 | 555.1346 | 0 | 3.0988 | 555.1346 | 635.2958
DEER-SFAM-CZ06-V1-eSA-13-ML-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-ML | 13.7954 | 1.3754 | 576.6677 | 0 | 3.0988 | 576.6677 | 656.5751
DEER-SFAM-CZ06-V1-eSA-13-MM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSA-13 | CZ06-V1-eSA-13-MM | 14.7073 | 1.32 | 555.8146 | 0 | 3.0988 | 555.8146 | 635.962
DEER-SFAM-CZ06-V1-eSA-14-HH-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-HH | 14.4122 | 1.2937 | 552.6216 | 0 | 3.0988 | 552.6216 | 619.8006
DEER-SFAM-CZ06-V1-eSA-14-HL-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-HL | 15.0897 | 1.2685 | 529.0077 | 0 | 3.0988 | 529.0077 | 578.4089
DEER-SFAM-CZ06-V1-eSA-14-HM-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-HM | 15.1322 | 1.27 | 528.1618 | 0 | 3.0988 | 528.1618 | 603.9625
DEER-SFAM-CZ06-V1-eSA-14-MH-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-MH | 14.3523 | 1.3036 | 569.3162 | 0 | 3.0988 | 569.3162 | 621.9781
DEER-SFAM-CZ06-V1-eSA-14-ML-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-ML | 14.4961 | 1.2869 | 540.4045 | 0 | 3.0988 | 540.4045 | 624.5228
DEER-SFAM-CZ06-V1-eSA-14-MM-s1 | 14 | CZ06 | V1 | CZ06-V1-eSA-14 | CZ06-V1-eSA-14-MM | 14.4833 | 1.2634 | 548.8673 | 0 | 3.0988 | 548.8673 | 606.6091
DEER-SFAM-CZ06-V1-eSA-15-HH-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-HH | 16.0433 | 1.1383 | 489.4803 | 0 | 3.0988 | 489.4803 | 545.4898
DEER-SFAM-CZ06-V1-eSA-15-HL-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-HL | 16.5248 | 1.1422 | 482.3761 | 0 | 3.0988 | 482.3761 | 552.1721
DEER-SFAM-CZ06-V1-eSA-15-HM-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-HM | 15.7954 | 1.1674 | 499.1075 | 0 | 3.0988 | 499.1075 | 555.3209
DEER-SFAM-CZ06-V1-eSA-15-MH-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-MH | 16.0844 | 1.1558 | 495.4293 | 0 | 3.0988 | 495.4293 | 537.1651
DEER-SFAM-CZ06-V1-eSA-15-ML-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-ML | 16.4451 | 1.1965 | 503.4267 | 0 | 3.0988 | 503.4267 | 559.5265
DEER-SFAM-CZ06-V1-eSA-15-MM-s1 | 15 | CZ06 | V1 | CZ06-V1-eSA-15 | CZ06-V1-eSA-15-MM | 15.9385 | 1.1936 | 502.3469 | 0 | 3.0988 | 502.3469 | 553.5216
DEER-SFAM-CZ06-V1-eSA-16-CH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-CH | 16.9341 | 1.2853 | 569.1568 | 0 | 3.0988 | 569.1568 | 601.1062
DEER-SFAM-CZ06-V1-eSA-16-CL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-CL | 17.4277 | 1.2167 | 533.217 | 0 | 3.0988 | 533.217 | 573.7416
DEER-SFAM-CZ06-V1-eSA-16-CM-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-CM | 17.1011 | 1.2362 | 544.9962 | 0 | 3.0988 | 544.9962 | 587.7437
DEER-SFAM-CZ06-V1-eSA-16-LH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-LH | 16.4974 | 1.1762 | 534.1956 | 0 | 3.0988 | 534.1956 | 589.2504
DEER-SFAM-CZ06-V1-eSA-16-LL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-LL | 16.1023 | 1.2213 | 548.7374 | 0 | 3.0988 | 548.7374 | 584.9446
DEER-SFAM-CZ06-V1-eSA-16-LM-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-LM | 16.1243 | 1.2393 | 552.1593 | 0 | 3.0988 | 552.1593 | 584.9747
DEER-SFAM-CZ06-V1-eSA-16-NM-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-NM | 17.2958 | 1.2173 | 541.3458 | 0 | 3.0988 | 541.3458 | 573.5296
DEER-SFAM-CZ06-V1-eSA-16-TH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-TH | 17.9852 | 1.1718 | 555.8074 | 0 | 3.0988 | 555.8074 | 576.2522
DEER-SFAM-CZ06-V1-eSA-16-TL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSA-16 | CZ06-V1-eSA-16-TL | 18.4276 | 1.1834 | 544.1263 | 0 | 3.0988 | 544.1263 | 566.2555
DEER-SFAM-CZ06-V1-eSA-17-CH-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-CH | 18.1398 | 1.1891 | 520.0349 | 0 | 3.0988 | 520.0349 | 560.5324
DEER-SFAM-CZ06-V1-eSA-17-CL-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-CL | 18.1551 | 1.196 | 519.4228 | 0 | 3.0988 | 519.4228 | 559.9121
DEER-SFAM-CZ06-V1-eSA-17-CM-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-CM | 18.2448 | 1.2266 | 527.0694 | 0 | 3.0988 | 527.0694 | 558.9242
DEER-SFAM-CZ06-V1-eSA-17-LH-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-LH | 17.2544 | 1.1176 | 503.5036 | 0 | 3.0988 | 503.5036 | 546.6609
DEER-SFAM-CZ06-V1-eSA-17-LL-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-LL | 17.2402 | 1.1507 | 520.562 | 0 | 3.0988 | 520.562 | 544.084
DEER-SFAM-CZ06-V1-eSA-17-LM-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-LM | 17.0137 | 1.1691 | 525.7025 | 0 | 3.0988 | 525.7025 | 546.0195
DEER-SFAM-CZ06-V1-eSA-17-TH-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-TH | 20.7279 | 0.99943 | 469.5445 | 0 | 3.0988 | 469.5445 | 502.3222
DEER-SFAM-CZ06-V1-eSA-17-TL-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-TL | 21.4904 | 1.034 | 445.6977 | 0 | 3.0988 | 445.6977 | 496.9991
DEER-SFAM-CZ06-V1-eSA-17-TM-s2 | 17 | CZ06 | V1 | CZ06-V1-eSA-17 | CZ06-V1-eSA-17-TM | 19.7204 | 1.2205 | 540.9916 | 0 | 3.0988 | 540.9916 | 558.0541
DEER-SFAM-CZ06-V1-eSA-18-LH-s2 | 18 | CZ06 | V1 | CZ06-V1-eSA-18 | CZ06-V1-eSA-18-LH | 18.1849 | 1.0923 | 493.0836 | 0 | 3.0988 | 493.0836 | 521.3824
DEER-SFAM-CZ06-V1-eSA-18-LL-s2 | 18 | CZ06 | V1 | CZ06-V1-eSA-18 | CZ06-V1-eSA-18-LL | 18.5617 | 1.0869 | 478.004 | 0 | 3.0988 | 478.004 | 514.9387
DEER-SFAM-CZ06-V1-eSA-18-TH-s2 | 18 | CZ06 | V1 | CZ06-V1-eSA-18 | CZ06-V1-eSA-18-TH | 21.0084 | 0.97561 | 461.2308 | 0 | 3.0988 | 461.2308 | 483.5295
DEER-SFAM-CZ06-V1-eSA-18-TL-s2 | 18 | CZ06 | V1 | CZ06-V1-eSA-18 | CZ06-V1-eSA-18-TL | 20.7729 | 1.0243 | 471.5273 | 0 | 3.0988 | 471.5273 | 495.9669
DEER-SFAM-CZ06-V1-eSA-18-TM-s2 | 18 | CZ06 | V1 | CZ06-V1-eSA-18 | CZ06-V1-eSA-18-TM | 20.3453 | 1.0032 | 477.7111 | 0 | 3.0988 | 477.7111 | 500.4841
DEER-SFAM-CZ06-V1-eSH-10-HH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-HH | 10.4482 | 1.7276 | 752.0699 | 1517.4997 | 3.0988 | 2269.5696 | 909.7211
DEER-SFAM-CZ06-V1-eSH-10-HL-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-HL | 10.3968 | 1.8117 | 773.6586 | 1540.7178 | 3.0988 | 2314.3764 | 932.4785
DEER-SFAM-CZ06-V1-eSH-10-HM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-HM | 10.9694 | 1.7785 | 761.3889 | 1464.1056 | 3.0988 | 2225.4945 | 911.9641
DEER-SFAM-CZ06-V1-eSH-10-LH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-LH | 10.4883 | 1.7264 | 763.8522 | 1623.3272 | 3.0988 | 2387.1794 | 927.8549
DEER-SFAM-CZ06-V1-eSH-10-LL-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-LL | 10.6045 | 1.8392 | 777.2811 | 1481.8169 | 3.0988 | 2259.0981 | 945.3581
DEER-SFAM-CZ06-V1-eSH-10-LM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-LM | 10.6213 | 1.7867 | 774.4657 | 1476.093 | 3.0988 | 2250.5587 | 928.4513
DEER-SFAM-CZ06-V1-eSH-10-MH-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-MH | 10.6245 | 1.7376 | 752.0465 | 1582.2273 | 3.0988 | 2334.2738 | 926.2337
DEER-SFAM-CZ06-V1-eSH-10-ML-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-ML | 10.71 | 1.826 | 765.8361 | 1379.6679 | 3.0988 | 2145.5041 | 918.7955
DEER-SFAM-CZ06-V1-eSH-10-MM-s1 | 10 | CZ06 | V1 | CZ06-V1-eSH-10 | CZ06-V1-eSH-10-MM | 10.9247 | 1.8057 | 772.9639 | 1522.9865 | 3.0988 | 2295.9504 | 919.9754
DEER-SFAM-CZ06-V1-eSH-13-HH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-HH | 13.9904 | 1.3283 | 575.4729 | 1445.7231 | 3.0988 | 2021.196 | 719.3355
DEER-SFAM-CZ06-V1-eSH-13-HL-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-HL | 13.5977 | 1.3611 | 570.3151 | 1245.9646 | 3.0988 | 1816.2796 | 713.1182
DEER-SFAM-CZ06-V1-eSH-13-HM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-HM | 14.0558 | 1.3438 | 576.5464 | 1285.5694 | 3.0988 | 1862.1158 | 705.5218
DEER-SFAM-CZ06-V1-eSH-13-LH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-LH | 13.5744 | 1.3309 | 576.1567 | 1491.4451 | 3.0988 | 2067.6018 | 794.1185
DEER-SFAM-CZ06-V1-eSH-13-LL-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-LL | 14.5661 | 1.3168 | 559.0797 | 1310.9841 | 3.0988 | 1870.0638 | 689.4698
DEER-SFAM-CZ06-V1-eSH-13-LM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-LM | 13.2585 | 1.4052 | 602.6339 | 1193.9075 | 3.0988 | 1796.5414 | 754.5439
DEER-SFAM-CZ06-V1-eSH-13-MH-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-MH | 14.4858 | 1.2345 | 545.8733 | 1448.6027 | 3.0988 | 1994.476 | 692.2637
DEER-SFAM-CZ06-V1-eSH-13-ML-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-ML | 13.7542 | 1.4064 | 591.9705 | 1385.0418 | 3.0988 | 1977.0122 | 742.1218
DEER-SFAM-CZ06-V1-eSH-13-MM-s1 | 13 | CZ06 | V1 | CZ06-V1-eSH-13 | CZ06-V1-eSH-13-MM | 14.6201 | 1.3223 | 559.7481 | 1356.9307 | 3.0988 | 1916.6788 | 677.075
DEER-SFAM-CZ06-V1-eSH-14-HH-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-HH | 14.9 | 1.2591 | 540.2607 | 1313.4045 | 3.0988 | 1853.6653 | 649.7314
DEER-SFAM-CZ06-V1-eSH-14-HL-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-HL | 14.8347 | 1.2917 | 540.2886 | 1280.9503 | 3.0988 | 1821.2389 | 672.4353
DEER-SFAM-CZ06-V1-eSH-14-HM-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-HM | 14.6244 | 1.278 | 546.6428 | 1266.1096 | 3.0988 | 1812.7524 | 639.7078
DEER-SFAM-CZ06-V1-eSH-14-MH-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-MH | 14.338 | 1.2494 | 542.4752 | 1342.995 | 3.0988 | 1885.4702 | 684.7496
DEER-SFAM-CZ06-V1-eSH-14-ML-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-ML | 14.9877 | 1.2639 | 525.4882 | 1408.6152 | 3.0988 | 1934.1035 | 704.9974
DEER-SFAM-CZ06-V1-eSH-14-MM-s1 | 14 | CZ06 | V1 | CZ06-V1-eSH-14 | CZ06-V1-eSH-14-MM | 14.4082 | 1.2672 | 538.0662 | 1250.6876 | 3.0988 | 1788.7539 | 663.219
DEER-SFAM-CZ06-V1-eSH-15-HH-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-HH | 15.7367 | 1.158 | 502.2888 | 1510.5898 | 3.0988 | 2012.8786 | 604.4964
DEER-SFAM-CZ06-V1-eSH-15-HL-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-HL | 15.8261 | 1.2006 | 507.2421 | 1107.3996 | 3.0988 | 1614.6416 | 608.5116
DEER-SFAM-CZ06-V1-eSH-15-HM-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-HM | 16.3463 | 1.1356 | 486.0924 | 1147.8039 | 3.0988 | 1633.8963 | 587.9542
DEER-SFAM-CZ06-V1-eSH-15-MH-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-MH | 16.4471 | 1.1392 | 481.3568 | 1363.951 | 3.0988 | 1845.3078 | 580.1426
DEER-SFAM-CZ06-V1-eSH-15-ML-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-ML | 16.0751 | 1.1805 | 491.7266 | 1233.6875 | 3.0988 | 1725.414 | 592.8948
DEER-SFAM-CZ06-V1-eSH-15-MM-s1 | 15 | CZ06 | V1 | CZ06-V1-eSH-15 | CZ06-V1-eSH-15-MM | 16.7169 | 1.1296 | 480.4284 | 1300.2732 | 3.0988 | 1780.7016 | 586.904
DEER-SFAM-CZ06-V1-eSH-16-CH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-CH | 17.3103 | 1.2429 | 554.9818 | 1290.8929 | 3.0988 | 1845.8747 | 636.2507
DEER-SFAM-CZ06-V1-eSH-16-CL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-CL | 17.497 | 1.2546 | 550.6306 | 1202.6579 | 3.0988 | 1753.2885 | 635.8224
DEER-SFAM-CZ06-V1-eSH-16-LH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-LH | 16.5656 | 1.1329 | 527.3123 | 1451.5105 | 3.0988 | 1978.8229 | 629.9504
DEER-SFAM-CZ06-V1-eSH-16-LL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-LL | 16.1475 | 1.2479 | 553.0677 | 1308.7455 | 3.0988 | 1861.8132 | 635.1518
DEER-SFAM-CZ06-V1-eSH-16-LM-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-LM | 15.9723 | 1.1948 | 550.6224 | 1448.6453 | 3.0988 | 1999.2677 | 665.4387
DEER-SFAM-CZ06-V1-eSH-16-TH-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-TH | 19.0651 | 1.0703 | 508.2456 | 1597.2347 | 3.0988 | 2105.4803 | 586.7957
DEER-SFAM-CZ06-V1-eSH-16-TL-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-TL | 18.1713 | 1.225 | 549.8962 | 1597.0649 | 3.0988 | 2146.961 | 619.9778
DEER-SFAM-CZ06-V1-eSH-16-TM-s2 | 16 | CZ06 | V1 | CZ06-V1-eSH-16 | CZ06-V1-eSH-16-TM | 18.3523 | 1.2114 | 544.4722 | 1628.5292 | 3.0988 | 2173.0015 | 616.2278
DEER-SFAM-CZ06-V1-eSH-17-CM-s2 | 17 | CZ06 | V1 | CZ06-V1-eSH-17 | CZ06-V1-eSH-17-CM | 18.5785 | 1.1829 | 518.7592 | 1396.7541 | 3.0988 | 1915.5132 | 621.6856
DEER-SFAM-CZ06-V1-eSH-17-LM-s2 | 17 | CZ06 | V1 | CZ06-V1-eSH-17 | CZ06-V1-eSH-17-LM | 17.4748 | 1.1537 | 512.2463 | 1274.685 | 3.0988 | 1786.9313 | 558.5229
DEER-SFAM-CZ06-V1-eSH-17-TH-s2 | 17 | CZ06 | V1 | CZ06-V1-eSH-17 | CZ06-V1-eSH-17-TH | 20.4454 | 1.0176 | 474.5323 | 1590.1458 | 3.0988 | 2064.6781 | 558.2405
DEER-SFAM-CZ06-V1-eSH-17-TL-s2 | 17 | CZ06 | V1 | CZ06-V1-eSH-17 | CZ06-V1-eSH-17-TL | 20.3041 | 1.0299 | 476.8169 | 1571.2222 | 3.0988 | 2048.0392 | 559.6173
DEER-SFAM-CZ06-V1-eSH-18-LH-s2 | 18 | CZ06 | V1 | CZ06-V1-eSH-18 | CZ06-V1-eSH-18-LH | 18.6748 | 1.0648 | 477.1407 | 1425.7542 | 3.0988 | 1902.8949 | 551.2455
DEER-SFAM-CZ06-V1-eSH-18-LL-s2 | 18 | CZ06 | V1 | CZ06-V1-eSH-18 | CZ06-V1-eSH-18-LL | 17.8734 | 1.1179 | 493.8755 | 1299.7361 | 3.0988 | 1793.6117 | 564.7467
DEER-SFAM-CZ06-V1-eSH-18-LM-s2 | 18 | CZ06 | V1 | CZ06-V1-eSH-18 | CZ06-V1-eSH-18-LM | 18.599 | 1.0652 | 481.9937 | 1496.584 | 3.0988 | 1978.5777 | 566.6378
DEER-SFAM-CZ06-V1-eSH-18-TM-s2 | 18 | CZ06 | V1 | CZ06-V1-eSH-18 | CZ06-V1-eSH-18-TM | 22.2659 | 0.93426 | 436.2385 | 1541.6505 | 3.0988 | 1977.889 | 558.6744
DEER-SFAM-CZ06-V2-eSA-10-HH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-HH | 10.9699 | 1.5735 | 527.1028 | 0 | 2.6219 | 527.1028 | 575.6498
DEER-SFAM-CZ06-V2-eSA-10-HL-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-HL | 10.9604 | 1.6041 | 517.3845 | 0 | 2.6219 | 517.3845 | 565.9919
DEER-SFAM-CZ06-V2-eSA-10-HM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-HM | 10.8131 | 1.6055 | 520.0555 | 0 | 2.6219 | 520.0555 | 568.6518
DEER-SFAM-CZ06-V2-eSA-10-LH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-LH | 10.7538 | 1.5313 | 502.1234 | 0 | 2.6219 | 502.1234 | 550.7917
DEER-SFAM-CZ06-V2-eSA-10-LL-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-LL | 10.5325 | 1.7345 | 534.2671 | 0 | 2.9329 | 534.2671 | 582.9483
DEER-SFAM-CZ06-V2-eSA-10-LM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-LM | 10.7486 | 1.5638 | 509.4271 | 0 | 2.6219 | 509.4271 | 558.0979
DEER-SFAM-CZ06-V2-eSA-10-MH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-MH | 10.7472 | 1.5102 | 509.7908 | 0 | 2.6219 | 509.7908 | 558.438
DEER-SFAM-CZ06-V2-eSA-10-ML-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-ML | 10.8451 | 1.6762 | 535.2077 | 0 | 2.6219 | 535.2077 | 583.8167
DEER-SFAM-CZ06-V2-eSA-10-MM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSA-10 | CZ06-V2-eSA-10-MM | 10.9566 | 1.5632 | 498.8094 | 0 | 2.6219 | 498.8094 | 547.4248
DEER-SFAM-CZ06-V2-eSA-13-HH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-HH | 13.2589 | 1.259 | 400.0495 | 0 | 2.9329 | 400.0495 | 443.9216
DEER-SFAM-CZ06-V2-eSA-13-HL-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-HL | 14.1042 | 1.2755 | 388.1917 | 0 | 2.6219 | 388.1917 | 426.5363
DEER-SFAM-CZ06-V2-eSA-13-HM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-HM | 13.7718 | 1.2627 | 394.524 | 0 | 2.9329 | 394.524 | 438.3751
DEER-SFAM-CZ06-V2-eSA-13-LH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-LH | 13.8417 | 1.1575 | 386.1253 | 0 | 2.6219 | 386.1253 | 434.7511
DEER-SFAM-CZ06-V2-eSA-13-LL-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-LL | 14.023 | 1.2408 | 400.3068 | 0 | 2.6219 | 400.3068 | 448.7881
DEER-SFAM-CZ06-V2-eSA-13-LM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-LM | 13.6216 | 1.2185 | 403.3798 | 0 | 2.6219 | 403.3798 | 451.9456
DEER-SFAM-CZ06-V2-eSA-13-MH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-MH | 14.9321 | 1.1424 | 374.6688 | 0 | 2.6219 | 374.6688 | 423.2658
DEER-SFAM-CZ06-V2-eSA-13-ML-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-ML | 13.8889 | 1.2503 | 391.0164 | 0 | 2.6219 | 391.0164 | 439.4542
DEER-SFAM-CZ06-V2-eSA-13-MM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSA-13 | CZ06-V2-eSA-13-MM | 14.8749 | 1.1681 | 374.8013 | 0 | 2.6219 | 374.8013 | 423.3871
DEER-SFAM-CZ06-V2-eSA-14-HH-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-HH | 14.522 | 1.1325 | 374.0185 | 0 | 2.6219 | 374.0185 | 414.7412
DEER-SFAM-CZ06-V2-eSA-14-HL-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-HL | 15.1913 | 1.1118 | 358.0712 | 0 | 2.6219 | 358.0712 | 388.0185
DEER-SFAM-CZ06-V2-eSA-14-HM-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-HM | 15.2658 | 1.1511 | 357.6929 | 0 | 2.6219 | 357.6929 | 403.6524
DEER-SFAM-CZ06-V2-eSA-14-MH-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-MH | 14.5769 | 1.1313 | 382.933 | 0 | 2.6219 | 382.933 | 414.8513
DEER-SFAM-CZ06-V2-eSA-14-ML-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-ML | 14.6547 | 1.1678 | 365.484 | 0 | 2.6219 | 365.484 | 416.4808
DEER-SFAM-CZ06-V2-eSA-14-MM-s1 | 14 | CZ06 | V2 | CZ06-V2-eSA-14 | CZ06-V2-eSA-14-MM | 14.6936 | 1.1024 | 369.9001 | 0 | 2.6219 | 369.9001 | 404.9025
DEER-SFAM-CZ06-V2-eSA-15-HH-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-HH | 16.0522 | 1.0588 | 336.1294 | 0 | 2.9329 | 336.1294 | 370.1287
DEER-SFAM-CZ06-V2-eSA-15-HL-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-HL | 16.5137 | 1.058 | 329.7332 | 0 | 2.9329 | 329.7332 | 372.097
DEER-SFAM-CZ06-V2-eSA-15-HM-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-HM | 15.8075 | 1.0481 | 339.881 | 0 | 2.9329 | 339.881 | 374.003
DEER-SFAM-CZ06-V2-eSA-15-MH-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-MH | 16.1894 | 1.016 | 333.928 | 0 | 2.6219 | 333.928 | 359.2319
DEER-SFAM-CZ06-V2-eSA-15-ML-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-ML | 16.5579 | 1.0544 | 339.6396 | 0 | 2.6219 | 339.6396 | 373.6293
DEER-SFAM-CZ06-V2-eSA-15-MM-s1 | 15 | CZ06 | V2 | CZ06-V2-eSA-15 | CZ06-V2-eSA-15-MM | 16.0539 | 1.0918 | 338.8634 | 0 | 2.6219 | 338.8634 | 369.8887
DEER-SFAM-CZ06-V2-eSA-16-CH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-CH | 16.8064 | 1.1598 | 382.3578 | 0 | 2.9329 | 382.3578 | 401.8996
DEER-SFAM-CZ06-V2-eSA-16-CL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-CL | 17.2942 | 1.0992 | 361.1586 | 0 | 2.9329 | 361.1586 | 385.888
DEER-SFAM-CZ06-V2-eSA-16-CM-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-CM | 16.9762 | 1.1176 | 367.8354 | 0 | 2.9329 | 367.8354 | 393.9097
DEER-SFAM-CZ06-V2-eSA-16-LH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-LH | 16.5305 | 1.0217 | 357.0844 | 0 | 2.6219 | 357.0844 | 390.6281
DEER-SFAM-CZ06-V2-eSA-16-LL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-LL | 16.0566 | 1.0607 | 368.9399 | 0 | 2.6219 | 368.9399 | 390.9783
DEER-SFAM-CZ06-V2-eSA-16-LM-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-LM | 16.0775 | 1.0698 | 370.0138 | 0 | 2.6219 | 370.0138 | 389.9917
DEER-SFAM-CZ06-V2-eSA-16-NM-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-NM | 17.2597 | 1.0662 | 363.2704 | 0 | 2.6219 | 363.2704 | 382.8613
DEER-SFAM-CZ06-V2-eSA-16-TH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-TH | 17.8513 | 1.0314 | 369.5721 | 0 | 2.6219 | 369.5721 | 382.1111
DEER-SFAM-CZ06-V2-eSA-16-TL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSA-16 | CZ06-V2-eSA-16-TL | 18.21 | 1.0722 | 366.7629 | 0 | 2.9329 | 366.7629 | 380.3389
DEER-SFAM-CZ06-V2-eSA-17-CH-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-CH | 18.0089 | 1.0752 | 353.242 | 0 | 2.9329 | 353.242 | 377.9516
DEER-SFAM-CZ06-V2-eSA-17-CL-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-CL | 18.0198 | 1.0816 | 353.0407 | 0 | 2.9329 | 353.0407 | 377.7454
DEER-SFAM-CZ06-V2-eSA-17-CM-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-CM | 18.1082 | 1.0865 | 355.2594 | 0 | 2.9329 | 355.2594 | 374.7443
DEER-SFAM-CZ06-V2-eSA-17-LH-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-LH | 17.2279 | 0.9731 | 338.3803 | 0 | 2.6219 | 338.3803 | 364.6673
DEER-SFAM-CZ06-V2-eSA-17-LL-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-LL | 17.1586 | 1.0269 | 350.9433 | 0 | 2.6219 | 350.9433 | 365.2826
DEER-SFAM-CZ06-V2-eSA-17-LM-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-LM | 16.9221 | 1.0127 | 354.262 | 0 | 2.6219 | 354.262 | 366.6323
DEER-SFAM-CZ06-V2-eSA-17-TH-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-TH | 20.5137 | 0.89097 | 314.8492 | 0 | 2.6219 | 314.8492 | 334.9067
DEER-SFAM-CZ06-V2-eSA-17-TL-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-TL | 21.0479 | 0.92302 | 302.695 | 0 | 2.6219 | 302.695 | 333.9885
DEER-SFAM-CZ06-V2-eSA-17-TM-s2 | 17 | CZ06 | V2 | CZ06-V2-eSA-17 | CZ06-V2-eSA-17-TM | 19.4703 | 1.0303 | 357.5709 | 0 | 2.9329 | 357.5709 | 368.0988
DEER-SFAM-CZ06-V2-eSA-18-LH-s2 | 18 | CZ06 | V2 | CZ06-V2-eSA-18 | CZ06-V2-eSA-18-LH | 18.147 | 0.94492 | 330.0523 | 0 | 2.6219 | 330.0523 | 347.2801
DEER-SFAM-CZ06-V2-eSA-18-LL-s2 | 18 | CZ06 | V2 | CZ06-V2-eSA-18 | CZ06-V2-eSA-18-LL | 18.459 | 0.97065 | 321.6208 | 0 | 2.6219 | 321.6208 | 344.1058
DEER-SFAM-CZ06-V2-eSA-18-TH-s2 | 18 | CZ06 | V2 | CZ06-V2-eSA-18 | CZ06-V2-eSA-18-TH | 20.9122 | 0.85081 | 307.9331 | 0 | 2.6219 | 307.9331 | 321.5693
DEER-SFAM-CZ06-V2-eSA-18-TL-s2 | 18 | CZ06 | V2 | CZ06-V2-eSA-18 | CZ06-V2-eSA-18-TL | 20.5399 | 0.90454 | 315.8617 | 0 | 2.6219 | 315.8617 | 330.827
DEER-SFAM-CZ06-V2-eSA-18-TM-s2 | 18 | CZ06 | V2 | CZ06-V2-eSA-18 | CZ06-V2-eSA-18-TM | 20.1843 | 0.88997 | 319.4782 | 0 | 2.6219 | 319.4782 | 333.407
DEER-SFAM-CZ06-V2-eSH-10-HH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-HH | 10.5174 | 1.5998 | 513.9475 | 914.6853 | 2.9329 | 1428.6328 | 608.1103
DEER-SFAM-CZ06-V2-eSH-10-HL-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-HL | 10.5509 | 1.5956 | 522.2261 | 919.0635 | 2.6219 | 1441.2897 | 616.6878
DEER-SFAM-CZ06-V2-eSH-10-HM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-HM | 11.0888 | 1.5655 | 513.6646 | 881.6681 | 2.6219 | 1395.3327 | 603.2733
DEER-SFAM-CZ06-V2-eSH-10-LH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-LH | 10.7033 | 1.4955 | 512.0937 | 967.5473 | 2.6219 | 1479.641 | 609.6431
DEER-SFAM-CZ06-V2-eSH-10-LL-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-LL | 10.7434 | 1.6148 | 523.6834 | 887.5093 | 2.6219 | 1411.1927 | 623.9197
DEER-SFAM-CZ06-V2-eSH-10-LM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-LM | 10.7875 | 1.5634 | 520.0908 | 885.9992 | 2.6219 | 1406.0901 | 612.0732
DEER-SFAM-CZ06-V2-eSH-10-MH-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-MH | 10.8244 | 1.5115 | 505.8702 | 942.7451 | 2.6219 | 1448.6153 | 609.4586
DEER-SFAM-CZ06-V2-eSH-10-ML-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-ML | 10.8128 | 1.6116 | 517.5738 | 827.6012 | 2.6219 | 1345.1749 | 609.0966
DEER-SFAM-CZ06-V2-eSH-10-MM-s1 | 10 | CZ06 | V2 | CZ06-V2-eSH-10 | CZ06-V2-eSH-10-MM | 11.0147 | 1.5902 | 522.761 | 910.5436 | 2.6219 | 1433.3046 | 610.5136
DEER-SFAM-CZ06-V2-eSH-13-HH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-HH | 14.1641 | 1.1644 | 388.1499 | 865.3959 | 2.6219 | 1253.5458 | 473.8276
DEER-SFAM-CZ06-V2-eSH-13-HL-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-HL | 13.5715 | 1.2477 | 389.4503 | 746.9196 | 2.9329 | 1136.37 | 474.7727
DEER-SFAM-CZ06-V2-eSH-13-HM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-HM | 14.1995 | 1.1835 | 389.2105 | 770.4869 | 2.6219 | 1159.6974 | 466.1918
DEER-SFAM-CZ06-V2-eSH-13-LH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-LH | 13.8152 | 1.1601 | 387.9771 | 882.3229 | 2.6219 | 1270.3 | 517.0203
DEER-SFAM-CZ06-V2-eSH-13-LL-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-LL | 14.7226 | 1.1582 | 377.1604 | 782.212 | 2.6219 | 1159.3724 | 454.934
DEER-SFAM-CZ06-V2-eSH-13-LM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-LM | 13.4346 | 1.2331 | 406.4625 | 710.1165 | 2.6219 | 1116.579 | 496.9081
DEER-SFAM-CZ06-V2-eSH-13-MH-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-MH | 14.4614 | 1.1322 | 373.9362 | 874.2595 | 2.9329 | 1248.1957 | 461.124
DEER-SFAM-CZ06-V2-eSH-13-ML-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-ML | 13.8706 | 1.247 | 400.1655 | 817.6724 | 2.6219 | 1217.8379 | 489.357
DEER-SFAM-CZ06-V2-eSH-13-MM-s1 | 13 | CZ06 | V2 | CZ06-V2-eSH-13 | CZ06-V2-eSH-13-MM | 14.7382 | 1.1612 | 377.9267 | 811.2972 | 2.6219 | 1189.2238 | 447.8346
DEER-SFAM-CZ06-V2-eSH-14-HH-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-HH | 15.0464 | 1.0975 | 364.834 | 786.7737 | 2.6219 | 1151.6077 | 430.072
DEER-SFAM-CZ06-V2-eSH-14-HL-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-HL | 14.8783 | 1.1834 | 369.0767 | 766.8844 | 2.9329 | 1135.961 | 447.8336
DEER-SFAM-CZ06-V2-eSH-14-HM-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-HM | 14.7944 | 1.1141 | 368.6129 | 757.1086 | 2.6219 | 1125.7215 | 424.094
DEER-SFAM-CZ06-V2-eSH-14-MH-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-MH | 14.6043 | 1.0846 | 364.866 | 796.6292 | 2.6219 | 1161.4952 | 449.4225
DEER-SFAM-CZ06-V2-eSH-14-ML-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-ML | 15.1389 | 1.1568 | 354.3171 | 826.0542 | 2.6219 | 1180.3713 | 460.4877
DEER-SFAM-CZ06-V2-eSH-14-MM-s1 | 14 | CZ06 | V2 | CZ06-V2-eSH-14 | CZ06-V2-eSH-14-MM | 14.5796 | 1.1053 | 363.9623 | 743.646 | 2.6219 | 1107.6083 | 438.3098
DEER-SFAM-CZ06-V2-eSH-15-HH-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-HH | 15.7235 | 1.0407 | 342.7038 | 898.2851 | 2.9329 | 1240.9889 | 403.4664
DEER-SFAM-CZ06-V2-eSH-15-HL-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-HL | 15.8717 | 1.1003 | 345.6431 | 666.3912 | 2.9329 | 1012.0343 | 406.1195
DEER-SFAM-CZ06-V2-eSH-15-HM-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-HM | 16.3068 | 1.0422 | 332.6105 | 693.8599 | 2.9329 | 1026.4704 | 393.2267
DEER-SFAM-CZ06-V2-eSH-15-MH-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-MH | 16.5901 | 1.0047 | 324.9259 | 800.0839 | 2.6219 | 1125.0098 | 383.3398
DEER-SFAM-CZ06-V2-eSH-15-ML-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-ML | 16.2186 | 1.0708 | 331.7307 | 727.1535 | 2.6219 | 1058.8842 | 391.6953
DEER-SFAM-CZ06-V2-eSH-15-MM-s1 | 15 | CZ06 | V2 | CZ06-V2-eSH-15 | CZ06-V2-eSH-15-MM | 16.6368 | 1.0167 | 328.1113 | 777.3345 | 2.9329 | 1105.4457 | 391.6538
DEER-SFAM-CZ06-V2-eSH-16-CH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-CH | 17.1616 | 1.1205 | 373.7499 | 749.8649 | 2.9329 | 1123.6147 | 422.0477
DEER-SFAM-CZ06-V2-eSH-16-CL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-CL | 17.348 | 1.1323 | 371.0727 | 698.2075 | 2.9329 | 1069.2802 | 421.8408
DEER-SFAM-CZ06-V2-eSH-16-LH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-LH | 16.353 | 1.0235 | 360.8793 | 860.6678 | 2.9329 | 1221.5471 | 421.7495
DEER-SFAM-CZ06-V2-eSH-16-LL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-LL | 16.1083 | 1.0806 | 371.6504 | 761.5876 | 2.6219 | 1133.238 | 420.4395
DEER-SFAM-CZ06-V2-eSH-16-LM-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-LM | 16.0193 | 1.0337 | 368.4452 | 846.702 | 2.6219 | 1215.1473 | 436.5321
DEER-SFAM-CZ06-V2-eSH-16-TH-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-TH | 18.7226 | 0.96149 | 346.3512 | 932.4407 | 2.9329 | 1278.792 | 392.4216
DEER-SFAM-CZ06-V2-eSH-16-TL-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-TL | 17.8868 | 1.0845 | 368.6281 | 908.4638 | 2.6219 | 1277.0919 | 410.6602
DEER-SFAM-CZ06-V2-eSH-16-TM-s2 | 16 | CZ06 | V2 | CZ06-V2-eSH-16 | CZ06-V2-eSH-16-TM | 18.0704 | 1.0689 | 364.8843 | 927.4603 | 2.6219 | 1292.3445 | 407.8702
DEER-SFAM-CZ06-V2-eSH-17-CM-s2 | 17 | CZ06 | V2 | CZ06-V2-eSH-17 | CZ06-V2-eSH-17-CM | 18.4306 | 1.068 | 348.5522 | 790.3559 | 2.9329 | 1138.9081 | 408.3412
DEER-SFAM-CZ06-V2-eSH-17-LM-s2 | 17 | CZ06 | V2 | CZ06-V2-eSH-17 | CZ06-V2-eSH-17-LM | 17.2558 | 1.0135 | 349.4522 | 746.7734 | 2.9329 | 1096.2256 | 376.9516
DEER-SFAM-CZ06-V2-eSH-17-TH-s2 | 17 | CZ06 | V2 | CZ06-V2-eSH-17 | CZ06-V2-eSH-17-TH | 20.0574 | 0.91657 | 323.7614 | 923.858 | 2.9329 | 1247.6194 | 372.6025
DEER-SFAM-CZ06-V2-eSH-17-TL-s2 | 17 | CZ06 | V2 | CZ06-V2-eSH-17 | CZ06-V2-eSH-17-TL | 19.9464 | 0.92755 | 325.0039 | 909.3507 | 2.9329 | 1234.3546 | 373.3803
DEER-SFAM-CZ06-V2-eSH-18-LH-s2 | 18 | CZ06 | V2 | CZ06-V2-eSH-18 | CZ06-V2-eSH-18-LH | 18.5889 | 0.94293 | 321.8517 | 822.803 | 2.6219 | 1144.6547 | 365.9725
DEER-SFAM-CZ06-V2-eSH-18-LL-s2 | 18 | CZ06 | V2 | CZ06-V2-eSH-18 | CZ06-V2-eSH-18-LL | 17.7505 | 0.96886 | 332.9303 | 754.4408 | 2.6219 | 1087.371 | 375.0054
DEER-SFAM-CZ06-V2-eSH-18-LM-s2 | 18 | CZ06 | V2 | CZ06-V2-eSH-18 | CZ06-V2-eSH-18-LM | 18.5248 | 0.95277 | 324.9006 | 862.3029 | 2.6219 | 1187.2035 | 375.302
DEER-SFAM-CZ06-V2-eSH-18-TM-s2 | 18 | CZ06 | V2 | CZ06-V2-eSH-18 | CZ06-V2-eSH-18-TM | 22.0274 | 0.84687 | 293.6189 | 884.4762 | 2.6219 | 1178.0951 | 366.3334
DEER-SFAM-CZ06-V3-eSA-10-HH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-HH | 11.0885 | 2.2554 | 1142.4181 | 0 | 2.8 | 1142.4181 | 1166.2776
DEER-SFAM-CZ06-V3-eSA-10-HL-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-HL | 11.1453 | 2.3181 | 1135.7464 | 0 | 2.8 | 1135.7464 | 1159.6391
DEER-SFAM-CZ06-V3-eSA-10-HM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-HM | 10.9981 | 2.3287 | 1143.7759 | 0 | 2.8 | 1143.7759 | 1167.6628
DEER-SFAM-CZ06-V3-eSA-10-LH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-LH | 10.7461 | 2.2502 | 1116.0381 | 0 | 2.8 | 1116.0381 | 1139.9646
DEER-SFAM-CZ06-V3-eSA-10-LL-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-LL | 10.6896 | 2.4391 | 1180.6284 | 0 | 2.8 | 1180.6284 | 1204.5289
DEER-SFAM-CZ06-V3-eSA-10-LM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-LM | 10.7104 | 2.2862 | 1131.7981 | 0 | 2.8 | 1131.7981 | 1155.726
DEER-SFAM-CZ06-V3-eSA-10-MH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-MH | 10.8337 | 2.1981 | 1119.5424 | 0 | 2.8 | 1119.5424 | 1143.4573
DEER-SFAM-CZ06-V3-eSA-10-ML-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-ML | 10.9776 | 2.4336 | 1179.2403 | 0 | 2.8 | 1179.2403 | 1203.134
DEER-SFAM-CZ06-V3-eSA-10-MM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSA-10 | CZ06-V3-eSA-10-MM | 11.0453 | 2.26 | 1100.709 | 0 | 2.8 | 1100.709 | 1124.6061
DEER-SFAM-CZ06-V3-eSA-13-HH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-HH | 13.554 | 1.757 | 878.86 | 0 | 2.8 | 878.86 | 900.3988
DEER-SFAM-CZ06-V3-eSA-13-HL-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-HL | 14.0362 | 1.8409 | 869.6706 | 0 | 2.8 | 869.6706 | 888.5192
DEER-SFAM-CZ06-V3-eSA-13-HM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-HM | 13.8298 | 1.8914 | 890.8877 | 0 | 3.2 | 890.8877 | 912.449
DEER-SFAM-CZ06-V3-eSA-13-LH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-LH | 13.8571 | 1.688 | 862.0459 | 0 | 2.8 | 862.0459 | 885.9487
DEER-SFAM-CZ06-V3-eSA-13-LL-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-LL | 13.9633 | 1.7981 | 888.141 | 0 | 2.8 | 888.141 | 911.9649
DEER-SFAM-CZ06-V3-eSA-13-LM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-LM | 13.6039 | 1.7862 | 895.0927 | 0 | 2.8 | 895.0927 | 918.9623
DEER-SFAM-CZ06-V3-eSA-13-MH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-MH | 15.1349 | 1.6357 | 819.3755 | 0 | 2.8 | 819.3755 | 843.2624
DEER-SFAM-CZ06-V3-eSA-13-ML-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-ML | 13.7826 | 1.8083 | 875.357 | 0 | 2.8 | 875.357 | 899.1641
DEER-SFAM-CZ06-V3-eSA-13-MM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSA-13 | CZ06-V3-eSA-13-MM | 15.1271 | 1.6675 | 822.0675 | 0 | 2.8 | 822.0675 | 845.9487
DEER-SFAM-CZ06-V3-eSA-14-HH-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-HH | 14.4847 | 1.6743 | 830.9705 | 0 | 2.8 | 830.9705 | 850.9868
DEER-SFAM-CZ06-V3-eSA-14-HL-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-HL | 15.1995 | 1.6692 | 804.6287 | 0 | 2.8 | 804.6287 | 819.3495
DEER-SFAM-CZ06-V3-eSA-14-HM-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-HM | 15.1309 | 1.6764 | 803.3452 | 0 | 2.8 | 803.3452 | 825.9376
DEER-SFAM-CZ06-V3-eSA-14-MH-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-MH | 14.5692 | 1.6503 | 845.3209 | 0 | 2.8 | 845.3209 | 861.0088
DEER-SFAM-CZ06-V3-eSA-14-ML-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-ML | 14.5143 | 1.693 | 818.9999 | 0 | 2.8 | 818.9999 | 844.0667
DEER-SFAM-CZ06-V3-eSA-14-MM-s1 | 14 | CZ06 | V3 | CZ06-V3-eSA-14 | CZ06-V3-eSA-14-MM | 14.7115 | 1.6102 | 819.3921 | 0 | 2.8 | 819.3921 | 836.597
DEER-SFAM-CZ06-V3-eSA-15-HH-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-HH | 16.3028 | 1.5465 | 748.0253 | 0 | 3.2 | 748.0253 | 764.7441
DEER-SFAM-CZ06-V3-eSA-15-HL-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-HL | 16.7497 | 1.4757 | 725.4476 | 0 | 2.8 | 725.4476 | 746.2416
DEER-SFAM-CZ06-V3-eSA-15-HM-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-HM | 15.9525 | 1.5962 | 764.944 | 0 | 3.2 | 764.944 | 781.7223
DEER-SFAM-CZ06-V3-eSA-15-MH-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-MH | 16.3242 | 1.5133 | 742.3066 | 0 | 2.8 | 742.3066 | 754.7457
DEER-SFAM-CZ06-V3-eSA-15-ML-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-ML | 16.5865 | 1.5381 | 751.2069 | 0 | 2.8 | 751.2069 | 767.9096
DEER-SFAM-CZ06-V3-eSA-15-MM-s1 | 15 | CZ06 | V3 | CZ06-V3-eSA-15 | CZ06-V3-eSA-15-MM | 16.0275 | 1.5688 | 758.5991 | 0 | 2.8 | 758.5991 | 773.8506
DEER-SFAM-CZ06-V3-eSA-16-CH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-CH | 16.7356 | 1.7036 | 825.4126 | 0 | 3.2 | 825.4126 | 835.0126
DEER-SFAM-CZ06-V3-eSA-16-CL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-CL | 17.3585 | 1.6269 | 778.2239 | 0 | 3.2 | 778.2239 | 790.363
DEER-SFAM-CZ06-V3-eSA-16-CM-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-CM | 16.9521 | 1.6482 | 798.7007 | 0 | 3.2 | 798.7007 | 811.4907
DEER-SFAM-CZ06-V3-eSA-16-LH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-LH | 17.2969 | 1.4633 | 744.5222 | 0 | 2.8 | 744.5222 | 761.0345
DEER-SFAM-CZ06-V3-eSA-16-LL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-LL | 16.5486 | 1.5368 | 776.3422 | 0 | 2.8 | 776.3422 | 787.1776
DEER-SFAM-CZ06-V3-eSA-16-LM-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-LM | 16.4272 | 1.5501 | 784.7763 | 0 | 2.8 | 784.7763 | 794.5969
DEER-SFAM-CZ06-V3-eSA-16-NM-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-NM | 17.2457 | 1.5629 | 785.8112 | 0 | 2.8 | 785.8112 | 795.4451
DEER-SFAM-CZ06-V3-eSA-16-TH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-TH | 18.5341 | 1.4334 | 746.8756 | 0 | 2.8 | 746.8756 | 753.0474
DEER-SFAM-CZ06-V3-eSA-16-TL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSA-16 | CZ06-V3-eSA-16-TL | 18.8686 | 1.4785 | 739.4332 | 0 | 2.8 | 739.4332 | 746.0989
DEER-SFAM-CZ06-V3-eSA-17-CH-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-CH | 17.9284 | 1.587 | 761.5668 | 0 | 3.2 | 761.5668 | 773.6954
DEER-SFAM-CZ06-V3-eSA-17-CL-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-CL | 17.9189 | 1.6025 | 762.1667 | 0 | 3.2 | 762.1667 | 774.2929
DEER-SFAM-CZ06-V3-eSA-17-CM-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-CM | 18.0273 | 1.6044 | 768.472 | 0 | 3.2 | 768.472 | 778.0446
DEER-SFAM-CZ06-V3-eSA-17-LH-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-LH | 17.8579 | 1.4108 | 712.4332 | 0 | 2.8 | 712.4332 | 725.3743
DEER-SFAM-CZ06-V3-eSA-17-LL-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-LL | 17.6052 | 1.4577 | 738.6576 | 0 | 2.8 | 738.6576 | 745.7064
DEER-SFAM-CZ06-V3-eSA-17-LM-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-LM | 17.3281 | 1.46 | 749.1759 | 0 | 2.8 | 749.1759 | 755.2554
DEER-SFAM-CZ06-V3-eSA-17-TH-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-TH | 21.3807 | 1.2375 | 636.7772 | 0 | 2.8 | 636.7772 | 646.6504
DEER-SFAM-CZ06-V3-eSA-17-TL-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-TL | 21.4204 | 1.2826 | 627.7693 | 0 | 2.8 | 627.7693 | 643.125
DEER-SFAM-CZ06-V3-eSA-17-TM-s2 | 17 | CZ06 | V3 | CZ06-V3-eSA-17 | CZ06-V3-eSA-17-TM | 20.2284 | 1.3977 | 711.6629 | 0 | 2.8 | 711.6629 | 716.8367
DEER-SFAM-CZ06-V3-eSA-18-LH-s2 | 18 | CZ06 | V3 | CZ06-V3-eSA-18 | CZ06-V3-eSA-18-LH | 18.7297 | 1.358 | 691.8824 | 0 | 2.8 | 691.8824 | 700.3503
DEER-SFAM-CZ06-V3-eSA-18-LL-s2 | 18 | CZ06 | V3 | CZ06-V3-eSA-18 | CZ06-V3-eSA-18-LL | 18.8954 | 1.3684 | 679.0269 | 0 | 2.8 | 679.0269 | 690.0831
DEER-SFAM-CZ06-V3-eSA-18-TH-s2 | 18 | CZ06 | V3 | CZ06-V3-eSA-18 | CZ06-V3-eSA-18-TH | 21.974 | 1.1817 | 621.5725 | 0 | 2.8 | 621.5725 | 628.2786
DEER-SFAM-CZ06-V3-eSA-18-TL-s2 | 18 | CZ06 | V3 | CZ06-V3-eSA-18 | CZ06-V3-eSA-18-TL | 21.2808 | 1.254 | 643.428 | 0 | 2.8 | 643.428 | 650.7886
DEER-SFAM-CZ06-V3-eSA-18-TM-s2 | 18 | CZ06 | V3 | CZ06-V3-eSA-18 | CZ06-V3-eSA-18-TM | 20.9689 | 1.2372 | 648.103 | 0 | 2.8 | 648.103 | 654.9568
DEER-SFAM-CZ06-V3-eSH-10-HH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-HH | 10.7307 | 2.1981 | 1115.3566 | 444.4964 | 2.8 | 1559.853 | 1161.053
DEER-SFAM-CZ06-V3-eSH-10-HL-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-HL | 10.5335 | 2.3102 | 1155.4702 | 448.4928 | 2.8 | 1603.963 | 1201.263
DEER-SFAM-CZ06-V3-eSH-10-HM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-HM | 11.184 | 2.2594 | 1123.6897 | 435.7893 | 2.8 | 1559.479 | 1167.179
DEER-SFAM-CZ06-V3-eSH-10-LH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-LH | 10.8316 | 2.1728 | 1127.7238 | 473.3276 | 2.8 | 1601.0514 | 1175.0514
DEER-SFAM-CZ06-V3-eSH-10-LL-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-LL | 10.7547 | 2.3497 | 1157.6572 | 435.0781 | 2.8 | 1592.7353 | 1206.4353
DEER-SFAM-CZ06-V3-eSH-10-LM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-LM | 10.8965 | 2.2652 | 1140.8318 | 436.45 | 2.8 | 1577.2818 | 1185.6818
DEER-SFAM-CZ06-V3-eSH-10-MH-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-MH | 10.8839 | 2.199 | 1114.9874 | 460.4306 | 2.8 | 1575.418 | 1165.218
DEER-SFAM-CZ06-V3-eSH-10-ML-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-ML | 10.8293 | 2.3609 | 1148.5764 | 406.8244 | 2.8 | 1555.4008 | 1193.3008
DEER-SFAM-CZ06-V3-eSH-10-MM-s1 | 10 | CZ06 | V3 | CZ06-V3-eSH-10 | CZ06-V3-eSH-10-MM | 11.1366 | 2.2719 | 1134.8163 | 445.7388 | 2.8 | 1580.5551 | 1177.5551
DEER-SFAM-CZ06-V3-eSH-13-HH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-HH | 14.3611 | 1.6884 | 854.5177 | 425.5472 | 2.8 | 1280.0649 | 896.1649
DEER-SFAM-CZ06-V3-eSH-13-HL-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-HL | 13.6712 | 1.87 | 878.253 | 365.3308 | 3.2 | 1243.5838 | 919.7838
DEER-SFAM-CZ06-V3-eSH-13-HM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-HM | 14.3676 | 1.718 | 858.209 | 378.8155 | 2.8 | 1237.0245 | 895.7245
DEER-SFAM-CZ06-V3-eSH-13-LH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-LH | 13.8635 | 1.6966 | 859.6763 | 429.3592 | 2.8 | 1289.0355 | 921.9355
DEER-SFAM-CZ06-V3-eSH-13-LL-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-LL | 14.8903 | 1.6828 | 831.8601 | 382.1706 | 2.8 | 1214.0307 | 869.7307
DEER-SFAM-CZ06-V3-eSH-13-LM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-LM | 13.4047 | 1.8142 | 903.5293 | 345.4089 | 2.8 | 1248.9382 | 947.4382
DEER-SFAM-CZ06-V3-eSH-13-MH-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-MH | 15.0558 | 1.5614 | 802.6023 | 425.7227 | 2.8 | 1228.325 | 844.725
DEER-SFAM-CZ06-V3-eSH-13-ML-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-ML | 13.8078 | 1.835 | 889.4813 | 394.4073 | 2.8 | 1283.8886 | 932.6886
DEER-SFAM-CZ06-V3-eSH-13-MM-s1 | 13 | CZ06 | V3 | CZ06-V3-eSH-13 | CZ06-V3-eSH-13-MM | 14.8458 | 1.6864 | 833.1864 | 397.3758 | 2.8 | 1230.5622 | 867.1622
DEER-SFAM-CZ06-V3-eSH-14-HH-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-HH | 15.1822 | 1.6094 | 807.7108 | 386.633 | 2.8 | 1194.3438 | 839.4438
DEER-SFAM-CZ06-V3-eSH-14-HL-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-HL | 14.9617 | 1.6737 | 817.7452 | 373.115 | 2.8 | 1190.8602 | 855.8602
DEER-SFAM-CZ06-V3-eSH-14-HM-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-HM | 14.8789 | 1.635 | 818.7624 | 371.2079 | 2.8 | 1189.9703 | 845.7703
DEER-SFAM-CZ06-V3-eSH-14-MH-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-MH | 14.6373 | 1.5854 | 810.6494 | 388.5004 | 2.8 | 1199.1498 | 851.6498
DEER-SFAM-CZ06-V3-eSH-14-ML-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-ML | 15.0046 | 1.6664 | 799.5382 | 397.0813 | 2.8 | 1196.6195 | 850.7195
DEER-SFAM-CZ06-V3-eSH-14-MM-s1 | 14 | CZ06 | V3 | CZ06-V3-eSH-14 | CZ06-V3-eSH-14-MM | 14.4726 | 1.6382 | 816.1317 | 361.9146 | 2.8 | 1178.0463 | 852.1463
DEER-SFAM-CZ06-V3-eSH-15-HH-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-HH | 16.1383 | 1.4818 | 750.4956 | 432.3722 | 2.8 | 1182.8678 | 779.7678
DEER-SFAM-CZ06-V3-eSH-15-HL-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-HL | 16.0168 | 1.5516 | 763.5853 | 325.4436 | 2.8 | 1089.0289 | 792.9289
DEER-SFAM-CZ06-V3-eSH-15-HM-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-HM | 16.6114 | 1.466 | 729.4724 | 340.3738 | 2.8 | 1069.8462 | 758.7462
DEER-SFAM-CZ06-V3-eSH-15-MH-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-MH | 16.5599 | 1.4968 | 726.9839 | 384.0505 | 2.8 | 1111.0344 | 755.1344
DEER-SFAM-CZ06-V3-eSH-15-ML-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-ML | 16.0756 | 1.5632 | 749.0159 | 351.0807 | 2.8 | 1100.0966 | 777.9966
DEER-SFAM-CZ06-V3-eSH-15-MM-s1 | 15 | CZ06 | V3 | CZ06-V3-eSH-15 | CZ06-V3-eSH-15-MM | 16.8994 | 1.5281 | 732.2304 | 379.5904 | 3.2 | 1111.8208 | 763.1208
DEER-SFAM-CZ06-V3-eSH-16-CH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-CH | 17.2335 | 1.6437 | 801.0923 | 353.866 | 3.2 | 1154.9583 | 824.2583
DEER-SFAM-CZ06-V3-eSH-16-CL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-CL | 17.3143 | 1.6675 | 798.8192 | 329.227 | 3.2 | 1128.0462 | 823.2462
DEER-SFAM-CZ06-V3-eSH-16-LH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-LH | 17.5166 | 1.3961 | 729.9985 | 406.49 | 2.8 | 1136.4885 | 759.1885
DEER-SFAM-CZ06-V3-eSH-16-LL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-LL | 16.4452 | 1.5733 | 792.922 | 360.4753 | 2.8 | 1153.3973 | 816.3973
DEER-SFAM-CZ06-V3-eSH-16-LM-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-LM | 16.6808 | 1.4922 | 773.1884 | 404.0297 | 2.8 | 1177.2181 | 805.8181
DEER-SFAM-CZ06-V3-eSH-16-TH-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-TH | 20.0065 | 1.4027 | 695.3593 | 440.4032 | 3.2 | 1135.7625 | 716.9625
DEER-SFAM-CZ06-V3-eSH-16-TL-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-TL | 18.0805 | 1.5172 | 765.5597 | 416.9391 | 2.8 | 1182.4988 | 784.8988
DEER-SFAM-CZ06-V3-eSH-16-TM-s2 | 16 | CZ06 | V3 | CZ06-V3-eSH-16 | CZ06-V3-eSH-16-TM | 18.2763 | 1.4915 | 757.3597 | 426.3447 | 2.8 | 1183.7044 | 777.1044
DEER-SFAM-CZ06-V3-eSH-17-CM-s2 | 17 | CZ06 | V3 | CZ06-V3-eSH-17 | CZ06-V3-eSH-17-CM | 18.3675 | 1.5717 | 752.8198 | 362.7133 | 3.2 | 1115.5331 | 780.8331
DEER-SFAM-CZ06-V3-eSH-17-LM-s2 | 17 | CZ06 | V3 | CZ06-V3-eSH-17 | CZ06-V3-eSH-17-LM | 17.9099 | 1.4153 | 730.5956 | 351.6271 | 2.8 | 1082.2227 | 743.8227
DEER-SFAM-CZ06-V3-eSH-17-TH-s2 | 17 | CZ06 | V3 | CZ06-V3-eSH-17 | CZ06-V3-eSH-17-TH | 21.0483 | 1.2671 | 647.4761 | 428.8842 | 2.8 | 1076.3603 | 670.7603
DEER-SFAM-CZ06-V3-eSH-17-TL-s2 | 17 | CZ06 | V3 | CZ06-V3-eSH-17 | CZ06-V3-eSH-17-TL | 20.8727 | 1.2894 | 653.1449 | 421.8617 | 2.8 | 1075.0066 | 676.2066
DEER-SFAM-CZ06-V3-eSH-18-LH-s2 | 18 | CZ06 | V3 | CZ06-V3-eSH-18 | CZ06-V3-eSH-18-LH | 19.0506 | 1.3405 | 678.2819 | 384.6501 | 2.8 | 1062.932 | 699.132
DEER-SFAM-CZ06-V3-eSH-18-LL-s2 | 18 | CZ06 | V3 | CZ06-V3-eSH-18 | CZ06-V3-eSH-18-LL | 18.087 | 1.4063 | 708.9254 | 356.1678 | 2.8 | 1065.0932 | 729.0932
DEER-SFAM-CZ06-V3-eSH-18-LM-s2 | 18 | CZ06 | V3 | CZ06-V3-eSH-18 | CZ06-V3-eSH-18-LM | 19.0521 | 1.35 | 680.3737 | 401.9997 | 2.8 | 1082.3734 | 704.0734
DEER-SFAM-CZ06-V3-eSH-18-TM-s2 | 18 | CZ06 | V3 | CZ06-V3-eSH-18 | CZ06-V3-eSH-18-TM | 22.8518 | 1.2025 | 596.8914 | 409.5097 | 2.8 | 1006.4011 | 630.5011
DEER-SFAM-CZ06-V4-eSA-10-HH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-HH | 10.9838 | 2.3539 | 1137.9087 | 0 | 3.2 | 1137.9087 | 1154.3817
DEER-SFAM-CZ06-V4-eSA-10-HL-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-HL | 11.0938 | 2.4631 | 1125.9052 | 0 | 3.2 | 1125.9052 | 1142.3993
DEER-SFAM-CZ06-V4-eSA-10-HM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-HM | 10.909 | 2.4743 | 1136.8208 | 0 | 3.2 | 1136.8208 | 1153.3109
DEER-SFAM-CZ06-V4-eSA-10-LH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-LH | 10.6349 | 2.3929 | 1113.6298 | 0 | 3.2 | 1113.6298 | 1130.1446
DEER-SFAM-CZ06-V4-eSA-10-LL-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-LL | 10.6454 | 2.5297 | 1164.89 | 0 | 3.2 | 1164.89 | 1181.3892
DEER-SFAM-CZ06-V4-eSA-10-LM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-LM | 10.6222 | 2.4306 | 1127.2232 | 0 | 3.2 | 1127.2232 | 1143.739
DEER-SFAM-CZ06-V4-eSA-10-MH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-MH | 10.6664 | 2.3485 | 1122.5468 | 0 | 3.2 | 1122.5468 | 1139.0547
DEER-SFAM-CZ06-V4-eSA-10-ML-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-ML | 10.9235 | 2.5339 | 1163.8567 | 0 | 3.2 | 1163.8567 | 1180.3513
DEER-SFAM-CZ06-V4-eSA-10-MM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSA-10 | CZ06-V4-eSA-10-MM | 10.9595 | 2.3224 | 1090.9254 | 0 | 3.2 | 1090.9254 | 1107.4221
DEER-SFAM-CZ06-V4-eSA-13-HH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-HH | 13.4343 | 1.8642 | 876.1544 | 0 | 3.2 | 876.1544 | 891.0234
DEER-SFAM-CZ06-V4-eSA-13-HL-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-HL | 13.9972 | 1.8875 | 857.7182 | 0 | 3.2 | 857.7182 | 870.73
DEER-SFAM-CZ06-V4-eSA-13-HM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-HM | 13.8566 | 1.8655 | 868.9357 | 0 | 3.2 | 868.9357 | 883.7965
DEER-SFAM-CZ06-V4-eSA-13-LH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-LH | 13.8726 | 1.665 | 842.8407 | 0 | 2.8 | 842.8407 | 859.3162
DEER-SFAM-CZ06-V4-eSA-13-LL-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-LL | 13.9031 | 1.8799 | 879.3669 | 0 | 3.2 | 879.3669 | 895.8177
DEER-SFAM-CZ06-V4-eSA-13-LM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-LM | 13.6234 | 1.7602 | 878.7965 | 0 | 2.8 | 878.7965 | 895.2489
DEER-SFAM-CZ06-V4-eSA-13-MH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-MH | 15.0068 | 1.745 | 817.0632 | 0 | 3.2 | 817.0632 | 833.5533
DEER-SFAM-CZ06-V4-eSA-13-ML-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-ML | 13.7276 | 1.8656 | 863.5807 | 0 | 3.2 | 863.5807 | 880.0168
DEER-SFAM-CZ06-V4-eSA-13-MM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSA-13 | CZ06-V4-eSA-13-MM | 15.0457 | 1.7699 | 816.9999 | 0 | 3.2 | 816.9999 | 833.4864
DEER-SFAM-CZ06-V4-eSA-14-HH-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-HH | 14.3847 | 1.7678 | 826.6665 | 0 | 3.2 | 826.6665 | 840.4854
DEER-SFAM-CZ06-V4-eSA-14-HL-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-HL | 15.1484 | 1.727 | 794.6308 | 0 | 3.2 | 794.6308 | 804.7937
DEER-SFAM-CZ06-V4-eSA-14-HM-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-HM | 15.0823 | 1.7304 | 793.3188 | 0 | 3.2 | 793.3188 | 808.9146
DEER-SFAM-CZ06-V4-eSA-14-MH-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-MH | 14.5927 | 1.6306 | 831.3552 | 0 | 2.8 | 831.3552 | 842.1684
DEER-SFAM-CZ06-V4-eSA-14-ML-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-ML | 14.438 | 1.7498 | 812.7731 | 0 | 3.2 | 812.7731 | 830.0779
DEER-SFAM-CZ06-V4-eSA-14-MM-s1 | 14 | CZ06 | V4 | CZ06-V4-eSA-14 | CZ06-V4-eSA-14-MM | 14.7262 | 1.6225 | 805.6639 | 0 | 2.8 | 805.6639 | 817.5229
DEER-SFAM-CZ06-V4-eSA-15-HH-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-HH | 16.3419 | 1.5234 | 729.409 | 0 | 3.2 | 729.409 | 740.9322
DEER-SFAM-CZ06-V4-eSA-15-HL-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-HL | 16.7082 | 1.5561 | 719.2074 | 0 | 3.2 | 719.2074 | 733.5634
DEER-SFAM-CZ06-V4-eSA-15-HM-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-HM | 15.978 | 1.5728 | 745.607 | 0 | 3.2 | 745.607 | 757.1711
DEER-SFAM-CZ06-V4-eSA-15-MH-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-MH | 16.1762 | 1.5604 | 736.9348 | 0 | 3.2 | 736.9348 | 745.5219
DEER-SFAM-CZ06-V4-eSA-15-ML-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-ML | 16.5418 | 1.6263 | 744.8793 | 0 | 3.2 | 744.8793 | 756.413
DEER-SFAM-CZ06-V4-eSA-15-MM-s1 | 15 | CZ06 | V4 | CZ06-V4-eSA-15 | CZ06-V4-eSA-15-MM | 15.955 | 1.6178 | 750.1792 | 0 | 3.2 | 750.1792 | 760.7076
DEER-SFAM-CZ06-V4-eSA-16-CH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-CH | 16.7949 | 1.6833 | 809.7414 | 0 | 3.2 | 809.7414 | 816.3653
DEER-SFAM-CZ06-V4-eSA-16-CL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-CL | 17.4164 | 1.6076 | 763.2975 | 0 | 3.2 | 763.2975 | 771.6731
DEER-SFAM-CZ06-V4-eSA-16-CM-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-CM | 17.0031 | 1.6273 | 783.7333 | 0 | 3.2 | 783.7333 | 792.5585
DEER-SFAM-CZ06-V4-eSA-16-LH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-LH | 17.1219 | 1.4893 | 743.8929 | 0 | 3.2 | 743.8929 | 755.2999
DEER-SFAM-CZ06-V4-eSA-16-LL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-LL | 16.4436 | 1.5589 | 774.0583 | 0 | 3.2 | 774.0583 | 781.5422
DEER-SFAM-CZ06-V4-eSA-16-LM-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-LM | 16.3447 | 1.5832 | 783.941 | 0 | 3.2 | 783.941 | 790.7239
DEER-SFAM-CZ06-V4-eSA-16-NM-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-NM | 17.2839 | 1.6184 | 773.662 | 0 | 3.2 | 773.662 | 780.3184
DEER-SFAM-CZ06-V4-eSA-16-TH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-TH | 18.6866 | 1.4673 | 737.1538 | 0 | 3.2 | 737.1538 | 741.4205
DEER-SFAM-CZ06-V4-eSA-16-TL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSA-16 | CZ06-V4-eSA-16-TL | 19.1588 | 1.5049 | 722.7654 | 0 | 3.2 | 722.7654 | 727.3713
DEER-SFAM-CZ06-V4-eSA-17-CH-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-CH | 17.99 | 1.5681 | 747.2115 | 0 | 3.2 | 747.2115 | 755.5795
DEER-SFAM-CZ06-V4-eSA-17-CL-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-CL | 17.9868 | 1.5846 | 747.4972 | 0 | 3.2 | 747.4972 | 755.8636
DEER-SFAM-CZ06-V4-eSA-17-CM-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-CM | 18.0877 | 1.5864 | 752.9773 | 0 | 3.2 | 752.9773 | 759.5824
DEER-SFAM-CZ06-V4-eSA-17-LH-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-LH | 17.7125 | 1.4346 | 711.3487 | 0 | 3.2 | 711.3487 | 720.288
DEER-SFAM-CZ06-V4-eSA-17-LL-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-LL | 17.5286 | 1.4779 | 733.1671 | 0 | 3.2 | 733.1671 | 738.0347
DEER-SFAM-CZ06-V4-eSA-17-LM-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-LM | 17.225 | 1.4913 | 746.5519 | 0 | 3.2 | 746.5519 | 750.7506
DEER-SFAM-CZ06-V4-eSA-17-TH-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-TH | 21.4727 | 1.2701 | 631.1082 | 0 | 3.2 | 631.1082 | 637.9322
DEER-SFAM-CZ06-V4-eSA-17-TL-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-TL | 22.0812 | 1.3195 | 609.2246 | 0 | 3.2 | 609.2246 | 619.8446
DEER-SFAM-CZ06-V4-eSA-17-TM-s2 | 17 | CZ06 | V4 | CZ06-V4-eSA-17 | CZ06-V4-eSA-17-TM | 20.4702 | 1.428 | 698.2048 | 0 | 3.2 | 698.2048 | 701.7807
DEER-SFAM-CZ06-V4-eSA-18-LH-s2 | 18 | CZ06 | V4 | CZ06-V4-eSA-18 | CZ06-V4-eSA-18-LH | 18.6021 | 1.3831 | 691.8013 | 0 | 3.2 | 691.8013 | 697.6499
DEER-SFAM-CZ06-V4-eSA-18-LL-s2 | 18 | CZ06 | V4 | CZ06-V4-eSA-18 | CZ06-V4-eSA-18-LL | 18.8931 | 1.3931 | 675.2699 | 0 | 3.2 | 675.2699 | 682.9069
DEER-SFAM-CZ06-V4-eSA-18-TH-s2 | 18 | CZ06 | V4 | CZ06-V4-eSA-18 | CZ06-V4-eSA-18-TH | 21.9326 | 1.209 | 617.7705 | 0 | 3.2 | 617.7705 | 622.404
DEER-SFAM-CZ06-V4-eSA-18-TL-s2 | 18 | CZ06 | V4 | CZ06-V4-eSA-18 | CZ06-V4-eSA-18-TL | 21.5155 | 1.2846 | 632.829 | 0 | 3.2 | 632.829 | 637.9173
DEER-SFAM-CZ06-V4-eSA-18-TM-s2 | 18 | CZ06 | V4 | CZ06-V4-eSA-18 | CZ06-V4-eSA-18-TM | 21.0108 | 1.2706 | 643.8502 | 0 | 3.2 | 643.8502 | 648.5868
DEER-SFAM-CZ06-V4-eSH-10-HH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-HH | 10.5955 | 2.3428 | 1115.708 | 312.1062 | 3.2 | 1427.8142 | 1147.6142
DEER-SFAM-CZ06-V4-eSH-10-HL-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-HL | 10.4491 | 2.416 | 1149.6838 | 314.3192 | 3.2 | 1464.003 | 1181.603
DEER-SFAM-CZ06-V4-eSH-10-HM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-HM | 11.098 | 2.3594 | 1117.5036 | 305.6442 | 3.2 | 1423.1478 | 1147.8478
DEER-SFAM-CZ06-V4-eSH-10-LH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-LH | 10.6493 | 2.2734 | 1126.3452 | 332.5236 | 3.2 | 1458.8688 | 1159.3688
DEER-SFAM-CZ06-V4-eSH-10-LL-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-LL | 10.6956 | 2.447 | 1150.0829 | 305.5801 | 3.2 | 1455.663 | 1184.163
DEER-SFAM-CZ06-V4-eSH-10-LM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-LM | 10.7824 | 2.3605 | 1137.754 | 307.2348 | 3.2 | 1444.9888 | 1169.0888
DEER-SFAM-CZ06-V4-eSH-10-MH-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-MH | 10.746 | 2.3085 | 1114.303 | 323.4463 | 3.2 | 1437.7493 | 1149.3493
DEER-SFAM-CZ06-V4-eSH-10-ML-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-ML | 10.7926 | 2.4971 | 1139.5919 | 284.9772 | 3.2 | 1424.5691 | 1170.8691
DEER-SFAM-CZ06-V4-eSH-10-MM-s1 | 10 | CZ06 | V4 | CZ06-V4-eSH-10 | CZ06-V4-eSH-10-MM | 11.0635 | 2.3795 | 1127.0347 | 312.23 | 3.2 | 1439.2647 | 1156.8647
DEER-SFAM-CZ06-V4-eSH-13-HH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-HH | 14.2024 | 1.7988 | 853.3188 | 299.0856 | 3.2 | 1152.4044 | 882.4044
DEER-SFAM-CZ06-V4-eSH-13-HL-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-HL | 13.7036 | 1.8451 | 858.9573 | 254.027 | 3.2 | 1112.9843 | 887.8843
DEER-SFAM-CZ06-V4-eSH-13-HM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-HM | 14.2467 | 1.8226 | 854.9685 | 265.8049 | 3.2 | 1120.7734 | 881.1734
DEER-SFAM-CZ06-V4-eSH-13-LH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-LH | 13.6842 | 1.7798 | 859.12 | 302.3689 | 3.2 | 1161.4889 | 902.5889
DEER-SFAM-CZ06-V4-eSH-13-LL-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-LL | 14.8015 | 1.7477 | 823.7015 | 268.2662 | 3.2 | 1091.9677 | 850.1677
DEER-SFAM-CZ06-V4-eSH-13-LM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-LM | 13.2784 | 1.928 | 900.4586 | 241.211 | 3.2 | 1141.6696 | 931.0696
DEER-SFAM-CZ06-V4-eSH-13-MH-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-MH | 14.8563 | 1.6605 | 803.7898 | 300.1905 | 3.2 | 1103.9803 | 833.1803
DEER-SFAM-CZ06-V4-eSH-13-ML-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-ML | 13.7545 | 1.9346 | 882.0865 | 275.0382 | 3.2 | 1157.1247 | 912.2247
DEER-SFAM-CZ06-V4-eSH-13-MM-s1 | 13 | CZ06 | V4 | CZ06-V4-eSH-13 | CZ06-V4-eSH-13-MM | 14.7635 | 1.7893 | 828.1165 | 278.5889 | 3.2 | 1106.7054 | 851.8054
DEER-SFAM-CZ06-V4-eSH-14-HH-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-HH | 15.0551 | 1.7112 | 805.1168 | 271.3608 | 3.2 | 1076.4776 | 827.2776
DEER-SFAM-CZ06-V4-eSH-14-HL-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-HL | 14.9272 | 1.7694 | 809.8199 | 260.9123 | 3.2 | 1070.7322 | 836.4322
DEER-SFAM-CZ06-V4-eSH-14-HM-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-HM | 14.7667 | 1.7371 | 815.5245 | 260.47 | 3.2 | 1075.9945 | 834.3945
DEER-SFAM-CZ06-V4-eSH-14-MH-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-MH | 14.6498 | 1.5635 | 796.3586 | 271.358 | 2.8 | 1067.7166 | 824.9166
DEER-SFAM-CZ06-V4-eSH-14-ML-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-ML | 14.9578 | 1.7157 | 789.5651 | 277.556 | 3.2 | 1067.1211 | 825.3211
DEER-SFAM-CZ06-V4-eSH-14-MM-s1 | 14 | CZ06 | V4 | CZ06-V4-eSH-14 | CZ06-V4-eSH-14-MM | 14.3766 | 1.7386 | 812.0781 | 253.3276 | 3.2 | 1065.4057 | 837.2057
DEER-SFAM-CZ06-V4-eSH-15-HH-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-HH | 15.9907 | 1.5699 | 745.9954 | 303.5571 | 3.2 | 1049.5525 | 766.4525
DEER-SFAM-CZ06-V4-eSH-15-HL-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-HL | 15.9513 | 1.64 | 757.9002 | 227.7795 | 3.2 | 985.6797 | 778.3797
DEER-SFAM-CZ06-V4-eSH-15-HM-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-HM | 16.5217 | 1.5458 | 725.2758 | 238.6243 | 3.2 | 963.9001 | 745.7001
DEER-SFAM-CZ06-V4-eSH-15-MH-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-MH | 16.4383 | 1.5411 | 720.2593 | 268.6436 | 3.2 | 988.9029 | 739.9029
DEER-SFAM-CZ06-V4-eSH-15-ML-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-ML | 16.0357 | 1.6042 | 738.9524 | 245.2409 | 3.2 | 984.1933 | 759.1933
DEER-SFAM-CZ06-V4-eSH-15-MM-s1 | 15 | CZ06 | V4 | CZ06-V4-eSH-15 | CZ06-V4-eSH-15-MM | 16.949 | 1.5076 | 713.7319 | 264.4181 | 3.2 | 978.15 | 735.25
DEER-SFAM-CZ06-V4-eSH-16-CH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-CH | 17.2835 | 1.6235 | 785.2163 | 246.9686 | 3.2 | 1032.1849 | 801.3849
DEER-SFAM-CZ06-V4-eSH-16-CL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-CL | 17.3613 | 1.6488 | 783.2577 | 229.6489 | 3.2 | 1012.9066 | 800.3066
DEER-SFAM-CZ06-V4-eSH-16-LH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-LH | 17.2262 | 1.4234 | 734.7388 | 288.6064 | 3.2 | 1023.3452 | 755.1452
DEER-SFAM-CZ06-V4-eSH-16-LL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-LL | 16.3669 | 1.5959 | 784.7826 | 253.1115 | 3.2 | 1037.8941 | 801.1941
DEER-SFAM-CZ06-V4-eSH-16-LM-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-LM | 16.4332 | 1.5189 | 776.6806 | 286.413 | 3.2 | 1063.0936 | 799.4936
DEER-SFAM-CZ06-V4-eSH-16-TH-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-TH | 20.0855 | 1.3565 | 674.2496 | 308.6047 | 3.2 | 982.8543 | 689.2543
DEER-SFAM-CZ06-V4-eSH-16-TL-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-TL | 18.4378 | 1.5545 | 745.8615 | 291.7826 | 3.2 | 1037.6441 | 758.9441
DEER-SFAM-CZ06-V4-eSH-16-TM-s2 | 16 | CZ06 | V4 | CZ06-V4-eSH-16 | CZ06-V4-eSH-16-TM | 18.6099 | 1.5305 | 738.9615 | 298.5394 | 3.2 | 1037.5009 | 752.3009
DEER-SFAM-CZ06-V4-eSH-17-CM-s2 | 17 | CZ06 | V4 | CZ06-V4-eSH-17 | CZ06-V4-eSH-17-CM | 18.4298 | 1.554 | 737.6736 | 252.227 | 3.2 | 989.9006 | 757.1006
DEER-SFAM-CZ06-V4-eSH-17-LM-s2 | 17 | CZ06 | V4 | CZ06-V4-eSH-17 | CZ06-V4-eSH-17-LM | 17.7757 | 1.4424 | 725.3812 | 247.343 | 3.2 | 972.7242 | 734.6242
DEER-SFAM-CZ06-V4-eSH-17-TH-s2 | 17 | CZ06 | V4 | CZ06-V4-eSH-17 | CZ06-V4-eSH-17-TH | 21.182 | 1.2943 | 639.1545 | 304.0584 | 3.2 | 943.2129 | 655.0129
DEER-SFAM-CZ06-V4-eSH-17-TL-s2 | 17 | CZ06 | V4 | CZ06-V4-eSH-17 | CZ06-V4-eSH-17-TL | 21.0462 | 1.314 | 642.8199 | 298.3204 | 3.2 | 941.1403 | 658.5403
DEER-SFAM-CZ06-V4-eSH-18-LH-s2 | 18 | CZ06 | V4 | CZ06-V4-eSH-18 | CZ06-V4-eSH-18-LH | 18.9414 | 1.3616 | 674.464 | 270.3499 | 3.2 | 944.8139 | 689.0139
DEER-SFAM-CZ06-V4-eSH-18-LL-s2 | 18 | CZ06 | V4 | CZ06-V4-eSH-18 | CZ06-V4-eSH-18-LL | 18.0084 | 1.4331 | 707.0895 | 249.9005 | 3.2 | 956.99 | 721.19
DEER-SFAM-CZ06-V4-eSH-18-LM-s2 | 18 | CZ06 | V4 | CZ06-V4-eSH-18 | CZ06-V4-eSH-18-LM | 18.9584 | 1.3712 | 678.0281 | 282.2185 | 3.2 | 960.2466 | 694.5466
DEER-SFAM-CZ06-V4-eSH-18-TM-s2 | 18 | CZ06 | V4 | CZ06-V4-eSH-18 | CZ06-V4-eSH-18-TM | 23.1223 | 1.2177 | 585.7582 | 290.8723 | 3.2 | 876.6305 | 608.6305
DEER-SFAM-CZ07-V1-eSA-10-HH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-HH | 10.6277 | 2.3255 | 1071.1724 | 0 | 3.0988 | 1071.1724 | 1139.052
DEER-SFAM-CZ07-V1-eSA-10-HL-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-HL | 10.6258 | 2.3949 | 1053.733 | 0 | 3.0988 | 1053.733 | 1121.679
DEER-SFAM-CZ07-V1-eSA-10-HM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-HM | 10.5433 | 2.3605 | 1056.8251 | 0 | 3.0988 | 1056.8251 | 1124.7591
DEER-SFAM-CZ07-V1-eSA-10-LH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-LH | 10.6015 | 2.275 | 1013.2603 | 0 | 3.0988 | 1013.2603 | 1081.2735
DEER-SFAM-CZ07-V1-eSA-10-LL-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-LL | 10.3643 | 2.4288 | 1073.7336 | 0 | 3.0988 | 1073.7336 | 1141.6954
DEER-SFAM-CZ07-V1-eSA-10-LM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-LM | 10.5607 | 2.3164 | 1028.9665 | 0 | 3.0988 | 1028.9665 | 1096.9825
DEER-SFAM-CZ07-V1-eSA-10-MH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-MH | 10.5588 | 2.2377 | 1029.309 | 0 | 3.0988 | 1029.309 | 1097.2988
DEER-SFAM-CZ07-V1-eSA-10-ML-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-ML | 10.542 | 2.4658 | 1083.8653 | 0 | 3.0988 | 1083.8653 | 1151.8131
DEER-SFAM-CZ07-V1-eSA-10-MM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSA-10 | CZ07-V1-eSA-10-MM | 10.7141 | 2.2683 | 1009.2428 | 0 | 3.0988 | 1009.2428 | 1077.1976
DEER-SFAM-CZ07-V1-eSA-13-HH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-HH | 13.1775 | 1.7822 | 801.2292 | 0 | 3.0988 | 801.2292 | 862.4788
DEER-SFAM-CZ07-V1-eSA-13-HL-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-HL | 13.752 | 1.8136 | 788.762 | 0 | 3.0988 | 788.762 | 842.3651
DEER-SFAM-CZ07-V1-eSA-13-HM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-HM | 13.5574 | 1.817 | 794.0957 | 0 | 3.0988 | 794.0957 | 855.3192
DEER-SFAM-CZ07-V1-eSA-13-LH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-LH | 13.6213 | 1.7226 | 780.6811 | 0 | 3.0988 | 780.6811 | 848.6477
DEER-SFAM-CZ07-V1-eSA-13-LL-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-LL | 13.6468 | 1.8183 | 811.8353 | 0 | 3.0988 | 811.8353 | 879.6426
DEER-SFAM-CZ07-V1-eSA-13-LM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-LM | 13.3921 | 1.7827 | 812.6702 | 0 | 3.0988 | 812.6702 | 880.5697
DEER-SFAM-CZ07-V1-eSA-13-MH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-MH | 14.46 | 1.7239 | 764.5794 | 0 | 3.0988 | 764.5794 | 832.5138
DEER-SFAM-CZ07-V1-eSA-13-ML-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-ML | 13.6208 | 1.7896 | 791.1755 | 0 | 3.0988 | 791.1755 | 858.8949
DEER-SFAM-CZ07-V1-eSA-13-MM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSA-13 | CZ07-V1-eSA-13-MM | 14.3757 | 1.7628 | 767.2056 | 0 | 3.0988 | 767.2056 | 835.128
DEER-SFAM-CZ07-V1-eSA-14-HH-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-HH | 14.1914 | 1.7015 | 759.7776 | 0 | 3.0988 | 759.7776 | 816.7102
DEER-SFAM-CZ07-V1-eSA-14-HL-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-HL | 14.8365 | 1.6762 | 726.1264 | 0 | 3.0988 | 726.1264 | 767.9932
DEER-SFAM-CZ07-V1-eSA-14-HM-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-HM | 14.8597 | 1.6826 | 727.3534 | 0 | 3.0988 | 727.3534 | 791.5936
DEER-SFAM-CZ07-V1-eSA-14-MH-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-MH | 14.333 | 1.6692 | 771.7013 | 0 | 3.0988 | 771.7013 | 816.3312
DEER-SFAM-CZ07-V1-eSA-14-ML-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-ML | 14.3971 | 1.6758 | 739.0426 | 0 | 3.0988 | 739.0426 | 810.3307
DEER-SFAM-CZ07-V1-eSA-14-MM-s1 | 14 | CZ07 | V1 | CZ07-V1-eSA-14 | CZ07-V1-eSA-14-MM | 14.4413 | 1.6306 | 746.9615 | 0 | 3.0988 | 746.9615 | 795.8962
DEER-SFAM-CZ07-V1-eSA-15-HH-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-HH | 15.8516 | 1.5163 | 672.0232 | 0 | 3.0988 | 672.0232 | 719.491
DEER-SFAM-CZ07-V1-eSA-15-HL-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-HL | 16.126 | 1.5348 | 666.3835 | 0 | 3.0988 | 666.3835 | 725.5344
DEER-SFAM-CZ07-V1-eSA-15-HM-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-HM | 15.6057 | 1.535 | 684.0188 | 0 | 3.0988 | 684.0188 | 731.6591
DEER-SFAM-CZ07-V1-eSA-15-MH-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-MH | 15.7719 | 1.5292 | 680.8847 | 0 | 3.0988 | 680.8847 | 716.2557
DEER-SFAM-CZ07-V1-eSA-15-ML-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-ML | 16.0153 | 1.5747 | 693.447 | 0 | 3.0988 | 693.447 | 740.9902
DEER-SFAM-CZ07-V1-eSA-15-MM-s1 | 15 | CZ07 | V1 | CZ07-V1-eSA-15 | CZ07-V1-eSA-15-MM | 15.6816 | 1.5629 | 687.7581 | 0 | 3.0988 | 687.7581 | 731.1285
DEER-SFAM-CZ07-V1-eSA-16-CH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-CH | 16.5709 | 1.7259 | 794.7018 | 0 | 3.0988 | 794.7018 | 821.8421
DEER-SFAM-CZ07-V1-eSA-16-CL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-CL | 17.0351 | 1.6671 | 748.1842 | 0 | 3.0988 | 748.1842 | 782.607
DEER-SFAM-CZ07-V1-eSA-16-CM-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-CM | 16.7297 | 1.685 | 764.8183 | 0 | 3.0988 | 764.8183 | 801.1348
DEER-SFAM-CZ07-V1-eSA-16-LH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-LH | 16.1115 | 1.5811 | 741.0314 | 0 | 3.0988 | 741.0314 | 787.7585
DEER-SFAM-CZ07-V1-eSA-16-LL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-LL | 15.7015 | 1.6357 | 762.9751 | 0 | 3.0988 | 762.9751 | 793.6814
DEER-SFAM-CZ07-V1-eSA-16-LM-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-LM | 15.8095 | 1.6275 | 765.066 | 0 | 3.0988 | 765.066 | 792.8953
DEER-SFAM-CZ07-V1-eSA-16-NM-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-NM | 17.1383 | 1.5367 | 734.8961 | 0 | 3.0988 | 734.8961 | 762.1946
DEER-SFAM-CZ07-V1-eSA-16-TH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-TH | 17.1349 | 1.6715 | 798.2976 | 0 | 3.0988 | 798.2976 | 815.6659
DEER-SFAM-CZ07-V1-eSA-16-TL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSA-16 | CZ07-V1-eSA-16-TL | 17.512 | 1.7009 | 780.7655 | 0 | 3.0988 | 780.7655 | 799.5447
DEER-SFAM-CZ07-V1-eSA-17-CH-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-CH | 17.7607 | 1.5964 | 723.1675 | 0 | 3.0988 | 723.1675 | 757.5663
DEER-SFAM-CZ07-V1-eSA-17-CL-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-CL | 17.7508 | 1.6115 | 723.521 | 0 | 3.0988 | 723.521 | 757.9123
DEER-SFAM-CZ07-V1-eSA-17-CM-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-CM | 17.8443 | 1.6197 | 738.7485 | 0 | 3.0988 | 738.7485 | 765.8085
DEER-SFAM-CZ07-V1-eSA-17-LH-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-LH | 16.8556 | 1.5031 | 701.6243 | 0 | 3.0988 | 701.6243 | 738.2491
DEER-SFAM-CZ07-V1-eSA-17-LL-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-LL | 16.7805 | 1.5601 | 725.7783 | 0 | 3.0988 | 725.7783 | 745.7237
DEER-SFAM-CZ07-V1-eSA-17-LM-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-LM | 16.6098 | 1.5489 | 732.1373 | 0 | 3.0988 | 732.1373 | 749.3659
DEER-SFAM-CZ07-V1-eSA-17-TH-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-TH | 19.6314 | 1.4548 | 676.5782 | 0 | 3.0988 | 676.5782 | 704.4076
DEER-SFAM-CZ07-V1-eSA-17-TL-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-TL | 19.9972 | 1.5198 | 654.8128 | 0 | 3.0988 | 654.8128 | 698.4006
DEER-SFAM-CZ07-V1-eSA-17-TM-s2 | 17 | CZ07 | V1 | CZ07-V1-eSA-17 | CZ07-V1-eSA-17-TM | 18.7952 | 1.6085 | 768.0317 | 0 | 3.0988 | 768.0317 | 782.5138
DEER-SFAM-CZ07-V1-eSA-18-LH-s2 | 18 | CZ07 | V1 | CZ07-V1-eSA-18 | CZ07-V1-eSA-18-LH | 17.7405 | 1.4559 | 686.0141 | 0 | 3.0988 | 686.0141 | 710.013
DEER-SFAM-CZ07-V1-eSA-18-LL-s2 | 18 | CZ07 | V1 | CZ07-V1-eSA-18 | CZ07-V1-eSA-18-LL | 18.0477 | 1.4625 | 667.8218 | 0 | 3.0988 | 667.8218 | 699.1475
DEER-SFAM-CZ07-V1-eSA-18-TH-s2 | 18 | CZ07 | V1 | CZ07-V1-eSA-18 | CZ07-V1-eSA-18-TH | 20.0394 | 1.3974 | 662.5609 | 0 | 3.0988 | 662.5609 | 681.4847
DEER-SFAM-CZ07-V1-eSA-18-TL-s2 | 18 | CZ07 | V1 | CZ07-V1-eSA-18 | CZ07-V1-eSA-18-TL | 19.6725 | 1.4786 | 681.7047 | 0 | 3.0988 | 681.7047 | 702.466
DEER-SFAM-CZ07-V1-eSA-18-TM-s2 | 18 | CZ07 | V1 | CZ07-V1-eSA-18 | CZ07-V1-eSA-18-TM | 19.4533 | 1.434 | 681.4549 | 0 | 3.0988 | 681.4549 | 700.7866
DEER-SFAM-CZ07-V1-eSH-10-HH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-HH | 10.454 | 2.2618 | 1024.471 | 1306.0127 | 3.0988 | 2330.4837 | 1160.4824
DEER-SFAM-CZ07-V1-eSH-10-HL-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-HL | 10.3515 | 2.37 | 1055.0389 | 1323.3454 | 3.0988 | 2378.3843 | 1191.6084
DEER-SFAM-CZ07-V1-eSH-10-HM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-HM | 10.7496 | 2.3177 | 1044.9659 | 1260.9887 | 3.0988 | 2305.9546 | 1174.6727
DEER-SFAM-CZ07-V1-eSH-10-LH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-LH | 10.5329 | 2.2102 | 1032.8353 | 1395.2727 | 3.0988 | 2428.108 | 1174.1247
DEER-SFAM-CZ07-V1-eSH-10-LL-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-LL | 10.479 | 2.3764 | 1060.7174 | 1282.3213 | 3.0988 | 2343.0387 | 1205.899
DEER-SFAM-CZ07-V1-eSH-10-LM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-LM | 10.5279 | 2.2853 | 1052.8726 | 1275.6714 | 3.0988 | 2328.544 | 1185.8609
DEER-SFAM-CZ07-V1-eSH-10-MH-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-MH | 10.6312 | 2.2493 | 1023.0805 | 1362.3013 | 3.0988 | 2385.3818 | 1173.1612
DEER-SFAM-CZ07-V1-eSH-10-ML-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-ML | 10.5561 | 2.3805 | 1048.4973 | 1194.3262 | 3.0988 | 2242.8235 | 1180.9188
DEER-SFAM-CZ07-V1-eSH-10-MM-s1 | 10 | CZ07 | V1 | CZ07-V1-eSH-10 | CZ07-V1-eSH-10-MM | 10.6637 | 2.3572 | 1064.0061 | 1310.117 | 3.0988 | 2374.1231 | 1190.7206
DEER-SFAM-CZ07-V1-eSH-13-HH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-HH | 13.7469 | 1.7681 | 791.7459 | 1246.7721 | 3.0988 | 2038.518 | 915.8289
DEER-SFAM-CZ07-V1-eSH-13-HL-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-HL | 13.4375 | 1.7921 | 783.752 | 1073.1114 | 3.0988 | 1856.8634 | 906.9841
DEER-SFAM-CZ07-V1-eSH-13-HM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-HM | 13.7928 | 1.7865 | 793.6044 | 1107.8951 | 3.0988 | 1901.4995 | 904.9346
DEER-SFAM-CZ07-V1-eSH-13-LH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-LH | 13.6083 | 1.7195 | 783.4512 | 1291.1551 | 3.0988 | 2074.6063 | 971.2727
DEER-SFAM-CZ07-V1-eSH-13-LL-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-LL | 14.2774 | 1.7393 | 769.7182 | 1130.2742 | 3.0988 | 1899.9924 | 882.3505
DEER-SFAM-CZ07-V1-eSH-13-LM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-LM | 13.2264 | 1.8035 | 818.207 | 1022.831 | 3.0988 | 1841.038 | 948.8997
DEER-SFAM-CZ07-V1-eSH-13-MH-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-MH | 14.246 | 1.6481 | 751.3901 | 1252.3908 | 3.0988 | 2003.7809 | 877.4159
DEER-SFAM-CZ07-V1-eSH-13-ML-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-ML | 13.5095 | 1.8264 | 810.5021 | 1189.954 | 3.0988 | 2000.4561 | 939.743
DEER-SFAM-CZ07-V1-eSH-13-MM-s1 | 13 | CZ07 | V1 | CZ07-V1-eSH-13 | CZ07-V1-eSH-13-MM | 14.2277 | 1.765 | 774.4768 | 1168.2747 | 3.0988 | 1942.7516 | 875.3746
DEER-SFAM-CZ07-V1-eSH-14-HH-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-HH | 14.6035 | 1.6832 | 745.547 | 1132.5819 | 3.0988 | 1878.1289 | 839.9712
DEER-SFAM-CZ07-V1-eSH-14-HL-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-HL | 14.5636 | 1.7165 | 744.9505 | 1105.8866 | 3.0988 | 1850.8371 | 858.8867
DEER-SFAM-CZ07-V1-eSH-14-HM-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-HM | 14.4288 | 1.6836 | 749.6275 | 1094.7726 | 3.0988 | 1844.4001 | 829.9834
DEER-SFAM-CZ07-V1-eSH-14-MH-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-MH | 14.4003 | 1.6122 | 736.6381 | 1163.5926 | 3.0988 | 1900.2308 | 859.4623
DEER-SFAM-CZ07-V1-eSH-14-ML-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-ML | 14.8533 | 1.6632 | 718.9055 | 1219.0839 | 3.0988 | 1937.9895 | 873.8355
DEER-SFAM-CZ07-V1-eSH-14-MM-s1 | 14 | CZ07 | V1 | CZ07-V1-eSH-14 | CZ07-V1-eSH-14-MM | 14.3814 | 1.6529 | 734.3035 | 1080.6127 | 3.0988 | 1814.9161 | 842.0863
DEER-SFAM-CZ07-V1-eSH-15-HH-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-HH | 15.4969 | 1.5358 | 690.4624 | 1305.2104 | 3.0988 | 1995.6729 | 778.6102
DEER-SFAM-CZ07-V1-eSH-15-HL-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-HL | 15.5684 | 1.5869 | 697.0923 | 954.6395 | 3.0988 | 1651.7318 | 784.3622
DEER-SFAM-CZ07-V1-eSH-15-HM-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-HM | 15.9965 | 1.5202 | 669.3487 | 990.7632 | 3.0988 | 1660.1119 | 757.0508
DEER-SFAM-CZ07-V1-eSH-15-MH-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-MH | 16.2012 | 1.5142 | 661.6068 | 1174.0444 | 3.0988 | 1835.6512 | 746.6851
DEER-SFAM-CZ07-V1-eSH-15-ML-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-ML | 15.891 | 1.5622 | 672.856 | 1067.4531 | 3.0988 | 1740.3091 | 760.1709
DEER-SFAM-CZ07-V1-eSH-15-MM-s1 | 15 | CZ07 | V1 | CZ07-V1-eSH-15 | CZ07-V1-eSH-15-MM | 16.2621 | 1.5293 | 665.1774 | 1125.7786 | 3.0988 | 1790.956 | 757.1104
DEER-SFAM-CZ07-V1-eSH-16-CH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-CH | 16.9569 | 1.6775 | 774.9724 | 1128.9323 | 3.0988 | 1903.9047 | 846.6399
DEER-SFAM-CZ07-V1-eSH-16-CL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-CL | 17.0885 | 1.6942 | 770.7013 | 1050.6739 | 3.0988 | 1821.3752 | 845.6696
DEER-SFAM-CZ07-V1-eSH-16-LH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-LH | 16.1917 | 1.5254 | 732.0107 | 1261.091 | 3.0988 | 1993.1017 | 820.8295
DEER-SFAM-CZ07-V1-eSH-16-LL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-LL | 15.8143 | 1.6396 | 767.3198 | 1136.3199 | 3.0988 | 1903.6397 | 838.4086
DEER-SFAM-CZ07-V1-eSH-16-LM-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-LM | 15.6601 | 1.5828 | 759.761 | 1259.4175 | 3.0988 | 2019.1785 | 859.1256
DEER-SFAM-CZ07-V1-eSH-16-TH-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-TH | 18.1406 | 1.5698 | 729.0757 | 1405.3483 | 3.0988 | 2134.424 | 799.1638
DEER-SFAM-CZ07-V1-eSH-16-TL-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-TL | 17.2366 | 1.7364 | 793.5596 | 1399.6105 | 3.0988 | 2193.1701 | 856.3919
DEER-SFAM-CZ07-V1-eSH-16-TM-s2 | 16 | CZ07 | V1 | CZ07-V1-eSH-16 | CZ07-V1-eSH-16-TM | 17.4106 | 1.7161 | 785.6313 | 1425.3503 | 3.0988 | 2210.9817 | 850.0119
DEER-SFAM-CZ07-V1-eSH-17-CM-s2 | 17 | CZ07 | V1 | CZ07-V1-eSH-17 | CZ07-V1-eSH-17-CM | 18.1363 | 1.5968 | 726.4216 | 1207.5336 | 3.0988 | 1933.9551 | 815.7615
DEER-SFAM-CZ07-V1-eSH-17-LM-s2 | 17 | CZ07 | V1 | CZ07-V1-eSH-17 | CZ07-V1-eSH-17-LM | 17.0121 | 1.5255 | 716.4059 | 1105.9322 | 3.0988 | 1822.3381 | 756.4588
DEER-SFAM-CZ07-V1-eSH-17-TH-s2 | 17 | CZ07 | V1 | CZ07-V1-eSH-17 | CZ07-V1-eSH-17-TH | 19.3973 | 1.4839 | 682.522 | 1396.7559 | 3.0988 | 2079.2779 | 757.3418
DEER-SFAM-CZ07-V1-eSH-17-TL-s2 | 17 | CZ07 | V1 | CZ07-V1-eSH-17 | CZ07-V1-eSH-17-TL | 19.2513 | 1.504 | 686.5756 | 1381.4513 | 3.0988 | 2068.0269 | 760.5571
DEER-SFAM-CZ07-V1-eSH-18-LH-s2 | 18 | CZ07 | V1 | CZ07-V1-eSH-18 | CZ07-V1-eSH-18-LH | 18.1623 | 1.4371 | 667.9735 | 1243.4001 | 3.0988 | 1911.3736 | 732.528
DEER-SFAM-CZ07-V1-eSH-18-LL-s2 | 18 | CZ07 | V1 | CZ07-V1-eSH-18 | CZ07-V1-eSH-18-LL | 17.4175 | 1.4831 | 687.5803 | 1130.1822 | 3.0988 | 1817.7625 | 749.0037
DEER-SFAM-CZ07-V1-eSH-18-LM-s2 | 18 | CZ07 | V1 | CZ07-V1-eSH-18 | CZ07-V1-eSH-18-LM | 18.0483 | 1.4572 | 674.0301 | 1306.2458 | 3.0988 | 1980.2759 | 747.8375
DEER-SFAM-CZ07-V1-eSH-18-TM-s2 | 18 | CZ07 | V1 | CZ07-V1-eSH-18 | CZ07-V1-eSH-18-TM | 20.9289 | 1.3933 | 635.7438 | 1361.1034 | 3.0988 | 1996.8472 | 745.2666
DEER-SFAM-CZ07-V2-eSA-10-HH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-HH | 10.7131 | 2.1636 | 800.2544 | 0 | 2.6219 | 800.2544 | 837.7868
DEER-SFAM-CZ07-V2-eSA-10-HL-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-HL | 10.6803 | 2.2359 | 789.2 | 0 | 2.6219 | 789.2 | 826.7824
DEER-SFAM-CZ07-V2-eSA-10-HM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-HM | 10.6159 | 2.2011 | 789.2333 | 0 | 2.6219 | 789.2333 | 826.8066
DEER-SFAM-CZ07-V2-eSA-10-LH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-LH | 10.7454 | 2.1236 | 755.6309 | 0 | 2.6219 | 755.6309 | 793.2635
DEER-SFAM-CZ07-V2-eSA-10-LL-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-LL | 10.4134 | 2.2804 | 802.1987 | 0 | 2.6219 | 802.1987 | 839.7924
DEER-SFAM-CZ07-V2-eSA-10-LM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-LM | 10.6852 | 2.1652 | 768.5973 | 0 | 2.6219 | 768.5973 | 806.2317
DEER-SFAM-CZ07-V2-eSA-10-MH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-MH | 10.7351 | 2.0795 | 764.9182 | 0 | 2.6219 | 764.9182 | 802.5329
DEER-SFAM-CZ07-V2-eSA-10-ML-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-ML | 10.5741 | 2.3084 | 811.2816 | 0 | 2.6219 | 811.2816 | 848.8651
DEER-SFAM-CZ07-V2-eSA-10-MM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSA-10 | CZ07-V2-eSA-10-MM | 10.8128 | 2.139 | 754.4027 | 0 | 2.6219 | 754.4027 | 791.9916
DEER-SFAM-CZ07-V2-eSA-13-HH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-HH | 13.2657 | 1.6657 | 600.0292 | 0 | 2.6219 | 600.0292 | 633.9085
DEER-SFAM-CZ07-V2-eSA-13-HL-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-HL | 13.8274 | 1.7192 | 590.5633 | 0 | 2.6219 | 590.5633 | 620.2105
DEER-SFAM-CZ07-V2-eSA-13-HM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-HM | 13.5831 | 1.7656 | 598.6064 | 0 | 2.9329 | 598.6064 | 632.5128
DEER-SFAM-CZ07-V2-eSA-13-LH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-LH | 13.8288 | 1.5979 | 581.4034 | 0 | 2.6219 | 581.4034 | 619.0006
DEER-SFAM-CZ07-V2-eSA-13-LL-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-LL | 13.7377 | 1.707 | 607.5178 | 0 | 2.6219 | 607.5178 | 644.9962
DEER-SFAM-CZ07-V2-eSA-13-LM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-LM | 13.5505 | 1.6639 | 606.2494 | 0 | 2.6219 | 606.2494 | 643.7969
DEER-SFAM-CZ07-V2-eSA-13-MH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-MH | 14.6018 | 1.612 | 570.8747 | 0 | 2.6219 | 570.8747 | 608.4486
DEER-SFAM-CZ07-V2-eSA-13-ML-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-ML | 13.6781 | 1.6931 | 592.0545 | 0 | 2.6219 | 592.0545 | 629.5038
DEER-SFAM-CZ07-V2-eSA-13-MM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSA-13 | CZ07-V2-eSA-13-MM | 14.5068 | 1.6557 | 572.6365 | 0 | 2.6219 | 572.6365 | 610.2016
DEER-SFAM-CZ07-V2-eSA-14-HH-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-HH | 14.2803 | 1.5953 | 567.1892 | 0 | 2.6219 | 567.1892 | 598.6747
DEER-SFAM-CZ07-V2-eSA-14-HL-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-HL | 14.9139 | 1.572 | 543.8288 | 0 | 2.6219 | 543.8288 | 566.9837
DEER-SFAM-CZ07-V2-eSA-14-HM-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-HM | 14.9628 | 1.5852 | 544.1333 | 0 | 2.6219 | 544.1333 | 579.6691
DEER-SFAM-CZ07-V2-eSA-14-MH-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-MH | 14.517 | 1.5484 | 575.0714 | 0 | 2.6219 | 575.0714 | 599.7489
DEER-SFAM-CZ07-V2-eSA-14-ML-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-ML | 14.5118 | 1.5821 | 551.6356 | 0 | 2.6219 | 551.6356 | 591.0648
DEER-SFAM-CZ07-V2-eSA-14-MM-s1 | 14 | CZ07 | V2 | CZ07-V2-eSA-14 | CZ07-V2-eSA-14-MM | 14.5901 | 1.5172 | 558.2098 | 0 | 2.6219 | 558.2098 | 585.2728
DEER-SFAM-CZ07-V2-eSA-15-HH-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-HH | 15.8221 | 1.4703 | 508.8994 | 0 | 2.9329 | 508.8994 | 535.1898
DEER-SFAM-CZ07-V2-eSA-15-HL-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-HL | 16.0691 | 1.4897 | 503.9411 | 0 | 2.9329 | 503.9411 | 536.6964
DEER-SFAM-CZ07-V2-eSA-15-HM-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-HM | 15.5728 | 1.4886 | 518.0106 | 0 | 2.9329 | 518.0106 | 544.3952
DEER-SFAM-CZ07-V2-eSA-15-MH-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-MH | 15.8683 | 1.4361 | 509.1415 | 0 | 2.6219 | 509.1415 | 528.7071
DEER-SFAM-CZ07-V2-eSA-15-ML-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-ML | 16.0957 | 1.4838 | 518.4426 | 0 | 2.6219 | 518.4426 | 544.7184
DEER-SFAM-CZ07-V2-eSA-15-MM-s1 | 15 | CZ07 | V2 | CZ07-V2-eSA-15 | CZ07-V2-eSA-15-MM | 15.7994 | 1.4702 | 513.479 | 0 | 2.6219 | 513.479 | 537.4681
DEER-SFAM-CZ07-V2-eSA-16-CH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-CH | 16.4608 | 1.6585 | 589.9517 | 0 | 2.9329 | 589.9517 | 605.0972
DEER-SFAM-CZ07-V2-eSA-16-CL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-CL | 16.9392 | 1.5993 | 558.0156 | 0 | 2.9329 | 558.0156 | 577.182
DEER-SFAM-CZ07-V2-eSA-16-CM-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-CM | 16.6089 | 1.6184 | 571.3479 | 0 | 2.9329 | 571.3479 | 591.5598
DEER-SFAM-CZ07-V2-eSA-16-LH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-LH | 16.1346 | 1.4838 | 546.2446 | 0 | 2.6219 | 546.2446 | 572.2168
DEER-SFAM-CZ07-V2-eSA-16-LL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-LL | 15.6687 | 1.5319 | 567.1119 | 0 | 2.6219 | 567.1119 | 584.1648
DEER-SFAM-CZ07-V2-eSA-16-LM-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-LM | 15.7527 | 1.5158 | 567.4525 | 0 | 2.6219 | 567.4525 | 582.9086
DEER-SFAM-CZ07-V2-eSA-16-NM-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-NM | 17.0821 | 1.4444 | 540.9861 | 0 | 2.6219 | 540.9861 | 556.1472
DEER-SFAM-CZ07-V2-eSA-16-TH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-TH | 16.9802 | 1.5418 | 583.7339 | 0 | 2.6219 | 583.7339 | 593.4512
DEER-SFAM-CZ07-V2-eSA-16-TL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSA-16 | CZ07-V2-eSA-16-TL | 17.3315 | 1.5774 | 570.616 | 0 | 2.6219 | 570.616 | 581.1081
DEER-SFAM-CZ07-V2-eSA-17-CH-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-CH | 17.6494 | 1.5373 | 540.1401 | 0 | 2.9329 | 540.1401 | 559.2902
DEER-SFAM-CZ07-V2-eSA-17-CL-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-CL | 17.6362 | 1.5515 | 540.8187 | 0 | 2.9329 | 540.8187 | 559.9646
DEER-SFAM-CZ07-V2-eSA-17-CM-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-CM | 17.7332 | 1.5581 | 548.1518 | 0 | 2.9329 | 548.1518 | 563.2533
DEER-SFAM-CZ07-V2-eSA-17-LH-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-LH | 16.8399 | 1.4112 | 519.0233 | 0 | 2.6219 | 519.0233 | 539.3762
DEER-SFAM-CZ07-V2-eSA-17-LL-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-LL | 16.7128 | 1.4518 | 539.4165 | 0 | 2.6219 | 539.4165 | 550.5053
DEER-SFAM-CZ07-V2-eSA-17-LM-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-LM | 16.5584 | 1.4414 | 542.5226 | 0 | 2.6219 | 542.5226 | 552.0909
DEER-SFAM-CZ07-V2-eSA-17-TH-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-TH | 19.3878 | 1.3418 | 498.8786 | 0 | 2.6219 | 498.8786 | 514.4171
DEER-SFAM-CZ07-V2-eSA-17-TL-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-TL | 19.6077 | 1.4016 | 483.9805 | 0 | 2.6219 | 483.9805 | 508.2373
DEER-SFAM-CZ07-V2-eSA-17-TM-s2 | 17 | CZ07 | V2 | CZ07-V2-eSA-17 | CZ07-V2-eSA-17-TM | 18.5932 | 1.4849 | 553.9124 | 0 | 2.6219 | 553.9124 | 562.0422
DEER-SFAM-CZ07-V2-eSA-18-LH-s2 | 18 | CZ07 | V2 | CZ07-V2-eSA-18 | CZ07-V2-eSA-18-LH | 17.7186 | 1.3573 | 507.5679 | 0 | 2.6219 | 507.5679 | 520.8966
DEER-SFAM-CZ07-V2-eSA-18-LL-s2 | 18 | CZ07 | V2 | CZ07-V2-eSA-18 | CZ07-V2-eSA-18-LL | 17.9398 | 1.3678 | 497.6312 | 0 | 2.6219 | 497.6312 | 515.031
DEER-SFAM-CZ07-V2-eSA-18-TH-s2 | 18 | CZ07 | V2 | CZ07-V2-eSA-18 | CZ07-V2-eSA-18-TH | 19.8895 | 1.2832 | 486.4744 | 0 | 2.6219 | 486.4744 | 497.0335
DEER-SFAM-CZ07-V2-eSA-18-TL-s2 | 18 | CZ07 | V2 | CZ07-V2-eSA-18 | CZ07-V2-eSA-18-TL | 19.447 | 1.3625 | 501.7338 | 0 | 2.6219 | 501.7338 | 513.3304
DEER-SFAM-CZ07-V2-eSA-18-TM-s2 | 18 | CZ07 | V2 | CZ07-V2-eSA-18 | CZ07-V2-eSA-18-TM | 19.2578 | 1.3222 | 500.9095 | 0 | 2.6219 | 500.9095 | 511.6988
DEER-SFAM-CZ07-V2-eSH-10-HH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-HH | 10.5856 | 2.1063 | 763.5982 | 715.2337 | 2.6219 | 1478.8319 | 837.8926
DEER-SFAM-CZ07-V2-eSH-10-HL-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-HL | 10.4532 | 2.2087 | 787.846 | 723.1174 | 2.6219 | 1510.9633 | 862.2253
DEER-SFAM-CZ07-V2-eSH-10-HM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-HM | 10.8561 | 2.1626 | 780.2692 | 695.6611 | 2.6219 | 1475.9302 | 850.9908
DEER-SFAM-CZ07-V2-eSH-10-LH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-LH | 10.7105 | 2.0453 | 767.4164 | 760.4412 | 2.6219 | 1527.8576 | 844.4003
DEER-SFAM-CZ07-V2-eSH-10-LL-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-LL | 10.5789 | 2.212 | 792.3212 | 703.8805 | 2.6219 | 1496.2017 | 871.6829
DEER-SFAM-CZ07-V2-eSH-10-LM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-LM | 10.6687 | 2.1245 | 783.3108 | 702.2688 | 2.6219 | 1485.5796 | 856.1279
DEER-SFAM-CZ07-V2-eSH-10-MH-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-MH | 10.7846 | 2.0891 | 762.7779 | 742.5482 | 2.6219 | 1505.3262 | 844.5333
DEER-SFAM-CZ07-V2-eSH-10-ML-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-ML | 10.6355 | 2.2282 | 783.2318 | 657.4196 | 2.6219 | 1440.6514 | 855.9067
DEER-SFAM-CZ07-V2-eSH-10-MM-s1 | 10 | CZ07 | V2 | CZ07-V2-eSH-10 | CZ07-V2-eSH-10-MM | 10.7446 | 2.1974 | 796.3664 | 717.5397 | 2.6219 | 1513.9061 | 865.668
DEER-SFAM-CZ07-V2-eSH-13-HH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-HH | 13.8923 | 1.6491 | 590.5343 | 682.9871 | 2.6219 | 1273.5214 | 658.2465
DEER-SFAM-CZ07-V2-eSH-13-HL-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-HL | 13.402 | 1.7411 | 592.5919 | 589.1731 | 2.9329 | 1181.7649 | 660.0807
DEER-SFAM-CZ07-V2-eSH-13-HM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-HM | 13.9174 | 1.6727 | 592.1646 | 607.8224 | 2.6219 | 1199.9869 | 653.0712
DEER-SFAM-CZ07-V2-eSH-13-LH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-LH | 13.8018 | 1.5971 | 583.7361 | 701.3024 | 2.6219 | 1285.0385 | 685.6048
DEER-SFAM-CZ07-V2-eSH-13-LL-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-LL | 14.3896 | 1.6365 | 575.0809 | 617.2392 | 2.6219 | 1192.32 | 636.6604
DEER-SFAM-CZ07-V2-eSH-13-LM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-LM | 13.3689 | 1.6855 | 611.0827 | 556.3173 | 2.6219 | 1167.3999 | 682.3433
DEER-SFAM-CZ07-V2-eSH-13-MH-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-MH | 14.3674 | 1.535 | 560.2993 | 685.9655 | 2.6219 | 1246.2647 | 628.8556
DEER-SFAM-CZ07-V2-eSH-13-ML-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-ML | 13.582 | 1.7173 | 606.6843 | 642.9629 | 2.6219 | 1249.6473 | 676.9999
DEER-SFAM-CZ07-V2-eSH-13-MM-s1 | 13 | CZ07 | V2 | CZ07-V2-eSH-13 | CZ07-V2-eSH-13-MM | 14.3302 | 1.659 | 578.5739 | 639.3607 | 2.6219 | 1217.9346 | 633.6228
DEER-SFAM-CZ07-V2-eSH-14-HH-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-HH | 14.7264 | 1.5723 | 556.7878 | 620.4545 | 2.6219 | 1177.2423 | 608.3511
DEER-SFAM-CZ07-V2-eSH-14-HL-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-HL | 14.6402 | 1.6142 | 558.2814 | 603.8598 | 2.6219 | 1162.1412 | 620.3474
DEER-SFAM-CZ07-V2-eSH-14-HM-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-HM | 14.5676 | 1.5738 | 559.244 | 599.1881 | 2.6219 | 1158.4321 | 603.1506
DEER-SFAM-CZ07-V2-eSH-14-MH-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-MH | 14.6019 | 1.4956 | 549.2072 | 633.4851 | 2.6219 | 1182.6923 | 616.0998
DEER-SFAM-CZ07-V2-eSH-14-ML-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-ML | 14.9852 | 1.5675 | 537.6962 | 656.1876 | 2.6219 | 1193.8837 | 621.6693
DEER-SFAM-CZ07-V2-eSH-14-MM-s1 | 14 | CZ07 | V2 | CZ07-V2-eSH-14 | CZ07-V2-eSH-14-MM | 14.5281 | 1.5473 | 548.6264 | 587.9581 | 2.6219 | 1136.5845 | 607.266
DEER-SFAM-CZ07-V2-eSH-15-HH-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-HH | 15.6186 | 1.4338 | 516.3056 | 708.0434 | 2.6219 | 1224.349 | 564.178
DEER-SFAM-CZ07-V2-eSH-15-HL-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-HL | 15.658 | 1.4919 | 521.6282 | 523.3914 | 2.6219 | 1045.0197 | 569.274
DEER-SFAM-CZ07-V2-eSH-15-HM-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-HM | 16.0465 | 1.4243 | 501.8439 | 544.4629 | 2.6219 | 1046.3068 | 549.5309
DEER-SFAM-CZ07-V2-eSH-15-MH-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-MH | 16.3348 | 1.4275 | 496.3026 | 630.7792 | 2.6219 | 1127.0817 | 542.3796
DEER-SFAM-CZ07-V2-eSH-15-ML-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-ML | 16.0107 | 1.4732 | 503.535 | 576.1869 | 2.6219 | 1079.722 | 550.9584
DEER-SFAM-CZ07-V2-eSH-15-MM-s1 | 15 | CZ07 | V2 | CZ07-V2-eSH-15 | CZ07-V2-eSH-15-MM | 16.1827 | 1.484 | 504.3927 | 615.1775 | 2.9329 | 1119.5702 | 554.679
DEER-SFAM-CZ07-V2-eSH-16-CH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-CH | 16.8276 | 1.6122 | 576.4656 | 599.7879 | 2.9329 | 1176.2535 | 615.5447
DEER-SFAM-CZ07-V2-eSH-16-CL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-CL | 16.9691 | 1.6288 | 572.3689 | 558.1771 | 2.9329 | 1130.5459 | 613.3551
DEER-SFAM-CZ07-V2-eSH-16-LH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-LH | 16.2426 | 1.4167 | 542.4837 | 676.0633 | 2.6219 | 1218.547 | 590.8449
DEER-SFAM-CZ07-V2-eSH-16-LL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-LL | 15.7573 | 1.5344 | 569.2056 | 605.7866 | 2.6219 | 1174.9921 | 607.9847
DEER-SFAM-CZ07-V2-eSH-16-LM-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-LM | 15.6926 | 1.4776 | 564.2938 | 674.2323 | 2.6219 | 1238.5261 | 618.3788
DEER-SFAM-CZ07-V2-eSH-16-TH-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-TH | 17.8511 | 1.4824 | 545.2884 | 750.1744 | 2.9329 | 1295.4628 | 583.0905
DEER-SFAM-CZ07-V2-eSH-16-TL-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-TL | 16.9764 | 1.6043 | 583.9093 | 730.192 | 2.6219 | 1314.1013 | 618.3689
DEER-SFAM-CZ07-V2-eSH-16-TM-s2 | 16 | CZ07 | V2 | CZ07-V2-eSH-16 | CZ07-V2-eSH-16-TM | 17.158 | 1.5823 | 577.7307 | 744.46 | 2.6219 | 1322.1907 | 612.9706
DEER-SFAM-CZ07-V2-eSH-17-CM-s2 | 17 | CZ07 | V2 | CZ07-V2-eSH-17 | CZ07-V2-eSH-17-CM | 17.9988 | 1.5362 | 539.6083 | 624.4684 | 2.9329 | 1164.0767 | 587.0447
DEER-SFAM-CZ07-V2-eSH-17-LM-s2 | 17 | CZ07 | V2 | CZ07-V2-eSH-17 | CZ07-V2-eSH-17-LM | 16.9526 | 1.4137 | 531.1072 | 589.9698 | 2.6219 | 1121.077 | 552.9476
DEER-SFAM-CZ07-V2-eSH-17-TH-s2 | 17 | CZ07 | V2 | CZ07-V2-eSH-17 | CZ07-V2-eSH-17-TH | 19.179 | 1.3716 | 503.1357 | 739.3056 | 2.6219 | 1242.4414 | 544.1541
DEER-SFAM-CZ07-V2-eSH-17-TL-s2 | 17 | CZ07 | V2 | CZ07-V2-eSH-17 | CZ07-V2-eSH-17-TL | 19.0275 | 1.3933 | 506.5233 | 729.1223 | 2.6219 | 1235.6456 | 547.157
DEER-SFAM-CZ07-V2-eSH-18-LH-s2 | 18 | CZ07 | V2 | CZ07-V2-eSH-18 | CZ07-V2-eSH-18-LH | 18.0624 | 1.3379 | 496.941 | 657.1092 | 2.6219 | 1154.0502 | 532.3358
DEER-SFAM-CZ07-V2-eSH-18-LL-s2 | 18 | CZ07 | V2 | CZ07-V2-eSH-18 | CZ07-V2-eSH-18-LL | 17.3292 | 1.3833 | 513.0851 | 600.9873 | 2.6219 | 1114.0724 | 546.5649
DEER-SFAM-CZ07-V2-eSH-18-LM-s2 | 18 | CZ07 | V2 | CZ07-V2-eSH-18 | CZ07-V2-eSH-18-LM | 17.9672 | 1.3598 | 501.2041 | 688.6305 | 2.6219 | 1189.8346 | 541.6447
DEER-SFAM-CZ07-V2-eSH-18-TM-s2 | 18 | CZ07 | V2 | CZ07-V2-eSH-18 | CZ07-V2-eSH-18-TM | 20.6324 | 1.2993 | 470.9227 | 716.5993 | 2.6219 | 1187.522 | 530.2953
DEER-SFAM-CZ07-V3-eSA-10-HH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-HH | 10.8138 | 2.534 | 1408.7464 | 0 | 2.8 | 1408.7464 | 1425.5909
DEER-SFAM-CZ07-V3-eSA-10-HL-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-HL | 10.8097 | 2.6485 | 1405.0199 | 0 | 2.8 | 1405.0199 | 1421.889
DEER-SFAM-CZ07-V3-eSA-10-HM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-HM | 10.7633 | 2.5996 | 1405.4692 | 0 | 2.8 | 1405.4692 | 1422.3339
DEER-SFAM-CZ07-V3-eSA-10-LH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-LH | 10.7321 | 2.5209 | 1362.7036 | 0 | 2.8 | 1362.7036 | 1379.5976
DEER-SFAM-CZ07-V3-eSA-10-LL-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-LL | 10.4931 | 2.7072 | 1443.8589 | 0 | 2.8 | 1443.8589 | 1460.7338
DEER-SFAM-CZ07-V3-eSA-10-LM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-LM | 10.6629 | 2.5601 | 1381.5639 | 0 | 2.8 | 1381.5639 | 1398.4589
DEER-SFAM-CZ07-V3-eSA-10-MH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-MH | 10.8101 | 2.4531 | 1363.203 | 0 | 2.8 | 1363.203 | 1380.0883
DEER-SFAM-CZ07-V3-eSA-10-ML-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-ML | 10.6738 | 2.7316 | 1445.5359 | 0 | 2.8 | 1445.5359 | 1462.406
DEER-SFAM-CZ07-V3-eSA-10-MM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSA-10 | CZ07-V3-eSA-10-MM | 10.9148 | 2.5097 | 1351.1926 | 0 | 2.8 | 1351.1926 | 1368.0655
DEER-SFAM-CZ07-V3-eSA-13-HH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-HH | 13.4075 | 1.9849 | 1079.3586 | 0 | 2.8 | 1079.3586 | 1094.5664
DEER-SFAM-CZ07-V3-eSA-13-HL-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-HL | 13.7932 | 2.0558 | 1066.3448 | 0 | 2.8 | 1066.3448 | 1079.6527
DEER-SFAM-CZ07-V3-eSA-13-HM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-HM | 13.6007 | 2.1492 | 1090.2239 | 0 | 3.2 | 1090.2239 | 1105.4472
DEER-SFAM-CZ07-V3-eSA-13-LH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-LH | 13.8287 | 1.8922 | 1048.3903 | 0 | 2.8 | 1048.3903 | 1065.2668
DEER-SFAM-CZ07-V3-eSA-13-LL-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-LL | 13.6883 | 2.026 | 1092.5111 | 0 | 2.8 | 1092.5111 | 1109.3284
DEER-SFAM-CZ07-V3-eSA-13-LM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-LM | 13.5301 | 1.9744 | 1092.1746 | 0 | 2.8 | 1092.1746 | 1109.0265
DEER-SFAM-CZ07-V3-eSA-13-MH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-MH | 14.748 | 1.9068 | 1015.0168 | 0 | 2.8 | 1015.0168 | 1031.8819
DEER-SFAM-CZ07-V3-eSA-13-ML-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-ML | 13.6025 | 2.0201 | 1075.702 | 0 | 2.8 | 1075.702 | 1092.5096
DEER-SFAM-CZ07-V3-eSA-13-MM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSA-13 | CZ07-V3-eSA-13-MM | 14.6644 | 1.9569 | 1020.7546 | 0 | 2.8 | 1020.7546 | 1037.6149
DEER-SFAM-CZ07-V3-eSA-14-HH-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-HH | 14.2128 | 1.9078 | 1023.7104 | 0 | 2.8 | 1023.7104 | 1037.842
DEER-SFAM-CZ07-V3-eSA-14-HL-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-HL | 14.9084 | 1.8957 | 986.8125 | 0 | 2.8 | 986.8125 | 997.2062
DEER-SFAM-CZ07-V3-eSA-14-HM-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-HM | 14.8324 | 1.904 | 987.3722 | 0 | 2.8 | 987.3722 | 1003.3236
DEER-SFAM-CZ07-V3-eSA-14-MH-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-MH | 14.4914 | 1.8342 | 1031.2199 | 0 | 2.8 | 1031.2199 | 1042.2956
DEER-SFAM-CZ07-V3-eSA-14-ML-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-ML | 14.3941 | 1.8923 | 1007.3776 | 0 | 2.8 | 1007.3776 | 1025.075
DEER-SFAM-CZ07-V3-eSA-14-MM-s1 | 14 | CZ07 | V3 | CZ07-V3-eSA-14 | CZ07-V3-eSA-14-MM | 14.6072 | 1.8029 | 1003.0647 | 0 | 2.8 | 1003.0647 | 1015.2118
DEER-SFAM-CZ07-V3-eSA-15-HH-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-HH | 15.9763 | 1.7871 | 920.4421 | 0 | 3.2 | 920.4421 | 932.2469
DEER-SFAM-CZ07-V3-eSA-15-HL-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-HL | 16.3238 | 1.7223 | 900.3492 | 0 | 2.8 | 900.3492 | 915.0298
DEER-SFAM-CZ07-V3-eSA-15-HM-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-HM | 15.6637 | 1.8093 | 937.1153 | 0 | 3.2 | 937.1153 | 948.9619
DEER-SFAM-CZ07-V3-eSA-15-MH-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-MH | 15.9539 | 1.7203 | 914.7801 | 0 | 2.8 | 914.7801 | 923.5629
DEER-SFAM-CZ07-V3-eSA-15-ML-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-ML | 16.0944 | 1.7648 | 929.1709 | 0 | 2.8 | 929.1709 | 940.9616
DEER-SFAM-CZ07-V3-eSA-15-MM-s1 | 15 | CZ07 | V3 | CZ07-V3-eSA-15 | CZ07-V3-eSA-15-MM | 15.7387 | 1.762 | 927.5355 | 0 | 2.8 | 927.5355 | 938.3037
DEER-SFAM-CZ07-V3-eSA-16-CH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-CH | 16.2333 | 1.9773 | 1030.3015 | 0 | 3.2 | 1030.3015 | 1037.0924
DEER-SFAM-CZ07-V3-eSA-16-CL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-CL | 16.8014 | 1.9156 | 976.7347 | 0 | 3.2 | 976.7347 | 985.3227
DEER-SFAM-CZ07-V3-eSA-16-CM-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-CM | 16.4547 | 1.9322 | 1000.6616 | 0 | 3.2 | 1000.6616 | 1009.7108
DEER-SFAM-CZ07-V3-eSA-16-LH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-LH | 16.6485 | 1.7189 | 933.506 | 0 | 2.8 | 933.506 | 945.1777
DEER-SFAM-CZ07-V3-eSA-16-LL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-LL | 15.988 | 1.7998 | 972.8159 | 0 | 2.8 | 972.8159 | 980.4712
DEER-SFAM-CZ07-V3-eSA-16-LM-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-LM | 15.941 | 1.7766 | 979.475 | 0 | 2.8 | 979.475 | 986.4112
DEER-SFAM-CZ07-V3-eSA-16-NM-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-NM | 16.8618 | 1.7254 | 959.8257 | 0 | 2.8 | 959.8257 | 966.6333
DEER-SFAM-CZ07-V3-eSA-16-TH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-TH | 17.3752 | 1.7894 | 960.4407 | 0 | 2.8 | 960.4407 | 964.8058
DEER-SFAM-CZ07-V3-eSA-16-TL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSA-16 | CZ07-V3-eSA-16-TL | 17.6743 | 1.8268 | 949.0251 | 0 | 2.8 | 949.0251 | 953.7341
DEER-SFAM-CZ07-V3-eSA-17-CH-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-CH | 17.3965 | 1.8401 | 950.5287 | 0 | 3.2 | 950.5287 | 959.1081
DEER-SFAM-CZ07-V3-eSA-17-CL-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-CL | 17.3806 | 1.862 | 951.6983 | 0 | 3.2 | 951.6983 | 960.2763
DEER-SFAM-CZ07-V3-eSA-17-CM-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-CM | 17.4683 | 1.8654 | 958.6128 | 0 | 3.2 | 958.6128 | 965.3845
DEER-SFAM-CZ07-V3-eSA-17-LH-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-LH | 17.2266 | 1.6486 | 894.3889 | 0 | 2.8 | 894.3889 | 903.5365
DEER-SFAM-CZ07-V3-eSA-17-LL-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-LL | 16.9678 | 1.7032 | 924.8281 | 0 | 2.8 | 924.8281 | 929.8045
DEER-SFAM-CZ07-V3-eSA-17-LM-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-LM | 16.766 | 1.6919 | 935.2239 | 0 | 2.8 | 935.2239 | 939.517
DEER-SFAM-CZ07-V3-eSA-17-TH-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-TH | 19.9191 | 1.5559 | 825.6897 | 0 | 2.8 | 825.6897 | 832.6711
DEER-SFAM-CZ07-V3-eSA-17-TL-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-TL | 19.7301 | 1.6606 | 823.5443 | 0 | 2.8 | 823.5443 | 834.4086
DEER-SFAM-CZ07-V3-eSA-17-TM-s2 | 17 | CZ07 | V3 | CZ07-V3-eSA-17 | CZ07-V3-eSA-17-TM | 19.0303 | 1.6998 | 905.0751 | 0 | 2.8 | 905.0751 | 908.727
DEER-SFAM-CZ07-V3-eSA-18-LH-s2 | 18 | CZ07 | V3 | CZ07-V3-eSA-18 | CZ07-V3-eSA-18-LH | 18.057 | 1.5883 | 868.7905 | 0 | 2.8 | 868.7905 | 874.7715
DEER-SFAM-CZ07-V3-eSA-18-LL-s2 | 18 | CZ07 | V3 | CZ07-V3-eSA-18 | CZ07-V3-eSA-18-LL | 18.1714 | 1.6056 | 856.0448 | 0 | 2.8 | 856.0448 | 863.8567
DEER-SFAM-CZ07-V3-eSA-18-TH-s2 | 18 | CZ07 | V3 | CZ07-V3-eSA-18 | CZ07-V3-eSA-18-TH | 20.5821 | 1.4817 | 798.8752 | 0 | 2.8 | 798.8752 | 803.615
DEER-SFAM-CZ07-V3-eSA-18-TL-s2 | 18 | CZ07 | V3 | CZ07-V3-eSA-18 | CZ07-V3-eSA-18-TL | 19.8607 | 1.5777 | 832.1547 | 0 | 2.8 | 832.1547 | 837.3607
DEER-SFAM-CZ07-V3-eSA-18-TM-s2 | 18 | CZ07 | V3 | CZ07-V3-eSA-18 | CZ07-V3-eSA-18-TM | 19.6939 | 1.536 | 833.1384 | 0 | 2.8 | 833.1384 | 837.9845
DEER-SFAM-CZ07-V3-eSH-10-HH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-HH | 10.6997 | 2.4839 | 1366.7253 | 321.0646 | 2.8 | 1687.7899 | 1399.7899
DEER-SFAM-CZ07-V3-eSH-10-HL-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-HL | 10.4711 | 2.6033 | 1416.6153 | 323.5903 | 2.8 | 1740.2056 | 1449.6056
DEER-SFAM-CZ07-V3-eSH-10-HM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-HM | 10.9406 | 2.5497 | 1381.3148 | 314.7042 | 2.8 | 1696.019 | 1412.719
DEER-SFAM-CZ07-V3-eSH-10-LH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-LH | 10.8234 | 2.409 | 1366.2511 | 340.2877 | 2.8 | 1706.5388 | 1400.4388
DEER-SFAM-CZ07-V3-eSH-10-LL-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-LL | 10.6178 | 2.6038 | 1417.8636 | 316.3415 | 2.8 | 1734.2051 | 1453.2051
DEER-SFAM-CZ07-V3-eSH-10-LM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-LM | 10.7779 | 2.5108 | 1393.4443 | 316.8937 | 2.8 | 1710.338 | 1425.938
DEER-SFAM-CZ07-V3-eSH-10-MH-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-MH | 10.8497 | 2.4623 | 1363.531 | 331.8839 | 2.8 | 1695.4149 | 1399.8149
DEER-SFAM-CZ07-V3-eSH-10-ML-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-ML | 10.6389 | 2.6625 | 1409.7548 | 296.1109 | 2.8 | 1705.8657 | 1442.2657
DEER-SFAM-CZ07-V3-eSH-10-MM-s1 | 10 | CZ07 | V3 | CZ07-V3-eSH-10 | CZ07-V3-eSH-10-MM | 10.8527 | 2.5671 | 1403.2014 | 321.8861 | 2.8 | 1725.0875 | 1434.0875
DEER-SFAM-CZ07-V3-eSH-13-HH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-HH | 14.0246 | 1.9661 | 1056.8922 | 307.3267 | 2.8 | 1364.2189 | 1087.0189
DEER-SFAM-CZ07-V3-eSH-13-HL-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-HL | 13.4452 | 2.1272 | 1079.9181 | 263.9631 | 3.2 | 1343.8812 | 1109.9812
DEER-SFAM-CZ07-V3-eSH-13-HM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-HM | 14.0442 | 1.989 | 1060.3511 | 273.6692 | 2.8 | 1334.0203 | 1087.5203
DEER-SFAM-CZ07-V3-eSH-13-LH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-LH | 13.8277 | 1.8951 | 1051.2916 | 310.5759 | 2.8 | 1361.8675 | 1096.2675
DEER-SFAM-CZ07-V3-eSH-13-LL-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-LL | 14.5644 | 1.9358 | 1023.3459 | 276.4432 | 2.8 | 1299.7891 | 1050.7891
DEER-SFAM-CZ07-V3-eSH-13-LM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-LM | 13.3324 | 2.0064 | 1103.463 | 248.162 | 2.8 | 1351.625 | 1135.125
DEER-SFAM-CZ07-V3-eSH-13-MH-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-MH | 14.7268 | 1.8234 | 992.7267 | 308.0846 | 2.8 | 1300.8113 | 1023.1113
DEER-SFAM-CZ07-V3-eSH-13-ML-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-ML | 13.5369 | 2.0554 | 1091.8264 | 284.4735 | 2.8 | 1376.2999 | 1122.9999
DEER-SFAM-CZ07-V3-eSH-13-MM-s1 | 13 | CZ07 | V3 | CZ07-V3-eSH-13 | CZ07-V3-eSH-13-MM | 14.3986 | 1.97 | 1035.3544 | 287.6831 | 2.8 | 1323.0375 | 1059.8375
DEER-SFAM-CZ07-V3-eSH-14-HH-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-HH | 14.8076 | 1.8793 | 1000.9123 | 279.3575 | 2.8 | 1280.2698 | 1023.8698
DEER-SFAM-CZ07-V3-eSH-14-HL-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-HL | 14.6425 | 1.932 | 1010.7474 | 270.5571 | 2.8 | 1281.3045 | 1038.3045
DEER-SFAM-CZ07-V3-eSH-14-HM-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-HM | 14.6169 | 1.8787 | 1007.8417 | 269.3651 | 2.8 | 1277.2068 | 1027.4068
DEER-SFAM-CZ07-V3-eSH-14-MH-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-MH | 14.6288 | 1.7733 | 988.5806 | 281.8917 | 2.8 | 1270.4723 | 1018.2723
DEER-SFAM-CZ07-V3-eSH-14-ML-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-ML | 14.8696 | 1.8729 | 974.7159 | 287.9437 | 2.8 | 1262.6596 | 1011.7596
DEER-SFAM-CZ07-V3-eSH-14-MM-s1 | 14 | CZ07 | V3 | CZ07-V3-eSH-14 | CZ07-V3-eSH-14-MM | 14.3936 | 1.8489 | 1003.7424 | 262.1981 | 2.8 | 1265.9405 | 1029.7405
DEER-SFAM-CZ07-V3-eSH-15-HH-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-HH | 15.8096 | 1.7068 | 923.9201 | 312.4789 | 2.8 | 1236.399 | 945.099
DEER-SFAM-CZ07-V3-eSH-15-HL-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-HL | 15.6918 | 1.787 | 941.9333 | 235.9055 | 2.8 | 1177.8388 | 963.1388
DEER-SFAM-CZ07-V3-eSH-15-HM-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-HM | 16.2149 | 1.7017 | 906.7712 | 246.2259 | 2.8 | 1152.9971 | 927.8971
DEER-SFAM-CZ07-V3-eSH-15-MH-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-MH | 16.2753 | 1.7128 | 896.2932 | 277.2202 | 2.8 | 1173.5134 | 916.6134
DEER-SFAM-CZ07-V3-eSH-15-ML-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-ML | 15.8666 | 1.7678 | 914.5694 | 254.4748 | 2.8 | 1169.0442 | 935.5442
DEER-SFAM-CZ07-V3-eSH-15-MM-s1 | 15 | CZ07 | V3 | CZ07-V3-eSH-15 | CZ07-V3-eSH-15-MM | 16.5069 | 1.7157 | 897.3642 | 273.9054 | 2.8 | 1171.2696 | 919.6696
DEER-SFAM-CZ07-V3-eSH-16-CH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-CH | 16.7059 | 1.9229 | 999.7268 | 258.8205 | 3.2 | 1258.5473 | 1016.9473
DEER-SFAM-CZ07-V3-eSH-16-CL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-CL | 16.7652 | 1.9449 | 997.2479 | 241.607 | 3.2 | 1238.8549 | 1015.3549
DEER-SFAM-CZ07-V3-eSH-16-LH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-LH | 16.8607 | 1.6535 | 916.6864 | 295.5417 | 2.8 | 1212.2281 | 937.8281
DEER-SFAM-CZ07-V3-eSH-16-LL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-LL | 15.9243 | 1.8042 | 983.0631 | 262.0732 | 2.8 | 1245.1363 | 1000.0363
DEER-SFAM-CZ07-V3-eSH-16-LM-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-LM | 16.1281 | 1.7304 | 965.1765 | 293.9093 | 2.8 | 1259.0858 | 988.7858
DEER-SFAM-CZ07-V3-eSH-16-TH-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-TH | 18.6499 | 1.6967 | 881.4223 | 320.5049 | 2.8 | 1201.9272 | 898.2272
DEER-SFAM-CZ07-V3-eSH-16-TL-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-TL | 17.0132 | 1.8662 | 979.6374 | 306.6416 | 2.8 | 1286.279 | 994.479
DEER-SFAM-CZ07-V3-eSH-16-TM-s2 | 16 | CZ07 | V3 | CZ07-V3-eSH-16 | CZ07-V3-eSH-16-TM | 17.2118 | 1.8369 | 968.3366 | 313.0687 | 2.8 | 1281.4053 | 983.5053
DEER-SFAM-CZ07-V3-eSH-17-CM-s2 | 17 | CZ07 | V3 | CZ07-V3-eSH-17 | CZ07-V3-eSH-17-CM | 17.7832 | 1.8348 | 939.8293 | 263.0053 | 3.2 | 1202.8346 | 960.2346
DEER-SFAM-CZ07-V3-eSH-17-LM-s2 | 17 | CZ07 | V3 | CZ07-V3-eSH-17 | CZ07-V3-eSH-17-LM | 17.2717 | 1.6527 | 910.3419 | 255.2586 | 2.8 | 1165.6005 | 919.9005
DEER-SFAM-CZ07-V3-eSH-17-TH-s2 | 17 | CZ07 | V3 | CZ07-V3-eSH-17 | CZ07-V3-eSH-17-TH | 19.6371 | 1.5954 | 836.5561 | 317.1586 | 2.8 | 1153.7147 | 854.4147
DEER-SFAM-CZ07-V3-eSH-17-TL-s2 | 17 | CZ07 | V3 | CZ07-V3-eSH-17 | CZ07-V3-eSH-17-TL | 19.4621 | 1.6262 | 843.5189 | 311.5642 | 2.8 | 1155.0831 | 861.1831
DEER-SFAM-CZ07-V3-eSH-18-LH-s2 | 18 | CZ07 | V3 | CZ07-V3-eSH-18 | CZ07-V3-eSH-18-LH | 18.3265 | 1.5695 | 851.8367 | 281.5098 | 2.8 | 1133.3465 | 867.1465
DEER-SFAM-CZ07-V3-eSH-18-LL-s2 | 18 | CZ07 | V3 | CZ07-V3-eSH-18 | CZ07-V3-eSH-18-LL | 17.4639 | 1.6304 | 890.5618 | 259.1977 | 2.8 | 1149.7595 | 905.1595
DEER-SFAM-CZ07-V3-eSH-18-LM-s2 | 18 | CZ07 | V3 | CZ07-V3-eSH-18 | CZ07-V3-eSH-18-LM | 18.2751 | 1.5955 | 858.3111 | 294.559 | 2.8 | 1152.8701 | 875.7701
DEER-SFAM-CZ07-V3-eSH-18-TM-s2 | 18 | CZ07 | V3 | CZ07-V3-eSH-18 | CZ07-V3-eSH-18-TM | 21.1058 | 1.522 | 779.4943 | 304.8521 | 2.8 | 1084.3464 | 805.2464
DEER-SFAM-CZ07-V4-eSA-10-HH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-HH | 10.6798 | 2.6654 | 1402.5311 | 0 | 3.2 | 1402.5311 | 1413.6821
DEER-SFAM-CZ07-V4-eSA-10-HL-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-HL | 10.7256 | 2.7719 | 1392.9807 | 0 | 3.2 | 1392.9807 | 1404.1468
DEER-SFAM-CZ07-V4-eSA-10-HM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-HM | 10.6612 | 2.729 | 1395.7766 | 0 | 3.2 | 1395.7766 | 1406.9401
DEER-SFAM-CZ07-V4-eSA-10-LH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-LH | 10.5946 | 2.6468 | 1361.381 | 0 | 3.2 | 1361.381 | 1372.5627
DEER-SFAM-CZ07-V4-eSA-10-LL-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-LL | 10.4336 | 2.8267 | 1431.7888 | 0 | 3.2 | 1431.7888 | 1442.9586
DEER-SFAM-CZ07-V4-eSA-10-LM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-LM | 10.5428 | 2.6885 | 1379.4002 | 0 | 3.2 | 1379.4002 | 1390.5824
DEER-SFAM-CZ07-V4-eSA-10-MH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-MH | 10.6091 | 2.5904 | 1363.0562 | 0 | 3.2 | 1363.0562 | 1374.2322
DEER-SFAM-CZ07-V4-eSA-10-ML-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-ML | 10.6138 | 2.8569 | 1437.7432 | 0 | 3.2 | 1437.7432 | 1448.9099
DEER-SFAM-CZ07-V4-eSA-10-MM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSA-10 | CZ07-V4-eSA-10-MM | 10.8992 | 2.5099 | 1313.6212 | 0 | 2.8 | 1313.6212 | 1324.7714
DEER-SFAM-CZ07-V4-eSA-13-HH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-HH | 13.2429 | 2.0784 | 1072.8444 | 0 | 3.2 | 1072.8444 | 1082.9108
DEER-SFAM-CZ07-V4-eSA-13-HL-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-HL | 13.7263 | 2.1356 | 1053.774 | 0 | 3.2 | 1053.774 | 1062.5834
DEER-SFAM-CZ07-V4-eSA-13-HM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-HM | 13.6111 | 2.1355 | 1068.1871 | 0 | 3.2 | 1068.1871 | 1078.2476
DEER-SFAM-CZ07-V4-eSA-13-LH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-LH | 13.8092 | 1.8925 | 1021.8763 | 0 | 2.8 | 1021.8763 | 1033.0295
DEER-SFAM-CZ07-V4-eSA-13-LL-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-LL | 13.6835 | 2.0248 | 1064.6853 | 0 | 2.8 | 1064.6853 | 1075.7973
DEER-SFAM-CZ07-V4-eSA-13-LM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-LM | 13.5241 | 1.9736 | 1064.0425 | 0 | 2.8 | 1064.0425 | 1075.1781
DEER-SFAM-CZ07-V4-eSA-13-MH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-MH | 14.5557 | 2.0028 | 1014.5851 | 0 | 3.2 | 1014.5851 | 1025.749
DEER-SFAM-CZ07-V4-eSA-13-ML-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-ML | 13.5251 | 2.1034 | 1061.8804 | 0 | 3.2 | 1061.8804 | 1073.0069
DEER-SFAM-CZ07-V4-eSA-13-MM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSA-13 | CZ07-V4-eSA-13-MM | 14.5305 | 2.0449 | 1016.6984 | 0 | 3.2 | 1016.6984 | 1027.8596
DEER-SFAM-CZ07-V4-eSA-14-HH-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-HH | 14.0847 | 1.9893 | 1020.6361 | 0 | 3.2 | 1020.6361 | 1029.991
DEER-SFAM-CZ07-V4-eSA-14-HL-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-HL | 14.8258 | 1.9721 | 978.1607 | 0 | 3.2 | 978.1607 | 985.0409
DEER-SFAM-CZ07-V4-eSA-14-HM-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-HM | 14.7412 | 1.9863 | 979.9961 | 0 | 3.2 | 979.9961 | 990.5548
DEER-SFAM-CZ07-V4-eSA-14-MH-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-MH | 14.4839 | 1.8336 | 1005.6981 | 0 | 2.8 | 1005.6981 | 1013.0171
DEER-SFAM-CZ07-V4-eSA-14-ML-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-ML | 14.2904 | 1.9751 | 995.7859 | 0 | 3.2 | 995.7859 | 1007.5006
DEER-SFAM-CZ07-V4-eSA-14-MM-s1 | 14 | CZ07 | V4 | CZ07-V4-eSA-14 | CZ07-V4-eSA-14-MM | 14.5994 | 1.8016 | 977.7426 | 0 | 2.8 | 977.7426 | 985.7696
DEER-SFAM-CZ07-V4-eSA-15-HH-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-HH | 15.9841 | 1.7759 | 901.8732 | 0 | 3.2 | 901.8732 | 909.6745
DEER-SFAM-CZ07-V4-eSA-15-HL-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-HL | 16.2096 | 1.7947 | 892.4033 | 0 | 3.2 | 892.4033 | 902.1217
DEER-SFAM-CZ07-V4-eSA-15-HM-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-HM | 15.6784 | 1.797 | 918.3054 | 0 | 3.2 | 918.3054 | 926.1342
DEER-SFAM-CZ07-V4-eSA-15-MH-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-MH | 15.7672 | 1.7986 | 910.3587 | 0 | 3.2 | 910.3587 | 916.1726
DEER-SFAM-CZ07-V4-eSA-15-ML-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-ML | 15.9919 | 1.8449 | 923.3887 | 0 | 3.2 | 923.3887 | 931.1952
DEER-SFAM-CZ07-V4-eSA-15-MM-s1 | 15 | CZ07 | V4 | CZ07-V4-eSA-15 | CZ07-V4-eSA-15-MM | 15.6305 | 1.8353 | 921.0998 | 0 | 3.2 | 921.0998 | 928.2277
DEER-SFAM-CZ07-V4-eSA-16-CH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-CH | 16.2915 | 1.9633 | 1007.7113 | 0 | 3.2 | 1007.7113 | 1012.2043
DEER-SFAM-CZ07-V4-eSA-16-CL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-CL | 16.859 | 1.9007 | 954.8848 | 0 | 3.2 | 954.8848 | 960.5664
DEER-SFAM-CZ07-V4-eSA-16-CM-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-CM | 16.4997 | 1.918 | 978.6799 | 0 | 3.2 | 978.6799 | 984.6675
DEER-SFAM-CZ07-V4-eSA-16-LH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-LH | 16.5419 | 1.771 | 928.8389 | 0 | 3.2 | 928.8389 | 936.5709
DEER-SFAM-CZ07-V4-eSA-16-LL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-LL | 15.9273 | 1.8483 | 967.1343 | 0 | 3.2 | 967.1343 | 972.2047
DEER-SFAM-CZ07-V4-eSA-16-LM-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-LM | 15.893 | 1.8359 | 971.3218 | 0 | 3.2 | 971.3218 | 975.916
DEER-SFAM-CZ07-V4-eSA-16-NM-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-NM | 17.0326 | 1.7506 | 938.9501 | 0 | 3.2 | 938.9501 | 943.4602
DEER-SFAM-CZ07-V4-eSA-16-TH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-TH | 17.4664 | 1.8621 | 957.6095 | 0 | 3.2 | 957.6095 | 960.5033
DEER-SFAM-CZ07-V4-eSA-16-TL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSA-16 | CZ07-V4-eSA-16-TL | 17.9157 | 1.8824 | 934.4282 | 0 | 3.2 | 934.4282 | 937.5482
DEER-SFAM-CZ07-V4-eSA-17-CH-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-CH | 17.462 | 1.8263 | 929.1276 | 0 | 3.2 | 929.1276 | 934.8035
DEER-SFAM-CZ07-V4-eSA-17-CL-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-CL | 17.4363 | 1.8467 | 930.777 | 0 | 3.2 | 930.777 | 936.4519
DEER-SFAM-CZ07-V4-eSA-17-CM-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-CM | 17.5275 | 1.8497 | 937.868 | 0 | 3.2 | 937.868 | 942.3479
DEER-SFAM-CZ07-V4-eSA-17-LH-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-LH | 17.1463 | 1.6948 | 888.284 | 0 | 3.2 | 888.284 | 894.343
DEER-SFAM-CZ07-V4-eSA-17-LL-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-LL | 16.9428 | 1.7547 | 919.9775 | 0 | 3.2 | 919.9775 | 923.2725
DEER-SFAM-CZ07-V4-eSA-17-LM-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-LM | 16.7095 | 1.7469 | 929.4898 | 0 | 3.2 | 929.4898 | 932.3327
DEER-SFAM-CZ07-V4-eSA-17-TH-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-TH | 19.9263 | 1.6234 | 823.5941 | 0 | 3.2 | 823.5941 | 828.2215
DEER-SFAM-CZ07-V4-eSA-17-TL-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-TL | 20.2989 | 1.7027 | 800.2155 | 0 | 3.2 | 800.2155 | 807.4199
DEER-SFAM-CZ07-V4-eSA-17-TM-s2 | 17 | CZ07 | V4 | CZ07-V4-eSA-17 | CZ07-V4-eSA-17-TM | 19.1774 | 1.7717 | 897.3032 | 0 | 3.2 | 897.3032 | 899.7228
DEER-SFAM-CZ07-V4-eSA-18-LH-s2 | 18 | CZ07 | V4 | CZ07-V4-eSA-18 | CZ07-V4-eSA-18-LH | 17.9798 | 1.6347 | 862.3404 | 0 | 3.2 | 862.3404 | 866.3018
DEER-SFAM-CZ07-V4-eSA-18-LL-s2 | 18 | CZ07 | V4 | CZ07-V4-eSA-18 | CZ07-V4-eSA-18-LL | 18.2288 | 1.6464 | 844.741 | 0 | 3.2 | 844.741 | 849.9153
DEER-SFAM-CZ07-V4-eSA-18-TH-s2 | 18 | CZ07 | V4 | CZ07-V4-eSA-18 | CZ07-V4-eSA-18-TH | 20.4948 | 1.5467 | 799.1056 | 0 | 3.2 | 799.1056 | 802.2463
DEER-SFAM-CZ07-V4-eSA-18-TL-s2 | 18 | CZ07 | V4 | CZ07-V4-eSA-18 | CZ07-V4-eSA-18-TL | 19.9901 | 1.6431 | 825.3823 | 0 | 3.2 | 825.3823 | 828.8334
DEER-SFAM-CZ07-V4-eSA-18-TM-s2 | 18 | CZ07 | V4 | CZ07-V4-eSA-18 | CZ07-V4-eSA-18-TM | 19.6947 | 1.599 | 830.6711 | 0 | 3.2 | 830.6711 | 833.883
DEER-SFAM-CZ07-V4-eSH-10-HH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-HH | 10.5201 | 2.6155 | 1366.0656 | 216.7339 | 3.2 | 1582.7995 | 1388.1995
DEER-SFAM-CZ07-V4-eSH-10-HL-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-HL | 10.3482 | 2.739 | 1401.9231 | 217.7487 | 3.2 | 1619.6718 | 1423.9718
DEER-SFAM-CZ07-V4-eSH-10-HM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-HM | 10.8084 | 2.6772 | 1381.0656 | 212.4066 | 3.2 | 1593.4722 | 1402.0722
DEER-SFAM-CZ07-V4-eSH-10-LH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-LH | 10.6088 | 2.5537 | 1367.6448 | 230.2753 | 3.2 | 1597.9201 | 1390.5201
DEER-SFAM-CZ07-V4-eSH-10-LL-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-LL | 10.506 | 2.7364 | 1406.6247 | 213.573 | 3.2 | 1620.1977 | 1430.2977
DEER-SFAM-CZ07-V4-eSH-10-LM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-LM | 10.6121 | 2.6399 | 1390.0775 | 214.2632 | 3.2 | 1604.3407 | 1411.8407
DEER-SFAM-CZ07-V4-eSH-10-MH-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-MH | 10.6766 | 2.5999 | 1360.8447 | 224.0768 | 3.2 | 1584.9215 | 1385.1215
DEER-SFAM-CZ07-V4-eSH-10-ML-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-ML | 10.561 | 2.7782 | 1401.7451 | 199.9968 | 3.2 | 1601.7419 | 1423.5419
DEER-SFAM-CZ07-V4-eSH-10-MM-s1 | 10 | CZ07 | V4 | CZ07-V4-eSH-10 | CZ07-V4-eSH-10-MM | 10.8471 | 2.5676 | 1368.8771 | 215.2119 | 2.8 | 1584.089 | 1389.489
DEER-SFAM-CZ07-V4-eSH-13-HH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-HH | 13.8209 | 2.0668 | 1058.2041 | 207.6726 | 3.2 | 1265.8767 | 1078.3767
DEER-SFAM-CZ07-V4-eSH-13-HL-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-HL | 13.4532 | 2.112 | 1059.359 | 176.4752 | 3.2 | 1235.8342 | 1079.4342
DEER-SFAM-CZ07-V4-eSH-13-HM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-HM | 13.88 | 2.0837 | 1058.3288 | 184.6945 | 3.2 | 1243.0233 | 1076.5233
DEER-SFAM-CZ07-V4-eSH-13-LH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-LH | 13.6138 | 2.0011 | 1045.6703 | 210.4169 | 3.2 | 1256.0872 | 1075.7872
DEER-SFAM-CZ07-V4-eSH-13-LL-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-LL | 14.4154 | 2.0195 | 1019.8901 | 185.9863 | 3.2 | 1205.8764 | 1038.2764
DEER-SFAM-CZ07-V4-eSH-13-LM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-LM | 13.3216 | 2.005 | 1075.0127 | 165.6109 | 2.8 | 1240.6236 | 1096.1236
DEER-SFAM-CZ07-V4-eSH-13-MH-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-MH | 14.4672 | 1.9152 | 996.8561 | 209.1272 | 3.2 | 1205.9833 | 1017.1833
DEER-SFAM-CZ07-V4-eSH-13-ML-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-ML | 13.4548 | 2.1464 | 1084.8791 | 190.7503 | 3.2 | 1275.6294 | 1105.7294
DEER-SFAM-CZ07-V4-eSH-13-MM-s1 | 13 | CZ07 | V4 | CZ07-V4-eSH-13 | CZ07-V4-eSH-13-MM | 14.2638 | 2.061 | 1031.0932 | 193.5671 | 3.2 | 1224.6603 | 1047.4603
DEER-SFAM-CZ07-V4-eSH-14-HH-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-HH | 14.6312 | 1.9695 | 998.3057 | 188.4717 | 3.2 | 1186.7774 | 1013.6774
DEER-SFAM-CZ07-V4-eSH-14-HL-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-HL | 14.5617 | 2.0126 | 1001.147 | 181.948 | 3.2 | 1183.095 | 1019.595
DEER-SFAM-CZ07-V4-eSH-14-HM-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-HM | 14.4588 | 1.965 | 1004.1451 | 181.7065 | 3.2 | 1185.8516 | 1017.2516
DEER-SFAM-CZ07-V4-eSH-14-MH-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-MH | 14.6037 | 1.7728 | 964.2893 | 188.9322 | 2.8 | 1153.2215 | 984.1215
DEER-SFAM-CZ07-V4-eSH-14-ML-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-ML | 14.775 | 1.9502 | 967.3047 | 193.7178 | 3.2 | 1161.0225 | 992.1225
DEER-SFAM-CZ07-V4-eSH-14-MM-s1 | 14 | CZ07 | V4 | CZ07-V4-eSH-14 | CZ07-V4-eSH-14-MM | 14.2757 | 1.9348 | 987.4151 | 176.4945 | 3.2 | 1163.9096 | 1004.8096
DEER-SFAM-CZ07-V4-eSH-15-HH-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-HH | 15.6091 | 1.7832 | 922.5967 | 210.092 | 3.2 | 1132.6887 | 936.7887
DEER-SFAM-CZ07-V4-eSH-15-HL-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-HL | 15.5816 | 1.8595 | 934.727 | 158.6894 | 3.2 | 1093.4164 | 948.9164
DEER-SFAM-CZ07-V4-eSH-15-HM-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-HM | 16.0868 | 1.7748 | 896.8246 | 166.2336 | 3.2 | 1063.0582 | 910.9582
DEER-SFAM-CZ07-V4-eSH-15-MH-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-MH | 16.1229 | 1.7898 | 889.6345 | 186.1982 | 3.2 | 1075.8327 | 903.2327
DEER-SFAM-CZ07-V4-eSH-15-ML-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-ML | 15.7773 | 1.8363 | 906.2707 | 171.1489 | 3.2 | 1077.4196 | 920.3196
DEER-SFAM-CZ07-V4-eSH-15-MM-s1 | 15 | CZ07 | V4 | CZ07-V4-eSH-15 | CZ07-V4-eSH-15-MM | 16.3879 | 1.7874 | 888.5661 | 184.6451 | 3.2 | 1073.2112 | 903.5112
DEER-SFAM-CZ07-V4-eSH-16-CH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-CH | 16.7488 | 1.908 | 979.1217 | 174.3318 | 3.2 | 1153.4535 | 990.6535
DEER-SFAM-CZ07-V4-eSH-16-CL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-CL | 16.8228 | 1.9324 | 976.0139 | 163.1153 | 3.2 | 1139.1292 | 988.1292
DEER-SFAM-CZ07-V4-eSH-16-LH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-LH | 16.6168 | 1.708 | 918.172 | 200.6464 | 3.2 | 1118.8184 | 932.3184
DEER-SFAM-CZ07-V4-eSH-16-LL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-LL | 15.8942 | 1.859 | 975.3699 | 176.181 | 3.2 | 1151.5509 | 986.7509
DEER-SFAM-CZ07-V4-eSH-16-LM-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-LM | 15.9294 | 1.7879 | 964.4635 | 199.2141 | 3.2 | 1163.6776 | 980.2776
DEER-SFAM-CZ07-V4-eSH-16-TH-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-TH | 18.6548 | 1.7552 | 878.3557 | 218.6976 | 3.2 | 1097.0533 | 889.2533
DEER-SFAM-CZ07-V4-eSH-16-TL-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-TL | 17.2896 | 1.9382 | 964.4166 | 207.1122 | 3.2 | 1171.5288 | 974.0288
DEER-SFAM-CZ07-V4-eSH-16-TM-s2 | 16 | CZ07 | V4 | CZ07-V4-eSH-16 | CZ07-V4-eSH-16-TM | 17.4653 | 1.9113 | 954.7161 | 211.3204 | 3.2 | 1166.0365 | 964.5365
DEER-SFAM-CZ07-V4-eSH-17-CM-s2 | 17 | CZ07 | V4 | CZ07-V4-eSH-17 | CZ07-V4-eSH-17-CM | 17.8322 | 1.8223 | 920.4227 | 175.9853 | 3.2 | 1096.408 | 934.008
DEER-SFAM-CZ07-V4-eSH-17-LM-s2 | 17 | CZ07 | V4 | CZ07-V4-eSH-17 | CZ07-V4-eSH-17-LM | 17.1643 | 1.7169 | 908.2948 | 172.206 | 3.2 | 1080.5008 | 914.7008
DEER-SFAM-CZ07-V4-eSH-17-TH-s2 | 17 | CZ07 | V4 | CZ07-V4-eSH-17 | CZ07-V4-eSH-17-TH | 19.7203 | 1.6551 | 829.6738 | 215.1961 | 3.2 | 1044.8699 | 841.2699
DEER-SFAM-CZ07-V4-eSH-17-TL-s2 | 17 | CZ07 | V4 | CZ07-V4-eSH-17 | CZ07-V4-eSH-17-TL | 19.5716 | 1.6881 | 836.6985 | 211.5708 | 3.2 | 1048.2693 | 848.1693
DEER-SFAM-CZ07-V4-eSH-18-LH-s2 | 18 | CZ07 | V4 | CZ07-V4-eSH-18 | CZ07-V4-eSH-18-LH | 18.2717 | 1.6213 | 847.112 | 189.6176 | 3.2 | 1036.7296 | 857.2296
DEER-SFAM-CZ07-V4-eSH-18-LL-s2 | 18 | CZ07 | V4 | CZ07-V4-eSH-18 | CZ07-V4-eSH-18-LL | 17.4248 | 1.6845 | 881.9403 | 174.9779 | 3.2 | 1056.9182 | 891.7182
DEER-SFAM-CZ07-V4-eSH-18-LM-s2 | 18 | CZ07 | V4 | CZ07-V4-eSH-18 | CZ07-V4-eSH-18-LM | 18.2421 | 1.6431 | 852.6607 | 198.392 | 3.2 | 1051.0527 | 864.1527
DEER-SFAM-CZ07-V4-eSH-18-TM-s2 | 18 | CZ07 | V4 | CZ07-V4-eSH-18 | CZ07-V4-eSH-18-TM | 21.2494 | 1.5851 | 773.4178 | 207.228 | 3.2 | 980.6458 | 790.2458
DEER-SFAM-CZ08-V1-eSA-10-HH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-HH | 10.2322 | 3.2868 | 1735.8992 | 0 | 3.0988 | 1735.8992 | 1812.2555
DEER-SFAM-CZ08-V1-eSA-10-HL-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-HL | 10.0056 | 3.587 | 1749.0612 | 0 | 3.0988 | 1749.0612 | 1825.4898
DEER-SFAM-CZ08-V1-eSA-10-HM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-HM | 9.9807 | 3.459 | 1731.3505 | 0 | 3.0988 | 1731.3505 | 1807.7665
DEER-SFAM-CZ08-V1-eSA-10-LH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-LH | 10.7784 | 3.2777 | 1615.9815 | 0 | 3.0988 | 1615.9815 | 1692.4832
DEER-SFAM-CZ08-V1-eSA-10-LL-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-LL | 10.0051 | 3.4754 | 1741.2689 | 0 | 3.0988 | 1741.2689 | 1817.7146
DEER-SFAM-CZ08-V1-eSA-10-LM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-LM | 10.634 | 3.3 | 1643.2635 | 0 | 3.0988 | 1643.2635 | 1719.7679
DEER-SFAM-CZ08-V1-eSA-10-MH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-MH | 10.6785 | 3.1831 | 1635.4804 | 0 | 3.0988 | 1635.4804 | 1711.9565
DEER-SFAM-CZ08-V1-eSA-10-ML-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-ML | 10.011 | 3.5195 | 1775.2781 | 0 | 3.0988 | 1775.2781 | 1851.7083
DEER-SFAM-CZ08-V1-eSA-10-MM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSA-10 | CZ08-V1-eSA-10-MM | 10.7466 | 3.0851 | 1598.9867 | 0 | 2.8241 | 1598.9867 | 1675.3692
DEER-SFAM-CZ08-V1-eSA-13-HH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-HH | 12.8072 | 2.681 | 1313.1164 | 0 | 3.0988 | 1313.1164 | 1382.0117
DEER-SFAM-CZ08-V1-eSA-13-HL-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-HL | 13.3181 | 2.8591 | 1283.9409 | 0 | 3.0988 | 1283.9409 | 1344.2358
DEER-SFAM-CZ08-V1-eSA-13-HM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-HM | 13.0673 | 2.7673 | 1305.9731 | 0 | 3.0988 | 1305.9731 | 1374.8412
DEER-SFAM-CZ08-V1-eSA-13-LH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-LH | 13.674 | 2.5095 | 1248.3008 | 0 | 3.0988 | 1248.3008 | 1324.7513
DEER-SFAM-CZ08-V1-eSA-13-LL-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-LL | 13.2974 | 2.6984 | 1315.797 | 0 | 3.0988 | 1315.797 | 1392.075
DEER-SFAM-CZ08-V1-eSA-13-LM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-LM | 13.4343 | 2.4634 | 1289.095 | 0 | 2.8241 | 1289.095 | 1365.4117
DEER-SFAM-CZ08-V1-eSA-13-MH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-MH | 14.1982 | 2.6081 | 1248.5708 | 0 | 3.0988 | 1248.5708 | 1324.9872
DEER-SFAM-CZ08-V1-eSA-13-ML-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-ML | 13.0759 | 2.7686 | 1291.7524 | 0 | 3.0988 | 1291.7524 | 1367.9282
DEER-SFAM-CZ08-V1-eSA-13-MM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSA-13 | CZ08-V1-eSA-13-MM | 13.9004 | 2.6245 | 1258.7479 | 0 | 3.0988 | 1258.7479 | 1335.1518
DEER-SFAM-CZ08-V1-eSA-14-HH-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-HH | 13.4939 | 2.6422 | 1250.0996 | 0 | 3.0988 | 1250.0996 | 1314.1416
DEER-SFAM-CZ08-V1-eSA-14-HL-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-HL | 14.5352 | 2.6113 | 1190.3282 | 0 | 3.0988 | 1190.3282 | 1237.4226
DEER-SFAM-CZ08-V1-eSA-14-HM-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-HM | 14.3904 | 2.7189 | 1192.1816 | 0 | 3.0988 | 1192.1816 | 1264.4407
DEER-SFAM-CZ08-V1-eSA-14-MH-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-MH | 14.3875 | 2.2816 | 1226.3962 | 0 | 2.8241 | 1226.3962 | 1276.5576
DEER-SFAM-CZ08-V1-eSA-14-ML-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-ML | 14.0933 | 2.6083 | 1195.7812 | 0 | 3.0988 | 1195.7812 | 1275.9701
DEER-SFAM-CZ08-V1-eSA-14-MM-s1 | 14 | CZ08 | V1 | CZ08-V1-eSA-14 | CZ08-V1-eSA-14-MM | 14.4397 | 2.2928 | 1191.6393 | 0 | 2.8241 | 1191.6393 | 1246.6413
DEER-SFAM-CZ08-V1-eSA-15-HH-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-HH | 15.141 | 2.3633 | 1117.3222 | 0 | 3.0988 | 1117.3222 | 1170.7153
DEER-SFAM-CZ08-V1-eSA-15-HL-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-HL | 15.7623 | 2.4225 | 1092.7004 | 0 | 3.0988 | 1092.7004 | 1159.2371
DEER-SFAM-CZ08-V1-eSA-15-HM-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-HM | 14.9058 | 2.3585 | 1129.6893 | 0 | 3.0988 | 1129.6893 | 1183.2779
DEER-SFAM-CZ08-V1-eSA-15-MH-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-MH | 15.2347 | 2.4589 | 1112.995 | 0 | 3.0988 | 1112.995 | 1152.7814
DEER-SFAM-CZ08-V1-eSA-15-ML-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-ML | 15.4676 | 2.4093 | 1135.054 | 0 | 3.0988 | 1135.054 | 1188.5362
DEER-SFAM-CZ08-V1-eSA-15-MM-s1 | 15 | CZ08 | V1 | CZ08-V1-eSA-15 | CZ08-V1-eSA-15-MM | 15.3542 | 2.4461 | 1112.2133 | 0 | 3.0988 | 1112.2133 | 1160.9975
DEER-SFAM-CZ08-V1-eSA-16-CH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-CH | 15.4161 | 2.6214 | 1350.9978 | 0 | 3.0988 | 1350.9978 | 1381.4767
DEER-SFAM-CZ08-V1-eSA-16-CL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-CL | 15.7532 | 2.5643 | 1282.402 | 0 | 3.0988 | 1282.402 | 1321.0797
DEER-SFAM-CZ08-V1-eSA-16-CM-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-CM | 15.4813 | 2.5915 | 1312.2149 | 0 | 3.0988 | 1312.2149 | 1353.0316
DEER-SFAM-CZ08-V1-eSA-16-LH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-LH | 15.3147 | 2.3074 | 1216.6568 | 0 | 3.0988 | 1216.6568 | 1269.1196
DEER-SFAM-CZ08-V1-eSA-16-LL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-LL | 14.7612 | 2.4839 | 1277.9319 | 0 | 3.0988 | 1277.9319 | 1312.4579
DEER-SFAM-CZ08-V1-eSA-16-LM-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-LM | 14.9444 | 2.4367 | 1268.0274 | 0 | 3.0988 | 1268.0274 | 1299.3206
DEER-SFAM-CZ08-V1-eSA-16-NM-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-NM | 16.333 | 2.3247 | 1189.6966 | 0 | 3.0988 | 1189.6966 | 1220.3848
DEER-SFAM-CZ08-V1-eSA-16-TH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-TH | 15.5667 | 2.6781 | 1384.0205 | 0 | 3.0988 | 1384.0205 | 1403.5192
DEER-SFAM-CZ08-V1-eSA-16-TL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSA-16 | CZ08-V1-eSA-16-TL | 15.94 | 2.5821 | 1333.672 | 0 | 3.0988 | 1333.672 | 1354.7808
DEER-SFAM-CZ08-V1-eSA-17-CH-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-CH | 16.4482 | 2.4718 | 1239.9151 | 0 | 3.0988 | 1239.9151 | 1278.5637
DEER-SFAM-CZ08-V1-eSA-17-CL-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-CL | 16.3779 | 2.5049 | 1243.9439 | 0 | 3.0988 | 1243.9439 | 1282.5847
DEER-SFAM-CZ08-V1-eSA-17-CM-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-CM | 16.4769 | 2.499 | 1263.6266 | 0 | 3.0988 | 1263.6266 | 1294.015
DEER-SFAM-CZ08-V1-eSA-17-LH-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-LH | 15.9182 | 2.2684 | 1165.2326 | 0 | 3.0988 | 1165.2326 | 1206.3705
DEER-SFAM-CZ08-V1-eSA-17-LL-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-LL | 15.6814 | 2.3933 | 1221.0773 | 0 | 3.0988 | 1221.0773 | 1243.5112
DEER-SFAM-CZ08-V1-eSA-17-LM-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-LM | 15.5509 | 2.3753 | 1219.9032 | 0 | 3.0988 | 1219.9032 | 1239.2798
DEER-SFAM-CZ08-V1-eSA-17-TH-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-TH | 17.8045 | 2.2967 | 1161.9276 | 0 | 3.0988 | 1161.9276 | 1193.1882
DEER-SFAM-CZ08-V1-eSA-17-TL-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-TL | 17.7986 | 2.3975 | 1125.0168 | 0 | 3.0988 | 1125.0168 | 1173.9848
DEER-SFAM-CZ08-V1-eSA-17-TM-s2 | 17 | CZ08 | V1 | CZ08-V1-eSA-17 | CZ08-V1-eSA-17-TM | 17.252 | 2.3902 | 1317.6626 | 0 | 3.0988 | 1317.6626 | 1333.9375
DEER-SFAM-CZ08-V1-eSA-18-LH-s2 | 18 | CZ08 | V1 | CZ08-V1-eSA-18 | CZ08-V1-eSA-18-LH | 16.6397 | 2.212 | 1144.2584 | 0 | 3.0988 | 1144.2584 | 1171.2446
DEER-SFAM-CZ08-V1-eSA-18-LL-s2 | 18 | CZ08 | V1 | CZ08-V1-eSA-18 | CZ08-V1-eSA-18-LL | 16.9042 | 2.2218 | 1113.2604 | 0 | 3.0988 | 1113.2604 | 1148.4796
DEER-SFAM-CZ08-V1-eSA-18-TH-s2 | 18 | CZ08 | V1 | CZ08-V1-eSA-18 | CZ08-V1-eSA-18-TH | 18.3542 | 2.1756 | 1131.2291 | 0 | 3.0988 | 1131.2291 | 1152.4981
DEER-SFAM-CZ08-V1-eSA-18-TL-s2 | 18 | CZ08 | V1 | CZ08-V1-eSA-18 | CZ08-V1-eSA-18-TL | 17.7232 | 2.3705 | 1196.9718 | 0 | 3.0988 | 1196.9718 | 1220.2723
DEER-SFAM-CZ08-V1-eSA-18-TM-s2 | 18 | CZ08 | V1 | CZ08-V1-eSA-18 | CZ08-V1-eSA-18-TM | 17.781 | 2.2653 | 1158.9333 | 0 | 3.0988 | 1158.9333 | 1180.6538
DEER-SFAM-CZ08-V1-eSH-10-HH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-HH | 10.5471 | 3.2854 | 1640.6575 | 1517.0043 | 3.0988 | 3157.6619 | 1800.4833
DEER-SFAM-CZ08-V1-eSH-10-HL-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-HL | 10.308 | 3.4556 | 1700.5494 | 1538.9878 | 3.0988 | 3239.5372 | 1859.9357
DEER-SFAM-CZ08-V1-eSH-10-HM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-HM | 10.5739 | 3.3509 | 1682.3207 | 1473.0399 | 3.0988 | 3155.3606 | 1834.3797
DEER-SFAM-CZ08-V1-eSH-10-LH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-LH | 10.692 | 3.1252 | 1632.1229 | 1609.9734 | 3.0988 | 3242.0963 | 1797.6056
DEER-SFAM-CZ08-V1-eSH-10-LL-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-LL | 10.5273 | 3.3406 | 1684.6892 | 1517.821 | 3.0988 | 3202.5102 | 1855.6931
DEER-SFAM-CZ08-V1-eSH-10-LM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-LM | 10.6033 | 3.1992 | 1664.1964 | 1500.8571 | 3.0988 | 3165.0535 | 1820.7702
DEER-SFAM-CZ08-V1-eSH-10-MH-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-MH | 10.7404 | 3.2283 | 1631.2341 | 1582.1977 | 3.0988 | 3213.4319 | 1807.0063
DEER-SFAM-CZ08-V1-eSH-10-ML-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-ML | 10.4758 | 3.4935 | 1689.2421 | 1415.5014 | 3.0988 | 3104.7435 | 1845.8374
DEER-SFAM-CZ08-V1-eSH-10-MM-s1 | 10 | CZ08 | V1 | CZ08-V1-eSH-10 | CZ08-V1-eSH-10-MM | 10.5155 | 3.1101 | 1702.2946 | 1527.7122 | 2.8241 | 3230.0068 | 1850.7234
DEER-SFAM-CZ08-V1-eSH-13-HH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-HH | 12.9923 | 2.7602 | 1323.439 | 1457.6896 | 3.0988 | 2781.1286 | 1469.1731
DEER-SFAM-CZ08-V1-eSH-13-HL-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-HL | 13.1047 | 2.7998 | 1285.8505 | 1261.3574 | 3.0988 | 2547.2078 | 1430.7163
DEER-SFAM-CZ08-V1-eSH-13-HM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-HM | 13.1121 | 2.7358 | 1318.1276 | 1296.7412 | 3.0988 | 2614.8689 | 1449.093
DEER-SFAM-CZ08-V1-eSH-13-LH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-LH | 13.657 | 2.5467 | 1254.4431 | 1533.0851 | 3.0988 | 2787.5283 | 1474.5585
DEER-SFAM-CZ08-V1-eSH-13-LL-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-LL | 14.0567 | 2.5718 | 1247.0208 | 1331.7837 | 3.0988 | 2578.8045 | 1379.7202
DEER-SFAM-CZ08-V1-eSH-13-LM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-LM | 13.2439 | 2.5209 | 1300.2476 | 1178.5182 | 2.8241 | 2478.7658 | 1452.6575
DEER-SFAM-CZ08-V1-eSH-13-MH-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-MH | 14.1178 | 2.556 | 1220.1714 | 1470.9188 | 3.0988 | 2691.0902 | 1367.607
DEER-SFAM-CZ08-V1-eSH-13-ML-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-ML | 13.1114 | 2.8311 | 1316.4449 | 1390.3223 | 3.0988 | 2706.7672 | 1467.6612
DEER-SFAM-CZ08-V1-eSH-13-MM-s1 | 13 | CZ08 | V1 | CZ08-V1-eSH-13 | CZ08-V1-eSH-13-MM | 13.7828 | 2.735 | 1274.3031 | 1367.4011 | 3.0988 | 2641.7042 | 1392.0451
DEER-SFAM-CZ08-V1-eSH-14-HH-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-HH | 13.7242 | 2.651 | 1252.0303 | 1328.6532 | 3.0988 | 2580.6835 | 1362.9353
DEER-SFAM-CZ08-V1-eSH-14-HL-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-HL | 13.7968 | 2.6468 | 1241.2622 | 1311.0894 | 3.0988 | 2552.3516 | 1375.03
DEER-SFAM-CZ08-V1-eSH-14-HM-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-HM | 13.7308 | 2.5632 | 1242.466 | 1292.1655 | 3.0988 | 2534.6315 | 1337.0472
DEER-SFAM-CZ08-V1-eSH-14-MH-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-MH | 14.6225 | 2.2313 | 1165.7523 | 1386.5504 | 2.8241 | 2552.3027 | 1309.9317
DEER-SFAM-CZ08-V1-eSH-14-ML-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-ML | 14.7325 | 2.5569 | 1162.2065 | 1461.0007 | 3.0988 | 2623.2072 | 1344.5158
DEER-SFAM-CZ08-V1-eSH-14-MM-s1 | 14 | CZ08 | V1 | CZ08-V1-eSH-14 | CZ08-V1-eSH-14-MM | 14.2666 | 2.5066 | 1186.8632 | 1277.7357 | 3.0988 | 2464.5989 | 1312.9966
DEER-SFAM-CZ08-V1-eSH-15-HH-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-HH | 14.7193 | 2.3569 | 1144.8767 | 1551.0086 | 3.0988 | 2695.8853 | 1248.3684
DEER-SFAM-CZ08-V1-eSH-15-HL-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-HL | 14.8781 | 2.439 | 1154.8734 | 1123.2897 | 3.0988 | 2278.1631 | 1257.203
DEER-SFAM-CZ08-V1-eSH-15-HM-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-HM | 15.7199 | 2.3863 | 1093.0196 | 1166.8369 | 3.0988 | 2259.8565 | 1195.6988
DEER-SFAM-CZ08-V1-eSH-15-MH-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-MH | 15.6951 | 2.467 | 1089.1032 | 1383.1975 | 3.0988 | 2472.3008 | 1188.7755
DEER-SFAM-CZ08-V1-eSH-15-ML-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-ML | 15.6747 | 2.415 | 1090.7802 | 1274.5466 | 3.0988 | 2365.3268 | 1193.5089
DEER-SFAM-CZ08-V1-eSH-15-MM-s1 | 15 | CZ08 | V1 | CZ08-V1-eSH-15 | CZ08-V1-eSH-15-MM | 15.9075 | 2.3814 | 1090.4122 | 1340.7488 | 3.0988 | 2431.161 | 1198.5647
DEER-SFAM-CZ08-V1-eSH-16-CH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-CH | 15.7607 | 2.5394 | 1314.8994 | 1371.1075 | 3.0988 | 2686.0069 | 1405.7287
DEER-SFAM-CZ08-V1-eSH-16-CL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-CL | 15.8408 | 2.6108 | 1318.1696 | 1277.1517 | 3.0988 | 2595.3212 | 1412.4756
DEER-SFAM-CZ08-V1-eSH-16-LH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-LH | 15.3345 | 2.2976 | 1204.4715 | 1498.0386 | 3.0988 | 2702.5101 | 1310.2618
DEER-SFAM-CZ08-V1-eSH-16-LL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-LL | 14.8826 | 2.4869 | 1268.7678 | 1367.0239 | 3.0988 | 2635.7917 | 1353.5075
DEER-SFAM-CZ08-V1-eSH-16-LM-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-LM | 14.8119 | 2.4052 | 1255.2533 | 1503.8262 | 3.0988 | 2759.0795 | 1373.6494
DEER-SFAM-CZ08-V1-eSH-16-TH-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-TH | 16.5087 | 2.4915 | 1245.1967 | 1708.6446 | 3.0988 | 2953.8413 | 1339.7555
DEER-SFAM-CZ08-V1-eSH-16-TL-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-TL | 15.5612 | 2.7222 | 1386.8101 | 1706.537 | 3.0988 | 3093.347 | 1472.9963
DEER-SFAM-CZ08-V1-eSH-16-TM-s2 | 16 | CZ08 | V1 | CZ08-V1-eSH-16 | CZ08-V1-eSH-16-TM | 15.7433 | 2.6666 | 1370.9123 | 1732.5468 | 3.0988 | 3103.4591 | 1459.3674
DEER-SFAM-CZ08-V1-eSH-17-CM-s2 | 17 | CZ08 | V1 | CZ08-V1-eSH-17 | CZ08-V1-eSH-17-CM | 16.7758 | 2.4744 | 1243.7408 | 1445.2249 | 3.0988 | 2688.9656 | 1353.632
DEER-SFAM-CZ08-V1-eSH-17-LM-s2 | 17 | CZ08 | V1 | CZ08-V1-eSH-17 | CZ08-V1-eSH-17-LM | 15.8479 | 2.3219 | 1211.0835 | 1325.8425 | 3.0988 | 2536.926 | 1258.7683
DEER-SFAM-CZ08-V1-eSH-17-TH-s2 | 17 | CZ08 | V1 | CZ08-V1-eSH-17 | CZ08-V1-eSH-17-TH | 17.5663 | 2.3471 | 1169.8684 | 1700.886 | 3.0988 | 2870.7545 | 1271.1687
DEER-SFAM-CZ08-V1-eSH-17-TL-s2 | 17 | CZ08 | V1 | CZ08-V1-eSH-17 | CZ08-V1-eSH-17-TL | 17.4078 | 2.3935 | 1181.0333 | 1688.2321 | 3.0988 | 2869.2654 | 1281.0965
DEER-SFAM-CZ08-V1-eSH-18-LH-s2 | 18 | CZ08 | V1 | CZ08-V1-eSH-18 | CZ08-V1-eSH-18-LH | 16.9248 | 2.2569 | 1121.5977 | 1520.1037 | 3.0988 | 2641.7014 | 1201.1942
DEER-SFAM-CZ08-V1-eSH-18-LL-s2 | 18 | CZ08 | V1 | CZ08-V1-eSH-18 | CZ08-V1-eSH-18-LL | 16.2147 | 2.345 | 1155.8282 | 1368.7106 | 3.0988 | 2524.5388 | 1229.3534
DEER-SFAM-CZ08-V1-eSH-18-LM-s2 | 18 | CZ08 | V1 | CZ08-V1-eSH-18 | CZ08-V1-eSH-18-LM | 16.777 | 2.2691 | 1137.8544 | 1602.8564 | 3.0988 | 2740.7108 | 1229.4409
DEER-SFAM-CZ08-V1-eSH-18-TM-s2 | 18 | CZ08 | V1 | CZ08-V1-eSH-18 | CZ08-V1-eSH-18-TM | 18.8026 | 2.1896 | 1089.6374 | 1675.7436 | 2.8241 | 2765.381 | 1240.8424
DEER-SFAM-CZ08-V2-eSA-10-HH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-HH | 10.2834 | 2.8776 | 1406.4554 | 0 | 2.6219 | 1406.4554 | 1452.4572
DEER-SFAM-CZ08-V2-eSA-10-HL-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-HL | 10.0105 | 3.1465 | 1421.6302 | 0 | 2.6219 | 1421.6302 | 1467.6884
DEER-SFAM-CZ08-V2-eSA-10-HM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-HM | 10.0062 | 3.0298 | 1401.8356 | 0 | 2.6219 | 1401.8356 | 1447.8844
DEER-SFAM-CZ08-V2-eSA-10-LH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-LH | 10.8973 | 2.8541 | 1308.2121 | 0 | 2.6219 | 1308.2121 | 1354.3245
DEER-SFAM-CZ08-V2-eSA-10-LL-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-LL | 10.0151 | 3.0575 | 1415.4055 | 0 | 2.6219 | 1415.4055 | 1461.477
DEER-SFAM-CZ08-V2-eSA-10-LM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-LM | 10.7274 | 2.8752 | 1331.6334 | 0 | 2.6219 | 1331.6334 | 1377.7485
DEER-SFAM-CZ08-V2-eSA-10-MH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-MH | 10.8156 | 2.7702 | 1319.9038 | 0 | 2.6219 | 1319.9038 | 1365.9982
DEER-SFAM-CZ08-V2-eSA-10-ML-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-ML | 10.0167 | 3.0821 | 1442.7922 | 0 | 2.6219 | 1442.7922 | 1488.8518
DEER-SFAM-CZ08-V2-eSA-10-MM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSA-10 | CZ08-V2-eSA-10-MM | 10.7451 | 2.8482 | 1304.4479 | 0 | 2.6219 | 1304.4479 | 1350.5136
DEER-SFAM-CZ08-V2-eSA-13-HH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-HH | 12.8327 | 2.3557 | 1067.9192 | 0 | 2.6219 | 1067.9192 | 1109.4389
DEER-SFAM-CZ08-V2-eSA-13-HL-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-HL | 13.3658 | 2.5356 | 1042.3912 | 0 | 2.6219 | 1042.3912 | 1078.7257
DEER-SFAM-CZ08-V2-eSA-13-HM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-HM | 13.1038 | 2.4612 | 1062.9292 | 0 | 2.6219 | 1062.9292 | 1104.4273
DEER-SFAM-CZ08-V2-eSA-13-LH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-LH | 13.8316 | 2.1988 | 1008.8223 | 0 | 2.6219 | 1008.8223 | 1054.8978
DEER-SFAM-CZ08-V2-eSA-13-LL-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-LL | 13.3555 | 2.3703 | 1068.6469 | 0 | 2.6219 | 1068.6469 | 1114.5903
DEER-SFAM-CZ08-V2-eSA-13-LM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-LM | 13.4289 | 2.2934 | 1052.3356 | 0 | 2.6219 | 1052.3356 | 1098.3542
DEER-SFAM-CZ08-V2-eSA-13-MH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-MH | 14.2931 | 2.3002 | 1013.5764 | 0 | 2.6219 | 1013.5764 | 1059.6254
DEER-SFAM-CZ08-V2-eSA-13-ML-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-ML | 13.1075 | 2.4481 | 1051.6415 | 0 | 2.6219 | 1051.6415 | 1097.5396
DEER-SFAM-CZ08-V2-eSA-13-MM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSA-13 | CZ08-V2-eSA-13-MM | 13.9669 | 2.333 | 1022.282 | 0 | 2.6219 | 1022.282 | 1068.321
DEER-SFAM-CZ08-V2-eSA-14-HH-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-HH | 13.5295 | 2.3284 | 1016.5527 | 0 | 2.6219 | 1016.5527 | 1055.1407
DEER-SFAM-CZ08-V2-eSA-14-HL-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-HL | 14.576 | 2.332 | 965.8857 | 0 | 2.6219 | 965.8857 | 994.2629
DEER-SFAM-CZ08-V2-eSA-14-HM-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-HM | 14.4733 | 2.3899 | 966.1137 | 0 | 2.6219 | 966.1137 | 1009.6629
DEER-SFAM-CZ08-V2-eSA-14-MH-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-MH | 14.3675 | 2.1226 | 1001.385 | 0 | 2.6219 | 1001.385 | 1031.6302
DEER-SFAM-CZ08-V2-eSA-14-ML-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-ML | 14.1929 | 2.3015 | 967.9997 | 0 | 2.6219 | 967.9997 | 1016.3225
DEER-SFAM-CZ08-V2-eSA-14-MM-s1 | 14 | CZ08 | V2 | CZ08-V2-eSA-14 | CZ08-V2-eSA-14-MM | 14.4067 | 2.1354 | 974.6287 | 0 | 2.6219 | 974.6287 | 1007.7966
DEER-SFAM-CZ08-V2-eSA-15-HH-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-HH | 15.1878 | 2.0962 | 909.4644 | 0 | 2.6219 | 909.4644 | 941.641
DEER-SFAM-CZ08-V2-eSA-15-HL-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-HL | 15.7864 | 2.1607 | 891.1863 | 0 | 2.6219 | 891.1863 | 931.2747
DEER-SFAM-CZ08-V2-eSA-15-HM-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-HM | 14.9377 | 2.1025 | 919.8762 | 0 | 2.6219 | 919.8762 | 952.1677
DEER-SFAM-CZ08-V2-eSA-15-MH-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-MH | 15.3313 | 2.1719 | 900.9385 | 0 | 2.6219 | 900.9385 | 924.9156
DEER-SFAM-CZ08-V2-eSA-15-ML-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-ML | 15.5155 | 2.1259 | 923.1479 | 0 | 2.6219 | 923.1479 | 955.3588
DEER-SFAM-CZ08-V2-eSA-15-MM-s1 | 15 | CZ08 | V2 | CZ08-V2-eSA-15 | CZ08-V2-eSA-15-MM | 15.455 | 2.1601 | 900.1776 | 0 | 2.6219 | 900.1776 | 929.576
DEER-SFAM-CZ08-V2-eSA-16-CH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-CH | 15.2574 | 2.2987 | 1075.4914 | 0 | 2.6219 | 1075.4914 | 1093.9914
DEER-SFAM-CZ08-V2-eSA-16-CL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-CL | 15.5815 | 2.2682 | 1026.3431 | 0 | 2.6219 | 1026.3431 | 1049.7701
DEER-SFAM-CZ08-V2-eSA-16-CM-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-CM | 15.3226 | 2.2897 | 1049.0692 | 0 | 2.6219 | 1049.0692 | 1073.7806
DEER-SFAM-CZ08-V2-eSA-16-LH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-LH | 15.2578 | 2.0489 | 976.6846 | 0 | 2.6219 | 976.6846 | 1008.445
DEER-SFAM-CZ08-V2-eSA-16-LL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-LL | 14.6882 | 2.2054 | 1024.5981 | 0 | 2.6219 | 1024.5981 | 1045.4873
DEER-SFAM-CZ08-V2-eSA-16-LM-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-LM | 14.875 | 2.1571 | 1016.9777 | 0 | 2.6219 | 1016.9777 | 1035.9163
DEER-SFAM-CZ08-V2-eSA-16-NM-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-NM | 16.2237 | 2.0902 | 949.5891 | 0 | 2.6219 | 949.5891 | 968.1554
DEER-SFAM-CZ08-V2-eSA-16-TH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-TH | 15.3611 | 2.3692 | 1091.0667 | 0 | 2.6219 | 1091.0667 | 1102.9502
DEER-SFAM-CZ08-V2-eSA-16-TL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSA-16 | CZ08-V2-eSA-16-TL | 15.706 | 2.3105 | 1051.5055 | 0 | 2.6219 | 1051.5055 | 1064.3607
DEER-SFAM-CZ08-V2-eSA-17-CH-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-CH | 16.2745 | 2.1766 | 992.7219 | 0 | 2.6219 | 992.7219 | 1016.1244
DEER-SFAM-CZ08-V2-eSA-17-CL-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-CL | 16.1843 | 2.2167 | 996.9452 | 0 | 2.6219 | 996.9452 | 1020.3438
DEER-SFAM-CZ08-V2-eSA-17-CM-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-CM | 16.2835 | 2.2095 | 1007.6178 | 0 | 2.6219 | 1007.6178 | 1026.064
DEER-SFAM-CZ08-V2-eSA-17-LH-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-LH | 15.8591 | 2.0049 | 937.3287 | 0 | 2.6219 | 937.3287 | 962.22
DEER-SFAM-CZ08-V2-eSA-17-LL-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-LL | 15.5865 | 2.1224 | 976.2987 | 0 | 2.6219 | 976.2987 | 989.8955
DEER-SFAM-CZ08-V2-eSA-17-LM-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-LM | 15.4811 | 2.1096 | 979.5437 | 0 | 2.6219 | 979.5437 | 991.2717
DEER-SFAM-CZ08-V2-eSA-17-TH-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-TH | 17.492 | 2.0285 | 925.1563 | 0 | 2.6219 | 925.1563 | 944.1647
DEER-SFAM-CZ08-V2-eSA-17-TL-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-TL | 17.406 | 2.1094 | 904.8979 | 0 | 2.6219 | 904.8979 | 934.5942
DEER-SFAM-CZ08-V2-eSA-17-TM-s2 | 17 | CZ08 | V2 | CZ08-V2-eSA-17 | CZ08-V2-eSA-17-TM | 17.0399 | 2.1132 | 1031.0077 | 0 | 2.6219 | 1031.0077 | 1040.9761
DEER-SFAM-CZ08-V2-eSA-18-LH-s2 | 18 | CZ08 | V2 | CZ08-V2-eSA-18 | CZ08-V2-eSA-18-LH | 16.5778 | 1.9651 | 917.1205 | 0 | 2.6219 | 917.1205 | 933.4523
DEER-SFAM-CZ08-V2-eSA-18-LL-s2 | 18 | CZ08 | V2 | CZ08-V2-eSA-18 | CZ08-V2-eSA-18-LL | 16.7542 | 1.9726 | 894.6536 | 0 | 2.6219 | 894.6536 | 915.9648
DEER-SFAM-CZ08-V2-eSA-18-TH-s2 | 18 | CZ08 | V2 | CZ08-V2-eSA-18 | CZ08-V2-eSA-18-TH | 18.1164 | 1.9298 | 897.718 | 0 | 2.6219 | 897.718 | 910.6484
DEER-SFAM-CZ08-V2-eSA-18-TL-s2 | 18 | CZ08 | V2 | CZ08-V2-eSA-18 | CZ08-V2-eSA-18-TL | 17.4802 | 2.0774 | 949.2838 | 0 | 2.6219 | 949.2838 | 963.4678
DEER-SFAM-CZ08-V2-eSA-18-TM-s2 | 18 | CZ08 | V2 | CZ08-V2-eSA-18 | CZ08-V2-eSA-18-TM | 17.5206 | 2.0017 | 919.8766 | 0 | 2.6219 | 919.8766 | 933.0796
DEER-SFAM-CZ08-V2-eSH-10-HH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-HH | 10.6286 | 2.9022 | 1330.4443 | 906.0807 | 2.6219 | 2236.525 | 1426.2094
DEER-SFAM-CZ08-V2-eSH-10-HL-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-HL | 10.3556 | 3.0444 | 1382.1703 | 919.28 | 2.6219 | 2301.4503 | 1477.2813
DEER-SFAM-CZ08-V2-eSH-10-HM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-HM | 10.6362 | 2.9373 | 1364.6932 | 889.3811 | 2.6219 | 2254.0744 | 1455.5821
DEER-SFAM-CZ08-V2-eSH-10-LH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-LH | 10.8315 | 2.7251 | 1316.5612 | 952.5862 | 2.6219 | 2269.1473 | 1415.4358
DEER-SFAM-CZ08-V2-eSH-10-LL-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-LL | 10.5847 | 2.938 | 1365.9206 | 912.0164 | 2.6219 | 2277.937 | 1468.4996
DEER-SFAM-CZ08-V2-eSH-10-LM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-LM | 10.6869 | 2.8172 | 1346.4571 | 903.2249 | 2.6219 | 2249.682 | 1440.5555
DEER-SFAM-CZ08-V2-eSH-10-MH-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-MH | 10.8554 | 2.8156 | 1319.0422 | 939.4627 | 2.6219 | 2258.5049 | 1424.0249
DEER-SFAM-CZ08-V2-eSH-10-ML-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-ML | 10.5231 | 3.0868 | 1372.2682 | 855.0652 | 2.6219 | 2227.3334 | 1466.6577
DEER-SFAM-CZ08-V2-eSH-10-MM-s1 | 10 | CZ08 | V2 | CZ08-V2-eSH-10 | CZ08-V2-eSH-10-MM | 10.484 | 2.8808 | 1390.1564 | 918.3703 | 2.6219 | 2308.5266 | 1479.3028
DEER-SFAM-CZ08-V2-eSH-13-HH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-HH | 13.0562 | 2.4374 | 1073.2484 | 867.8074 | 2.6219 | 1941.0558 | 1160.5267
DEER-SFAM-CZ08-V2-eSH-13-HL-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-HL | 13.0982 | 2.499 | 1046.5627 | 754.3224 | 2.6219 | 1800.8852 | 1133.4099
DEER-SFAM-CZ08-V2-eSH-13-HM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-HM | 13.1661 | 2.4219 | 1069.9189 | 776.3269 | 2.6219 | 1846.2458 | 1148.5512
DEER-SFAM-CZ08-V2-eSH-13-LH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-LH | 13.8075 | 2.2258 | 1014.3009 | 902.0099 | 2.6219 | 1916.3108 | 1145.3242
DEER-SFAM-CZ08-V2-eSH-13-LL-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-LL | 14.097 | 2.2803 | 1011.4399 | 791.9501 | 2.6219 | 1803.39 | 1091.0858
DEER-SFAM-CZ08-V2-eSH-13-LM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-LM | 13.2338 | 2.3484 | 1061.7881 | 702.5596 | 2.6219 | 1764.3478 | 1152.9755
DEER-SFAM-CZ08-V2-eSH-13-MH-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-MH | 14.1969 | 2.2554 | 986.9743 | 873.6103 | 2.6219 | 1860.5847 | 1074.9213
DEER-SFAM-CZ08-V2-eSH-13-ML-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-ML | 13.1679 | 2.4838 | 1069.604 | 817.0415 | 2.6219 | 1886.6455 | 1159.7865
DEER-SFAM-CZ08-V2-eSH-13-MM-s1 | 13 | CZ08 | V2 | CZ08-V2-eSH-13 | CZ08-V2-eSH-13-MM | 13.8377 | 2.4212 | 1032.8306 | 818.6774 | 2.6219 | 1851.508 | 1103.2529
DEER-SFAM-CZ08-V2-eSH-14-HH-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-HH | 13.769 | 2.3446 | 1017.3181 | 792.9299 | 2.6219 | 1810.248 | 1083.7793
DEER-SFAM-CZ08-V2-eSH-14-HL-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-HL | 13.8091 | 2.35 | 1011.368 | 780.2392 | 2.6219 | 1791.6072 | 1091.303
DEER-SFAM-CZ08-V2-eSH-14-HM-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-HM | 13.7883 | 2.2702 | 1008.5824 | 770.2746 | 2.6219 | 1778.857 | 1065.3089
DEER-SFAM-CZ08-V2-eSH-14-MH-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-MH | 14.6252 | 2.0798 | 952.6919 | 814.5797 | 2.6219 | 1767.2717 | 1039.0469
DEER-SFAM-CZ08-V2-eSH-14-ML-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-ML | 14.8733 | 2.2594 | 939.4111 | 851.4009 | 2.6219 | 1790.812 | 1047.8433
DEER-SFAM-CZ08-V2-eSH-14-MM-s1 | 14 | CZ08 | V2 | CZ08-V2-eSH-14 | CZ08-V2-eSH-14-MM | 14.371 | 2.2147 | 960.3078 | 756.1535 | 2.6219 | 1716.4613 | 1035.5531
DEER-SFAM-CZ08-V2-eSH-15-HH-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-HH | 14.7641 | 2.0903 | 930.3898 | 914.293 | 2.6219 | 1844.6829 | 992.1849
DEER-SFAM-CZ08-V2-eSH-15-HL-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-HL | 14.9127 | 2.1704 | 940.1005 | 673.689 | 2.6219 | 1613.7895 | 1001.3747
DEER-SFAM-CZ08-V2-eSH-15-HM-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-HM | 15.7305 | 2.1193 | 888.2348 | 699.0182 | 2.6219 | 1587.253 | 949.4422
DEER-SFAM-CZ08-V2-eSH-15-MH-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-MH | 15.8019 | 2.1764 | 882.4881 | 801.9068 | 2.6219 | 1684.3949 | 941.6701
DEER-SFAM-CZ08-V2-eSH-15-ML-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-ML | 15.8072 | 2.144 | 882.6482 | 746.172 | 2.6219 | 1628.8202 | 943.8449
DEER-SFAM-CZ08-V2-eSH-15-MM-s1 | 15 | CZ08 | V2 | CZ08-V2-eSH-15 | CZ08-V2-eSH-15-MM | 15.905 | 2.1172 | 887.5734 | 794.8084 | 2.6219 | 1682.3818 | 952.3583
DEER-SFAM-CZ08-V2-eSH-16-CH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-CH | 15.5809 | 2.249 | 1047.9873 | 797.5919 | 2.6219 | 1845.5792 | 1103.6587
DEER-SFAM-CZ08-V2-eSH-16-CL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-CL | 15.6642 | 2.2916 | 1050.4795 | 743.8872 | 2.6219 | 1794.3667 | 1108.208
DEER-SFAM-CZ08-V2-eSH-16-LH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-LH | 15.2995 | 2.0391 | 966.7732 | 867.3398 | 2.6219 | 1834.113 | 1029.7663
DEER-SFAM-CZ08-V2-eSH-16-LL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-LL | 14.7995 | 2.1982 | 1019.9706 | 790.8029 | 2.6219 | 1810.7734 | 1070.3104
DEER-SFAM-CZ08-V2-eSH-16-LM-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-LM | 14.7893 | 2.1231 | 1007.6014 | 870.0037 | 2.6219 | 1877.6051 | 1078.0023
DEER-SFAM-CZ08-V2-eSH-16-TH-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-TH | 16.2915 | 2.2202 | 989.7361 | 990.7742 | 2.6219 | 1980.5103 | 1048.4386
DEER-SFAM-CZ08-V2-eSH-16-TL-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-TL | 15.3165 | 2.3949 | 1096.3367 | 981.8557 | 2.6219 | 2078.1924 | 1150.0536
DEER-SFAM-CZ08-V2-eSH-16-TM-s2 | 16 | CZ08 | V2 | CZ08-V2-eSH-16 | CZ08-V2-eSH-16-TM | 15.4942 | 2.3471 | 1083.8405 | 997.8691 | 2.6219 | 2081.7096 | 1138.9612
DEER-SFAM-CZ08-V2-eSH-17-CM-s2 | 17 | CZ08 | V2 | CZ08-V2-eSH-17 | CZ08-V2-eSH-17-CM | 16.5775 | 2.172 | 991.9475 | 820.107 | 2.6219 | 1812.0545 | 1057.2437
DEER-SFAM-CZ08-V2-eSH-17-LM-s2 | 17 | CZ08 | V2 | CZ08-V2-eSH-17 | CZ08-V2-eSH-17-LM | 15.7665 | 2.0614 | 970.1671 | 766.2825 | 2.6219 | 1736.4496 | 998.4866
DEER-SFAM-CZ08-V2-eSH-17-TH-s2 | 17 | CZ08 | V2 | CZ08-V2-eSH-17 | CZ08-V2-eSH-17-TH | 17.2866 | 2.0804 | 931.1541 | 988.0887 | 2.6219 | 1919.2428 | 994.037
DEER-SFAM-CZ08-V2-eSH-17-TL-s2 | 17 | CZ08 | V2 | CZ08-V2-eSH-17 | CZ08-V2-eSH-17-TL | 17.1322 | 2.1264 | 940.7004 | 978.3106 | 2.6219 | 1919.011 | 1002.7928
DEER-SFAM-CZ08-V2-eSH-18-LH-s2 | 18 | CZ08 | V2 | CZ08-V2-eSH-18 | CZ08-V2-eSH-18-LH | 16.7952 | 1.99 | 900.9487 | 875.517 | 2.6219 | 1776.4657 | 948.8752
DEER-SFAM-CZ08-V2-eSH-18-LL-s2 | 18 | CZ08 | V2 | CZ08-V2-eSH-18 | CZ08-V2-eSH-18-LL | 16.1033 | 2.0682 | 930.3035 | 791.2994 | 2.6219 | 1721.603 | 974.018
DEER-SFAM-CZ08-V2-eSH-18-LM-s2 | 18 | CZ08 | V2 | CZ08-V2-eSH-18 | CZ08-V2-eSH-18-LM | 16.6574 | 2.0073 | 910.1819 | 922.5395 | 2.6219 | 1832.7213 | 965.4786
DEER-SFAM-CZ08-V2-eSH-18-TM-s2 | 18 | CZ08 | V2 | CZ08-V2-eSH-18 | CZ08-V2-eSH-18-TM | 18.458 | 2.0303 | 882.7341 | 970.8061 | 2.6219 | 1853.5402 | 973.7605
DEER-SFAM-CZ08-V3-eSA-10-HH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-HH | 10.4696 | 3.1335 | 2101.6797 | 0 | 2.8 | 2101.6797 | 2126.8138
DEER-SFAM-CZ08-V3-eSA-10-HL-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-HL | 10.1904 | 3.4263 | 2151.4819 | 0 | 2.8 | 2151.4819 | 2176.6492
DEER-SFAM-CZ08-V3-eSA-10-HM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-HM | 10.1828 | 3.3012 | 2127.6874 | 0 | 2.8 | 2127.6874 | 2152.8489
DEER-SFAM-CZ08-V3-eSA-10-LH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-LH | 10.8349 | 3.1089 | 2008.87 | 0 | 2.8 | 2008.87 | 2034.0711
DEER-SFAM-CZ08-V3-eSA-10-LL-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-LL | 10.1305 | 3.3303 | 2160.3134 | 0 | 2.8 | 2160.3134 | 2185.4888
DEER-SFAM-CZ08-V3-eSA-10-LM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-LM | 10.6978 | 3.1269 | 2037.5196 | 0 | 2.8 | 2037.5196 | 2062.7218
DEER-SFAM-CZ08-V3-eSA-10-MH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-MH | 10.8595 | 3.0124 | 2006.0957 | 0 | 2.8 | 2006.0957 | 2031.2849
DEER-SFAM-CZ08-V3-eSA-10-ML-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-ML | 10.1422 | 3.3559 | 2188.3538 | 0 | 2.8 | 2188.3538 | 2213.5221
DEER-SFAM-CZ08-V3-eSA-10-MM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSA-10 | CZ08-V3-eSA-10-MM | 10.8028 | 3.0688 | 1994.3847 | 0 | 2.8 | 1994.3847 | 2019.5563
DEER-SFAM-CZ08-V3-eSA-13-HH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-HH | 13.0346 | 2.5545 | 1631.5658 | 0 | 2.8 | 1631.5658 | 1654.2534
DEER-SFAM-CZ08-V3-eSA-13-HL-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-HL | 13.404 | 2.7826 | 1600.9513 | 0 | 2.8 | 1600.9513 | 1620.8055
DEER-SFAM-CZ08-V3-eSA-13-HM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-HM | 13.2211 | 2.6924 | 1628.6977 | 0 | 2.8 | 1628.6977 | 1651.3728
DEER-SFAM-CZ08-V3-eSA-13-LH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-LH | 13.8454 | 2.3989 | 1543.4188 | 0 | 2.8 | 1543.4188 | 1568.5962
DEER-SFAM-CZ08-V3-eSA-13-LL-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-LL | 13.3617 | 2.5872 | 1629.7875 | 0 | 2.8 | 1629.7875 | 1654.8853
DEER-SFAM-CZ08-V3-eSA-13-LM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-LM | 13.44 | 2.4972 | 1608.5685 | 0 | 2.8 | 1608.5685 | 1633.7127
DEER-SFAM-CZ08-V3-eSA-13-MH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-MH | 14.3976 | 2.5115 | 1534.238 | 0 | 2.8 | 1534.238 | 1559.3995
DEER-SFAM-CZ08-V3-eSA-13-ML-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-ML | 13.15 | 2.6781 | 1610.0478 | 0 | 2.8 | 1610.0478 | 1635.1265
DEER-SFAM-CZ08-V3-eSA-13-MM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSA-13 | CZ08-V3-eSA-13-MM | 14.1514 | 2.5594 | 1545.4048 | 0 | 2.8 | 1545.4048 | 1570.5609
DEER-SFAM-CZ08-V3-eSA-14-HH-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-HH | 13.6181 | 2.5433 | 1552.6762 | 0 | 2.8 | 1552.6762 | 1573.7609
DEER-SFAM-CZ08-V3-eSA-14-HL-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-HL | 14.5596 | 2.565 | 1494.2149 | 0 | 2.8 | 1494.2149 | 1509.7213
DEER-SFAM-CZ08-V3-eSA-14-HM-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-HM | 14.3693 | 2.6198 | 1499.4293 | 0 | 2.8 | 1499.4293 | 1523.2265
DEER-SFAM-CZ08-V3-eSA-14-MH-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-MH | 14.3776 | 2.3097 | 1523.3868 | 0 | 2.8 | 1523.3868 | 1539.9125
DEER-SFAM-CZ08-V3-eSA-14-ML-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-ML | 14.1305 | 2.5172 | 1498.5693 | 0 | 2.8 | 1498.5693 | 1524.9737
DEER-SFAM-CZ08-V3-eSA-14-MM-s1 | 14 | CZ08 | V3 | CZ08-V3-eSA-14 | CZ08-V3-eSA-14-MM | 14.4343 | 2.3249 | 1488.4474 | 0 | 2.8 | 1488.4474 | 1506.5712
DEER-SFAM-CZ08-V3-eSA-15-HH-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-HH | 15.474 | 2.2884 | 1384.4301 | 0 | 2.8 | 1384.4301 | 1402.013
DEER-SFAM-CZ08-V3-eSA-15-HL-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-HL | 15.819 | 2.3627 | 1368.4726 | 0 | 2.8 | 1368.4726 | 1390.3768
DEER-SFAM-CZ08-V3-eSA-15-HM-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-HM | 15.1943 | 2.3017 | 1403.6334 | 0 | 2.8 | 1403.6334 | 1421.2784
DEER-SFAM-CZ08-V3-eSA-15-MH-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-MH | 15.4148 | 2.3748 | 1380.6897 | 0 | 2.8 | 1380.6897 | 1393.7924
DEER-SFAM-CZ08-V3-eSA-15-ML-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-ML | 15.5541 | 2.3263 | 1405.9498 | 0 | 2.8 | 1405.9498 | 1423.5459
DEER-SFAM-CZ08-V3-eSA-15-MM-s1 | 15 | CZ08 | V3 | CZ08-V3-eSA-15 | CZ08-V3-eSA-15-MM | 15.4053 | 2.3656 | 1389.2158 | 0 | 2.8 | 1389.2158 | 1405.2808
DEER-SFAM-CZ08-V3-eSA-16-CH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-CH | 15.127 | 2.4898 | 1574.8975 | 0 | 2.8 | 1574.8975 | 1584.9989
DEER-SFAM-CZ08-V3-eSA-16-CL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-CL | 15.499 | 2.4739 | 1509.0763 | 0 | 2.8 | 1509.0763 | 1521.8562
DEER-SFAM-CZ08-V3-eSA-16-CM-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-CM | 15.2672 | 2.4738 | 1537.4738 | 0 | 2.8 | 1537.4738 | 1550.9434
DEER-SFAM-CZ08-V3-eSA-16-LH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-LH | 15.7017 | 2.25 | 1418.1747 | 0 | 2.8 | 1418.1747 | 1435.5588
DEER-SFAM-CZ08-V3-eSA-16-LL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-LL | 15.0644 | 2.4172 | 1490.6945 | 0 | 2.8 | 1490.6945 | 1502.1101
DEER-SFAM-CZ08-V3-eSA-16-LM-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-LM | 15.1027 | 2.3621 | 1485.4498 | 0 | 2.8 | 1485.4498 | 1495.7983
DEER-SFAM-CZ08-V3-eSA-16-NM-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-NM | 16.1341 | 2.3016 | 1420.564 | 0 | 2.8 | 1420.564 | 1430.7111
DEER-SFAM-CZ08-V3-eSA-16-TH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-TH | 15.6801 | 2.5882 | 1530.3042 | 0 | 2.8 | 1530.3042 | 1536.807
DEER-SFAM-CZ08-V3-eSA-16-TL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSA-16 | CZ08-V3-eSA-16-TL | 15.9861 | 2.5354 | 1487.0342 | 0 | 2.8 | 1487.0342 | 1494.0629
DEER-SFAM-CZ08-V3-eSA-17-CH-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-CH | 16.1434 | 2.3673 | 1462.3427 | 0 | 2.8 | 1462.3427 | 1475.1084
DEER-SFAM-CZ08-V3-eSA-17-CL-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-CL | 16.0265 | 2.4183 | 1471.2059 | 0 | 2.8 | 1471.2059 | 1483.9696
DEER-SFAM-CZ08-V3-eSA-17-CM-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-CM | 16.1371 | 2.4058 | 1477.2451 | 0 | 2.8 | 1477.2451 | 1487.3177
DEER-SFAM-CZ08-V3-eSA-17-LH-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-LH | 16.2453 | 2.1958 | 1367.0831 | 0 | 2.8 | 1367.0831 | 1380.7063
DEER-SFAM-CZ08-V3-eSA-17-LL-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-LL | 15.9285 | 2.3231 | 1419.7095 | 0 | 2.8 | 1419.7095 | 1427.1406
DEER-SFAM-CZ08-V3-eSA-17-LM-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-LM | 15.7741 | 2.3131 | 1428.113 | 0 | 2.8 | 1428.113 | 1434.5208
DEER-SFAM-CZ08-V3-eSA-17-TH-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-TH | 17.9155 | 2.2124 | 1312.1548 | 0 | 2.8 | 1312.1548 | 1322.5539
DEER-SFAM-CZ08-V3-eSA-17-TL-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-TL | 17.5557 | 2.3243 | 1308.3821 | 0 | 2.8 | 1308.3821 | 1324.58
DEER-SFAM-CZ08-V3-eSA-17-TM-s2 | 17 | CZ08 | V3 | CZ08-V3-eSA-17 | CZ08-V3-eSA-17-TM | 17.4649 | 2.2867 | 1428.8256 | 0 | 2.8 | 1428.8256 | 1434.2828
DEER-SFAM-CZ08-V3-eSA-18-LH-s2 | 18 | CZ08 | V3 | CZ08-V3-eSA-18 | CZ08-V3-eSA-18-LH | 16.9615 | 2.1553 | 1328.0584 | 0 | 2.8 | 1328.0584 | 1336.9822
DEER-SFAM-CZ08-V3-eSA-18-LL-s2 | 18 | CZ08 | V3 | CZ08-V3-eSA-18 | CZ08-V3-eSA-18-LL | 16.999 | 2.1641 | 1311.0344 | 0 | 2.8 | 1311.0344 | 1322.6817
DEER-SFAM-CZ08-V3-eSA-18-TH-s2 | 18 | CZ08 | V3 | CZ08-V3-eSA-18 | CZ08-V3-eSA-18-TH | 18.6881 | 2.1088 | 1263.4445 | 0 | 2.8 | 1263.4445 | 1270.512
DEER-SFAM-CZ08-V3-eSA-18-TL-s2 | 18 | CZ08 | V3 | CZ08-V3-eSA-18 | CZ08-V3-eSA-18-TL | 17.8821 | 2.2474 | 1335.8669 | 0 | 2.8 | 1335.8669 | 1343.6235
DEER-SFAM-CZ08-V3-eSA-18-TM-s2 | 18 | CZ08 | V3 | CZ08-V3-eSA-18 | CZ08-V3-eSA-18-TM | 17.8831 | 2.1832 | 1308.3937 | 0 | 2.8 | 1308.3937 | 1315.6138
DEER-SFAM-CZ08-V3-eSH-10-HH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-HH | 10.6657 | 3.1605 | 2027.8241 | 497.8747 | 2.8 | 2525.6988 | 2079.8988
DEER-SFAM-CZ08-V3-eSH-10-HL-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-HL | 10.3419 | 3.3167 | 2109.1538 | 502.9108 | 2.8 | 2612.0646 | 2160.6646
DEER-SFAM-CZ08-V3-eSH-10-HM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-HM | 10.7743 | 3.203 | 2057.9307 | 493.7921 | 2.8 | 2551.7228 | 2107.2228
DEER-SFAM-CZ08-V3-eSH-10-LH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-LH | 10.9262 | 2.9645 | 1993.4521 | 521.5358 | 2.8 | 2514.9879 | 2047.0879
DEER-SFAM-CZ08-V3-eSH-10-LL-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-LL | 10.5949 | 3.2058 | 2083.8354 | 502.7196 | 2.8 | 2586.555 | 2139.655
DEER-SFAM-CZ08-V3-eSH-10-LM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-LM | 10.8023 | 3.0744 | 2038.4253 | 500.2285 | 2.8 | 2538.6538 | 2089.7538
DEER-SFAM-CZ08-V3-eSH-10-MH-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-MH | 10.9038 | 3.064 | 2003.8856 | 513.7034 | 2.8 | 2517.589 | 2060.789
DEER-SFAM-CZ08-V3-eSH-10-ML-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-ML | 10.527 | 3.3745 | 2098.7796 | 472.7346 | 2.8 | 2571.5142 | 2150.4142
DEER-SFAM-CZ08-V3-eSH-10-MM-s1 | 10 | CZ08 | V3 | CZ08-V3-eSH-10 | CZ08-V3-eSH-10-MM | 10.6477 | 3.1157 | 2083.0088 | 504.455 | 2.8 | 2587.4638 | 2131.5638
DEER-SFAM-CZ08-V3-eSH-13-HH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-HH | 13.2883 | 2.656 | 1626.9862 | 477.6534 | 2.8 | 2104.6396 | 1674.4396
DEER-SFAM-CZ08-V3-eSH-13-HL-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-HL | 13.1897 | 2.7348 | 1619.5017 | 414.3578 | 2.8 | 2033.8595 | 1666.7595
DEER-SFAM-CZ08-V3-eSH-13-HM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-HM | 13.3861 | 2.6434 | 1621.062 | 428.778 | 2.8 | 2049.84 | 1663.94
DEER-SFAM-CZ08-V3-eSH-13-LH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-LH | 13.8134 | 2.4249 | 1551.6445 | 482.5107 | 2.8 | 2034.1552 | 1622.2552
DEER-SFAM-CZ08-V3-eSH-13-LL-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-LL | 14.3251 | 2.4958 | 1533.374 | 433.3837 | 2.8 | 1966.7577 | 1576.7577
DEER-SFAM-CZ08-V3-eSH-13-LM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-LM | 13.2208 | 2.5573 | 1629.2337 | 382.5883 | 2.8 | 2011.822 | 1678.722
DEER-SFAM-CZ08-V3-eSH-13-MH-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-MH | 14.4305 | 2.4372 | 1501.1894 | 479.7973 | 2.8 | 1980.9867 | 1548.7867
DEER-SFAM-CZ08-V3-eSH-13-ML-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-ML | 13.1863 | 2.7115 | 1638.3402 | 441.2231 | 2.8 | 2079.5633 | 1687.1633
DEER-SFAM-CZ08-V3-eSH-13-MM-s1 | 13 | CZ08 | V3 | CZ08-V3-eSH-13 | CZ08-V3-eSH-13-MM | 13.9403 | 2.6512 | 1573.7362 | 450.1669 | 2.8 | 2023.9031 | 1612.0031
DEER-SFAM-CZ08-V3-eSH-14-HH-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-HH | 13.9839 | 2.5566 | 1545.7052 | 436.6635 | 2.8 | 1982.3687 | 1581.8687
DEER-SFAM-CZ08-V3-eSH-14-HL-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-HL | 13.9388 | 2.567 | 1547.669 | 426.9514 | 2.8 | 1974.6204 | 1591.0204
DEER-SFAM-CZ08-V3-eSH-14-HM-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-HM | 13.9705 | 2.4765 | 1538.0144 | 423.7947 | 2.8 | 1961.8091 | 1568.9091
DEER-SFAM-CZ08-V3-eSH-14-MH-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-MH | 14.6335 | 2.2659 | 1458.1807 | 440.1251 | 2.8 | 1898.3058 | 1505.0058
DEER-SFAM-CZ08-V3-eSH-14-ML-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-ML | 14.6972 | 2.4719 | 1459.9924 | 452.4654 | 2.8 | 1912.4578 | 1518.3578
DEER-SFAM-CZ08-V3-eSH-14-MM-s1 | 14 | CZ08 | V3 | CZ08-V3-eSH-14 | CZ08-V3-eSH-14-MM | 14.2641 | 2.4224 | 1486.8712 | 411.9383 | 2.8 | 1898.8095 | 1527.6095
DEER-SFAM-CZ08-V3-eSH-15-HH-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-HH | 15.0755 | 2.2802 | 1412.7098 | 481.9946 | 2.8 | 1894.7044 | 1446.1044
DEER-SFAM-CZ08-V3-eSH-15-HL-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-HL | 15.0621 | 2.3753 | 1436.7997 | 371.6225 | 2.8 | 1808.4222 | 1470.1222
DEER-SFAM-CZ08-V3-eSH-15-HM-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-HM | 15.7744 | 2.2969 | 1369.4033 | 387.3089 | 2.8 | 1756.7122 | 1402.5122
DEER-SFAM-CZ08-V3-eSH-15-MH-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-MH | 15.7936 | 2.3858 | 1358.919 | 427.4434 | 2.8 | 1786.3624 | 1390.7624
DEER-SFAM-CZ08-V3-eSH-15-ML-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-ML | 15.6428 | 2.3513 | 1371.0311 | 402.0387 | 2.8 | 1773.0698 | 1404.0698
DEER-SFAM-CZ08-V3-eSH-15-MM-s1 | 15 | CZ08 | V3 | CZ08-V3-eSH-15 | CZ08-V3-eSH-15-MM | 16.0222 | 2.3013 | 1360.841 | 432.2103 | 2.8 | 1793.0513 | 1396.0513
DEER-SFAM-CZ08-V3-eSH-16-CH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-CH | 15.516 | 2.4541 | 1528.4032 | 414.4055 | 2.8 | 1942.8087 | 1557.4087
DEER-SFAM-CZ08-V3-eSH-16-CL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-CL | 15.5574 | 2.4798 | 1535.4089 | 388.6125 | 2.8 | 1924.0214 | 1565.6214
DEER-SFAM-CZ08-V3-eSH-16-LH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-LH | 15.8437 | 2.2365 | 1396.1523 | 451.3441 | 2.8 | 1847.4964 | 1429.2964
DEER-SFAM-CZ08-V3-eSH-16-LL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-LL | 15.017 | 2.406 | 1492.8265 | 410.6396 | 2.8 | 1903.4661 | 1519.4661
DEER-SFAM-CZ08-V3-eSH-16-LM-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-LM | 15.2228 | 2.321 | 1466.2587 | 449.9158 | 2.8 | 1916.1745 | 1503.2745
DEER-SFAM-CZ08-V3-eSH-16-TH-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-TH | 16.7846 | 2.4334 | 1396.9655 | 506.6981 | 2.8 | 1903.6636 | 1426.0636
DEER-SFAM-CZ08-V3-eSH-16-TL-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-TL | 15.4204 | 2.6139 | 1556.637 | 497.6356 | 2.8 | 2054.2726 | 1583.2726
DEER-SFAM-CZ08-V3-eSH-16-TM-s2 | 16 | CZ08 | V3 | CZ08-V3-eSH-16 | CZ08-V3-eSH-16-TM | 15.6255 | 2.5611 | 1536.8369 | 506.2765 | 2.8 | 2043.1134 | 1564.2134
DEER-SFAM-CZ08-V3-eSH-17-CM-s2 | 17 | CZ08 | V3 | CZ08-V3-eSH-17 | CZ08-V3-eSH-17-CM | 16.4578 | 2.3485 | 1449.3216 | 415.538 | 2.8 | 1864.8596 | 1482.3596
DEER-SFAM-CZ08-V3-eSH-17-LM-s2 | 17 | CZ08 | V3 | CZ08-V3-eSH-17 | CZ08-V3-eSH-17-LM | 16.194 | 2.2537 | 1405.0895 | 399.3903 | 2.8 | 1804.4798 | 1420.0798
DEER-SFAM-CZ08-V3-eSH-17-TH-s2 | 17 | CZ08 | V3 | CZ08-V3-eSH-17 | CZ08-V3-eSH-17-TH | 17.6746 | 2.2755 | 1323.9624 | 504.9441 | 2.8 | 1828.9065 | 1355.4065
DEER-SFAM-CZ08-V3-eSH-17-TL-s2 | 17 | CZ08 | V3 | CZ08-V3-eSH-17 | CZ08-V3-eSH-17-TL | 17.4996 | 2.3258 | 1338.6254 | 498.3384 | 2.8 | 1836.9638 | 1369.5638
DEER-SFAM-CZ08-V3-eSH-18-LH-s2 | 18 | CZ08 | V3 | CZ08-V3-eSH-18 | CZ08-V3-eSH-18-LH | 17.0846 | 2.1742 | 1309.453 | 443.7511 | 2.8 | 1753.2041 | 1333.6041
DEER-SFAM-CZ08-V3-eSH-18-LL-s2 | 18 | CZ08 | V3 | CZ08-V3-eSH-18 | CZ08-V3-eSH-18-LL | 16.3156 | 2.2595 | 1365.1042 | 407.5091 | 2.8 | 1772.6133 | 1388.0133
DEER-SFAM-CZ08-V3-eSH-18-LM-s2 | 18 | CZ08 | V3 | CZ08-V3-eSH-18 | CZ08-V3-eSH-18-LM | 17.0273 | 2.1953 | 1323.8308 | 464.8186 | 2.8 | 1788.6494 | 1351.4494
DEER-SFAM-CZ08-V3-eSH-18-TM-s2 | 18 | CZ08 | V3 | CZ08-V3-eSH-18 | CZ08-V3-eSH-18-TM | 18.7504 | 2.1566 | 1257.5821 | 491.0516 | 2.8 | 1748.6337 | 1303.7337
DEER-SFAM-CZ08-V4-eSA-10-HH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-HH | 10.4645 | 3.1312 | 2041.6091 | 0 | 2.8 | 2041.6091 | 2060.1172
DEER-SFAM-CZ08-V4-eSA-10-HL-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-HL | 10.1997 | 3.424 | 2087.2182 | 0 | 2.8 | 2087.2182 | 2105.7517
DEER-SFAM-CZ08-V4-eSA-10-HM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-HM | 10.1951 | 3.296 | 2062.6827 | 0 | 2.8 | 2062.6827 | 2081.2118
DEER-SFAM-CZ08-V4-eSA-10-LH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-LH | 10.8296 | 3.1076 | 1945.2416 | 0 | 2.8 | 1945.2416 | 1963.8006
DEER-SFAM-CZ08-V4-eSA-10-LL-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-LL | 10.1365 | 3.3288 | 2092.1434 | 0 | 2.8 | 2092.1434 | 2110.6829
DEER-SFAM-CZ08-V4-eSA-10-LM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-LM | 10.6927 | 3.1262 | 1973.4998 | 0 | 2.8 | 1973.4998 | 1992.0598
DEER-SFAM-CZ08-V4-eSA-10-MH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-MH | 10.8459 | 3.0114 | 1944.5746 | 0 | 2.8 | 1944.5746 | 1963.1247
DEER-SFAM-CZ08-V4-eSA-10-ML-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-ML | 10.1587 | 3.3534 | 2122.0498 | 0 | 2.8 | 2122.0498 | 2140.5839
DEER-SFAM-CZ08-V4-eSA-10-MM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSA-10 | CZ08-V4-eSA-10-MM | 10.7976 | 3.0661 | 1931.3377 | 0 | 2.8 | 1931.3377 | 1949.8743
DEER-SFAM-CZ08-V4-eSA-13-HH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-HH | 12.8468 | 2.8832 | 1606.3874 | 0 | 3.2 | 1606.3874 | 1623.1197
DEER-SFAM-CZ08-V4-eSA-13-HL-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-HL | 13.4105 | 2.7813 | 1550.3589 | 0 | 2.8 | 1550.3589 | 1564.9797
DEER-SFAM-CZ08-V4-eSA-13-HM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-HM | 13.0983 | 3.0012 | 1594.6486 | 0 | 3.2 | 1594.6486 | 1611.3723
DEER-SFAM-CZ08-V4-eSA-13-LH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-LH | 13.8317 | 2.3975 | 1497.6453 | 0 | 2.8 | 1497.6453 | 1516.1867
DEER-SFAM-CZ08-V4-eSA-13-LL-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-LL | 13.3726 | 2.5857 | 1579.1804 | 0 | 2.8 | 1579.1804 | 1597.6611
DEER-SFAM-CZ08-V4-eSA-13-LM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-LM | 13.4369 | 2.4964 | 1559.4425 | 0 | 2.8 | 1559.4425 | 1577.9584
DEER-SFAM-CZ08-V4-eSA-13-MH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-MH | 14.4058 | 2.5104 | 1486.9525 | 0 | 2.8 | 1486.9525 | 1505.4816
DEER-SFAM-CZ08-V4-eSA-13-ML-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-ML | 13.1614 | 2.6778 | 1558.7578 | 0 | 2.8 | 1558.7578 | 1577.2251
DEER-SFAM-CZ08-V4-eSA-13-MM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSA-13 | CZ08-V4-eSA-13-MM | 14.0032 | 2.8526 | 1516.1602 | 0 | 3.2 | 1516.1602 | 1534.7137
DEER-SFAM-CZ08-V4-eSA-14-HH-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-HH | 13.6234 | 2.5426 | 1503.7339 | 0 | 2.8 | 1503.7339 | 1519.2607
DEER-SFAM-CZ08-V4-eSA-14-HL-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-HL | 14.5737 | 2.5644 | 1444.0821 | 0 | 2.8 | 1444.0821 | 1455.501
DEER-SFAM-CZ08-V4-eSA-14-HM-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-HM | 14.4005 | 2.6181 | 1449.9841 | 0 | 2.8 | 1449.9841 | 1467.5085
DEER-SFAM-CZ08-V4-eSA-14-MH-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-MH | 14.3768 | 2.3089 | 1477.791 | 0 | 2.8 | 1477.791 | 1489.9605
DEER-SFAM-CZ08-V4-eSA-14-ML-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-ML | 14.1429 | 2.5156 | 1450.7932 | 0 | 2.8 | 1450.7932 | 1470.2371
DEER-SFAM-CZ08-V4-eSA-14-MM-s1 | 14 | CZ08 | V4 | CZ08-V4-eSA-14 | CZ08-V4-eSA-14-MM | 14.4326 | 2.324 | 1443.7734 | 0 | 2.8 | 1443.7734 | 1457.1196
DEER-SFAM-CZ08-V4-eSA-15-HH-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-HH | 15.2284 | 2.5514 | 1362.1312 | 0 | 3.2 | 1362.1312 | 1375.0985
DEER-SFAM-CZ08-V4-eSA-15-HL-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-HL | 15.6882 | 2.6296 | 1338.0005 | 0 | 3.2 | 1338.0005 | 1354.1564
DEER-SFAM-CZ08-V4-eSA-15-HM-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-HM | 14.9929 | 2.5628 | 1377.1236 | 0 | 3.2 | 1377.1236 | 1390.137
DEER-SFAM-CZ08-V4-eSA-15-MH-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-MH | 15.4312 | 2.3755 | 1336.704 | 0 | 2.8 | 1336.704 | 1346.3528
DEER-SFAM-CZ08-V4-eSA-15-ML-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-ML | 15.574 | 2.3249 | 1360.6516 | 0 | 2.8 | 1360.6516 | 1373.6082
DEER-SFAM-CZ08-V4-eSA-15-MM-s1 | 15 | CZ08 | V4 | CZ08-V4-eSA-15 | CZ08-V4-eSA-15-MM | 15.4228 | 2.3647 | 1345.2452 | 0 | 2.8 | 1345.2452 | 1357.0755
DEER-SFAM-CZ08-V4-eSA-16-CH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-CH | 15.263 | 2.7585 | 1548.697 | 0 | 3.2 | 1548.697 | 1556.1612
DEER-SFAM-CZ08-V4-eSA-16-CL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-CL | 15.7115 | 2.6719 | 1473.3885 | 0 | 3.2 | 1473.3885 | 1482.829
DEER-SFAM-CZ08-V4-eSA-16-CM-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-CM | 15.4019 | 2.6997 | 1509.4747 | 0 | 3.2 | 1509.4747 | 1519.4263
DEER-SFAM-CZ08-V4-eSA-16-LH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-LH | 15.7001 | 2.2469 | 1377.7029 | 0 | 2.8 | 1377.7029 | 1390.513
DEER-SFAM-CZ08-V4-eSA-16-LL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-LL | 15.0712 | 2.4157 | 1449.0499 | 0 | 2.8 | 1449.0499 | 1457.4596
DEER-SFAM-CZ08-V4-eSA-16-LM-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-LM | 15.1193 | 2.3602 | 1443.7786 | 0 | 2.8 | 1443.7786 | 1451.4022
DEER-SFAM-CZ08-V4-eSA-16-NM-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-NM | 16.2064 | 2.2998 | 1374.8856 | 0 | 2.8 | 1374.8856 | 1382.3619
DEER-SFAM-CZ08-V4-eSA-16-TH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-TH | 15.7285 | 2.5853 | 1487.0305 | 0 | 2.8 | 1487.0305 | 1491.8255
DEER-SFAM-CZ08-V4-eSA-16-TL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSA-16 | CZ08-V4-eSA-16-TL | 16.2792 | 2.7893 | 1451.0907 | 0 | 3.2 | 1451.0907 | 1456.2804
DEER-SFAM-CZ08-V4-eSA-17-CH-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-CH | 16.3077 | 2.6284 | 1433.3527 | 0 | 3.2 | 1433.3527 | 1442.785
DEER-SFAM-CZ08-V4-eSA-17-CL-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-CL | 16.2512 | 2.6659 | 1436.8172 | 0 | 3.2 | 1436.8172 | 1446.2475
DEER-SFAM-CZ08-V4-eSA-17-CM-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-CM | 16.3415 | 2.666 | 1446.2712 | 0 | 3.2 | 1446.2712 | 1453.7136
DEER-SFAM-CZ08-V4-eSA-17-LH-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-LH | 16.2541 | 2.1943 | 1326.6697 | 0 | 2.8 | 1326.6697 | 1336.7087
DEER-SFAM-CZ08-V4-eSA-17-LL-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-LL | 15.9431 | 2.3218 | 1382.2888 | 0 | 2.8 | 1382.2888 | 1387.7633
DEER-SFAM-CZ08-V4-eSA-17-LM-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-LM | 15.7853 | 2.3124 | 1386.6203 | 0 | 2.8 | 1386.6203 | 1391.3412
DEER-SFAM-CZ08-V4-eSA-17-TH-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-TH | 17.9682 | 2.211 | 1275.5473 | 0 | 2.8 | 1275.5473 | 1283.2136
DEER-SFAM-CZ08-V4-eSA-17-TL-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-TL | 17.6712 | 2.3078 | 1267.054 | 0 | 2.8 | 1267.054 | 1279.0007
DEER-SFAM-CZ08-V4-eSA-17-TM-s2 | 17 | CZ08 | V4 | CZ08-V4-eSA-17 | CZ08-V4-eSA-17-TM | 17.5538 | 2.5324 | 1403.8532 | 0 | 3.2 | 1403.8532 | 1407.8842
DEER-SFAM-CZ08-V4-eSA-18-LH-s2 | 18 | CZ08 | V4 | CZ08-V4-eSA-18 | CZ08-V4-eSA-18-LH | 16.9798 | 2.1541 | 1290.9547 | 0 | 2.8 | 1290.9547 | 1297.5289
DEER-SFAM-CZ08-V4-eSA-18-LL-s2 | 18 | CZ08 | V4 | CZ08-V4-eSA-18 | CZ08-V4-eSA-18-LL | 17.0392 | 2.162 | 1271.7361 | 0 | 2.8 | 1271.7361 | 1280.3165
DEER-SFAM-CZ08-V4-eSA-18-TH-s2 | 18 | CZ08 | V4 | CZ08-V4-eSA-18 | CZ08-V4-eSA-18-TH | 18.616 | 2.3327 | 1257.3015 | 0 | 3.2 | 1257.3015 | 1262.5192
DEER-SFAM-CZ08-V4-eSA-18-TL-s2 | 18 | CZ08 | V4 | CZ08-V4-eSA-18 | CZ08-V4-eSA-18-TL | 17.9359 | 2.2464 | 1303.334 | 0 | 2.8 | 1303.334 | 1309.0535
DEER-SFAM-CZ08-V4-eSA-18-TM-s2 | 18 | CZ08 | V4 | CZ08-V4-eSA-18 | CZ08-V4-eSA-18-TM | 17.9351 | 2.1811 | 1273.7183 | 0 | 2.8 | 1273.7183 | 1279.0406
DEER-SFAM-CZ08-V4-eSH-10-HH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-HH | 10.4705 | 3.5435 | 2003.9425 | 376.5934 | 3.2 | 2380.5359 | 2042.8359
DEER-SFAM-CZ08-V4-eSH-10-HL-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-HL | 10.2054 | 3.7248 | 2075.2299 | 378.503 | 3.2 | 2453.7329 | 2113.6329
DEER-SFAM-CZ08-V4-eSH-10-HM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-HM | 10.7753 | 3.2001 | 1994.6867 | 369.5107 | 2.8 | 2364.1974 | 2031.3974
DEER-SFAM-CZ08-V4-eSH-10-LH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-LH | 10.9081 | 2.9628 | 1935.9493 | 390.5505 | 2.8 | 2326.4998 | 1975.8998
DEER-SFAM-CZ08-V4-eSH-10-LL-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-LL | 10.5941 | 3.2045 | 2019.9261 | 376.8311 | 2.8 | 2396.7572 | 2061.5572
DEER-SFAM-CZ08-V4-eSH-10-LM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-LM | 10.7923 | 3.0736 | 1978.8168 | 375.3785 | 2.8 | 2354.1953 | 2017.0953
DEER-SFAM-CZ08-V4-eSH-10-MH-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-MH | 10.8905 | 3.0623 | 1945.6092 | 384.8843 | 2.8 | 2330.4935 | 1987.9935
DEER-SFAM-CZ08-V4-eSH-10-ML-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-ML | 10.536 | 3.3733 | 2033.3787 | 354.7563 | 2.8 | 2388.135 | 2071.935
DEER-SFAM-CZ08-V4-eSH-10-MM-s1 | 10 | CZ08 | V4 | CZ08-V4-eSH-10 | CZ08-V4-eSH-10-MM | 10.6398 | 3.1132 | 2020.7501 | 377.0714 | 2.8 | 2397.8215 | 2056.9215
DEER-SFAM-CZ08-V4-eSH-13-HH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-HH | 13.0672 | 2.9739 | 1606.4166 | 361.0526 | 3.2 | 1967.4692 | 1641.8692
DEER-SFAM-CZ08-V4-eSH-13-HL-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-HL | 13.0919 | 3.0474 | 1577.8829 | 310.8039 | 3.2 | 1888.6868 | 1613.1868
DEER-SFAM-CZ08-V4-eSH-13-HM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-HM | 13.2019 | 2.9574 | 1596.1823 | 323.1399 | 3.2 | 1919.3222 | 1628.2222
DEER-SFAM-CZ08-V4-eSH-13-LH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-LH | 13.8027 | 2.4244 | 1505.8977 | 362.0126 | 2.8 | 1867.9103 | 1558.5103
DEER-SFAM-CZ08-V4-eSH-13-LL-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-LL | 14.3251 | 2.4951 | 1485.8898 | 324.5591 | 2.8 | 1810.4489 | 1518.2489
DEER-SFAM-CZ08-V4-eSH-13-LM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-LM | 13.2206 | 2.5567 | 1578.127 | 286.2301 | 2.8 | 1864.3571 | 1614.9571
DEER-SFAM-CZ08-V4-eSH-13-MH-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-MH | 14.145 | 2.7122 | 1484.9001 | 364.9237 | 3.2 | 1849.8238 | 1520.4238
DEER-SFAM-CZ08-V4-eSH-13-ML-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-ML | 13.1967 | 2.7108 | 1585.5974 | 329.1482 | 2.8 | 1914.7456 | 1621.9456
DEER-SFAM-CZ08-V4-eSH-13-MM-s1 | 13 | CZ08 | V4 | CZ08-V4-eSH-13 | CZ08-V4-eSH-13-MM | 13.9558 | 2.6497 | 1523.4215 | 336.6726 | 2.8 | 1860.0941 | 1551.8941
DEER-SFAM-CZ08-V4-eSH-14-HH-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-HH | 13.788 | 2.8602 | 1522.0349 | 329.5166 | 3.2 | 1851.5515 | 1549.0515
DEER-SFAM-CZ08-V4-eSH-14-HL-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-HL | 13.836 | 2.8643 | 1513.9772 | 320.2801 | 3.2 | 1834.2573 | 1546.3573
DEER-SFAM-CZ08-V4-eSH-14-HM-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-HM | 13.7885 | 2.7606 | 1512.9722 | 320.0927 | 3.2 | 1833.0649 | 1536.0649
DEER-SFAM-CZ08-V4-eSH-14-MH-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-MH | 14.6207 | 2.2655 | 1414.6351 | 330.2205 | 2.8 | 1744.8556 | 1449.5556
DEER-SFAM-CZ08-V4-eSH-14-ML-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-ML | 14.5918 | 2.7631 | 1424.2338 | 339.6294 | 3.2 | 1763.8632 | 1467.8632
DEER-SFAM-CZ08-V4-eSH-14-MM-s1 | 14 | CZ08 | V4 | CZ08-V4-eSH-14 | CZ08-V4-eSH-14-MM | 14.2705 | 2.4218 | 1441.0032 | 308.3373 | 2.8 | 1749.3405 | 1471.3405
DEER-SFAM-CZ08-V4-eSH-15-HH-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-HH | 14.8375 | 2.5421 | 1389.7844 | 363.1696 | 3.2 | 1752.954 | 1414.754
DEER-SFAM-CZ08-V4-eSH-15-HL-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-HL | 14.9318 | 2.6602 | 1406.9331 | 279.4775 | 3.2 | 1686.4106 | 1431.8106
DEER-SFAM-CZ08-V4-eSH-15-HM-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-HM | 15.6051 | 2.5531 | 1339.8614 | 292.0108 | 3.2 | 1631.8722 | 1364.5722
DEER-SFAM-CZ08-V4-eSH-15-MH-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-MH | 15.8151 | 2.3848 | 1315.0715 | 319.1171 | 2.8 | 1634.1886 | 1338.7886
DEER-SFAM-CZ08-V4-eSH-15-ML-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-ML | 15.54 | 2.6199 | 1338.5364 | 301.6899 | 3.2 | 1640.2263 | 1363.2263
DEER-SFAM-CZ08-V4-eSH-15-MM-s1 | 15 | CZ08 | V4 | CZ08-V4-eSH-15 | CZ08-V4-eSH-15-MM | 15.8546 | 2.5477 | 1330.8553 | 326.0237 | 3.2 | 1656.879 | 1357.179
DEER-SFAM-CZ08-V4-eSH-16-CH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-CH | 15.6479 | 2.6872 | 1504.5106 | 312.1223 | 3.2 | 1816.6329 | 1525.3329
DEER-SFAM-CZ08-V4-eSH-16-CL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-CL | 15.7051 | 2.7421 | 1508.5282 | 291.676 | 3.2 | 1800.2042 | 1530.3042
DEER-SFAM-CZ08-V4-eSH-16-LH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-LH | 15.8364 | 2.2353 | 1358.8309 | 337.7779 | 2.8 | 1696.6088 | 1383.5088
DEER-SFAM-CZ08-V4-eSH-16-LL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-LL | 15.0415 | 2.404 | 1450.2709 | 306.6578 | 2.8 | 1756.9287 | 1470.1287
DEER-SFAM-CZ08-V4-eSH-16-LM-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-LM | 15.217 | 2.3198 | 1424.1965 | 335.8746 | 2.8 | 1760.0711 | 1451.7711
DEER-SFAM-CZ08-V4-eSH-16-TH-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-TH | 16.8775 | 2.6618 | 1378.1577 | 384.2869 | 3.2 | 1762.4446 | 1397.9446
DEER-SFAM-CZ08-V4-eSH-16-TL-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-TL | 15.4923 | 2.6102 | 1517.0016 | 373.3359 | 2.8 | 1890.3375 | 1536.2375
DEER-SFAM-CZ08-V4-eSH-16-TM-s2 | 16 | CZ08 | V4 | CZ08-V4-eSH-16 | CZ08-V4-eSH-16-TM | 15.6976 | 2.5575 | 1497.2706 | 379.4805 | 2.8 | 1876.7511 | 1517.0511
DEER-SFAM-CZ08-V4-eSH-17-CM-s2 | 17 | CZ08 | V4 | CZ08-V4-eSH-17 | CZ08-V4-eSH-17-CM | 16.6235 | 2.5938 | 1424.0801 | 310.4031 | 3.2 | 1734.4832 | 1447.6832
DEER-SFAM-CZ08-V4-eSH-17-LM-s2 | 17 | CZ08 | V4 | CZ08-V4-eSH-17 | CZ08-V4-eSH-17-LM | 16.186 | 2.2538 | 1369.4849 | 298.3709 | 2.8 | 1667.8558 | 1380.6558
DEER-SFAM-CZ08-V4-eSH-17-TH-s2 | 17 | CZ08 | V4 | CZ08-V4-eSH-17 | CZ08-V4-eSH-17-TH | 17.7873 | 2.5066 | 1305.8128 | 381.9874 | 3.2 | 1687.8002 | 1327.1002
DEER-SFAM-CZ08-V4-eSH-17-TL-s2 | 17 | CZ08 | V4 | CZ08-V4-eSH-17 | CZ08-V4-eSH-17-TL | 17.6477 | 2.5656 | 1317.4077 | 376.285 | 3.2 | 1693.6927 | 1338.3927
DEER-SFAM-CZ08-V4-eSH-18-LH-s2 | 18 | CZ08 | V4 | CZ08-V4-eSH-18 | CZ08-V4-eSH-18-LH | 17.1202 | 2.173 | 1272.4076 | 331.1709 | 2.8 | 1603.5785 | 1290.1785
DEER-SFAM-CZ08-V4-eSH-18-LL-s2 | 18 | CZ08 | V4 | CZ08-V4-eSH-18 | CZ08-V4-eSH-18-LL | 16.3538 | 2.2586 | 1326.1856 | 304.0651 | 2.8 | 1630.2507 | 1343.2507
DEER-SFAM-CZ08-V4-eSH-18-LM-s2 | 18 | CZ08 | V4 | CZ08-V4-eSH-18 | CZ08-V4-eSH-18-LM | 17.0483 | 2.1944 | 1286.5751 | 346.1434 | 2.8 | 1632.7185 | 1306.8185
DEER-SFAM-CZ08-V4-eSH-18-TM-s2 | 18 | CZ08 | V4 | CZ08-V4-eSH-18 | CZ08-V4-eSH-18-TM | 18.8458 | 2.1635 | 1223.3965 | 368.9886 | 2.8 | 1592.3851 | 1257.0851
DEER-SFAM-CZ09-V1-eSA-10-HH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-HH | 9.7377 | 4.052 | 2136.827 | 0 | 3.6518 | 2136.827 | 2217.4811
DEER-SFAM-CZ09-V1-eSA-10-HL-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-HL | 9.2958 | 4.4226 | 2199.01 | 0 | 3.6518 | 2199.01 | 2279.7326
DEER-SFAM-CZ09-V1-eSA-10-HM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-HM | 9.2835 | 3.8975 | 2146.5669 | 0 | 3.6518 | 2146.5669 | 2227.2778
DEER-SFAM-CZ09-V1-eSA-10-LH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-LH | 10.7151 | 3.8101 | 1970.3421 | 0 | 3.6518 | 1970.3421 | 2051.1288
DEER-SFAM-CZ09-V1-eSA-10-LL-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-LL | 9.5403 | 4.2202 | 2140.4288 | 0 | 3.6518 | 2140.4288 | 2221.1664
DEER-SFAM-CZ09-V1-eSA-10-LM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-LM | 10.529 | 3.8917 | 1996.7426 | 0 | 3.6518 | 1996.7426 | 2077.5324
DEER-SFAM-CZ09-V1-eSA-10-MH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-MH | 10.4959 | 3.7308 | 1999.1179 | 0 | 3.6518 | 1999.1179 | 2079.8827
DEER-SFAM-CZ09-V1-eSA-10-ML-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-ML | 9.4359 | 4.2804 | 2196.887 | 0 | 3.6518 | 2196.887 | 2277.6108
DEER-SFAM-CZ09-V1-eSA-10-MM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSA-10 | CZ09-V1-eSA-10-MM | 10.4551 | 3.665 | 1961.1061 | 0 | 3.3147 | 1961.1061 | 2041.7648
DEER-SFAM-CZ09-V1-eSA-13-HH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-HH | 12.1757 | 3.2914 | 1637.5736 | 0 | 3.6518 | 1637.5736 | 1710.3384
DEER-SFAM-CZ09-V1-eSA-13-HL-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-HL | 12.7567 | 3.3745 | 1586.8768 | 0 | 3.6518 | 1586.8768 | 1650.5598
DEER-SFAM-CZ09-V1-eSA-13-HM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-HM | 12.3939 | 3.4098 | 1625.1345 | 0 | 3.6518 | 1625.1345 | 1697.8737
DEER-SFAM-CZ09-V1-eSA-13-LH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-LH | 13.452 | 2.9691 | 1523.5495 | 0 | 3.6518 | 1523.5495 | 1604.2914
DEER-SFAM-CZ09-V1-eSA-13-LL-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-LL | 12.8674 | 3.2389 | 1607.0669 | 0 | 3.6518 | 1607.0669 | 1687.649
DEER-SFAM-CZ09-V1-eSA-13-LM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-LM | 12.9739 | 3.0912 | 1586.5157 | 0 | 3.6518 | 1586.5157 | 1667.1906
DEER-SFAM-CZ09-V1-eSA-13-MH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-MH | 13.4342 | 3.0515 | 1565.6586 | 0 | 3.6518 | 1565.6586 | 1646.3698
DEER-SFAM-CZ09-V1-eSA-13-ML-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-ML | 12.3443 | 3.3377 | 1603.0164 | 0 | 3.6518 | 1603.0164 | 1683.4764
DEER-SFAM-CZ09-V1-eSA-13-MM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSA-13 | CZ09-V1-eSA-13-MM | 13.3381 | 3.2241 | 1557.2208 | 0 | 3.6518 | 1557.2208 | 1637.9198
DEER-SFAM-CZ09-V1-eSA-14-HH-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-HH | 12.6155 | 3.1768 | 1564.4 | 0 | 3.6518 | 1564.4 | 1632.0427
DEER-SFAM-CZ09-V1-eSA-14-HL-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-HL | 13.9381 | 3.1624 | 1482.7665 | 0 | 3.6518 | 1482.7665 | 1532.507
DEER-SFAM-CZ09-V1-eSA-14-HM-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-HM | 13.8098 | 3.1193 | 1489.2302 | 0 | 3.6518 | 1489.2302 | 1565.5454
DEER-SFAM-CZ09-V1-eSA-14-MH-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-MH | 13.8369 | 2.8857 | 1516.5389 | 0 | 3.6518 | 1516.5389 | 1569.5664
DEER-SFAM-CZ09-V1-eSA-14-ML-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-ML | 13.6131 | 3.0459 | 1472.1053 | 0 | 3.6518 | 1472.1053 | 1556.801
DEER-SFAM-CZ09-V1-eSA-14-MM-s1 | 14 | CZ09 | V1 | CZ09-V1-eSA-14 | CZ09-V1-eSA-14-MM | 14.0398 | 2.7004 | 1462.495 | 0 | 3.3147 | 1462.495 | 1520.5784
DEER-SFAM-CZ09-V1-eSA-15-HH-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-HH | 14.1254 | 2.9122 | 1414.9477 | 0 | 3.6518 | 1414.9477 | 1471.3394
DEER-SFAM-CZ09-V1-eSA-15-HL-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-HL | 14.9293 | 2.8719 | 1371.9728 | 0 | 3.6518 | 1371.9728 | 1442.2527
DEER-SFAM-CZ09-V1-eSA-15-HM-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-HM | 13.9734 | 2.7827 | 1415.1795 | 0 | 3.6518 | 1415.1795 | 1471.7792
DEER-SFAM-CZ09-V1-eSA-15-MH-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-MH | 14.4732 | 2.8645 | 1395.6735 | 0 | 3.6518 | 1395.6735 | 1437.692
DEER-SFAM-CZ09-V1-eSA-15-ML-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-ML | 14.8456 | 2.8875 | 1398.1646 | 0 | 3.6518 | 1398.1646 | 1454.6645
DEER-SFAM-CZ09-V1-eSA-15-MM-s1 | 15 | CZ09 | V1 | CZ09-V1-eSA-15 | CZ09-V1-eSA-15-MM | 14.8659 | 2.8539 | 1370.1315 | 0 | 3.6518 | 1370.1315 | 1421.6553
DEER-SFAM-CZ09-V1-eSA-16-CH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-CH | 14.527 | 3.1319 | 1734.8154 | 0 | 3.6518 | 1734.8154 | 1766.7804
DEER-SFAM-CZ09-V1-eSA-16-CL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-CL | 14.737 | 3.1686 | 1648.9591 | 0 | 3.6518 | 1648.9591 | 1689.5487
DEER-SFAM-CZ09-V1-eSA-16-CM-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-CM | 14.4846 | 3.1672 | 1696.3285 | 0 | 3.6518 | 1696.3285 | 1739.166
DEER-SFAM-CZ09-V1-eSA-16-LH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-LH | 14.294 | 2.8407 | 1525.1524 | 0 | 3.6518 | 1525.1524 | 1580.304
DEER-SFAM-CZ09-V1-eSA-16-LL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-LL | 13.7652 | 3.154 | 1614.0883 | 0 | 3.6518 | 1614.0883 | 1650.4756
DEER-SFAM-CZ09-V1-eSA-16-LM-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-LM | 13.9862 | 3.0448 | 1594.9315 | 0 | 3.6518 | 1594.9315 | 1627.9146
DEER-SFAM-CZ09-V1-eSA-16-NM-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-NM | 15.4757 | 2.8029 | 1464.4816 | 0 | 3.6518 | 1464.4816 | 1496.8177
DEER-SFAM-CZ09-V1-eSA-16-TH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-TH | 14.1047 | 3.2947 | 1839.0501 | 0 | 3.6518 | 1839.0501 | 1859.4955
DEER-SFAM-CZ09-V1-eSA-16-TL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSA-16 | CZ09-V1-eSA-16-TL | 14.6954 | 2.9242 | 1712.6855 | 0 | 3.6518 | 1712.6855 | 1734.8783
DEER-SFAM-CZ09-V1-eSA-17-CH-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-CH | 15.4122 | 2.99 | 1599.8057 | 0 | 3.6518 | 1599.8057 | 1640.3736
DEER-SFAM-CZ09-V1-eSA-17-CL-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-CL | 15.3383 | 3.0474 | 1602.4613 | 0 | 3.6518 | 1602.4613 | 1643.0203
DEER-SFAM-CZ09-V1-eSA-17-CM-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-CM | 15.4386 | 3.0325 | 1627.4218 | 0 | 3.6518 | 1627.4218 | 1659.2913
DEER-SFAM-CZ09-V1-eSA-17-LH-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-LH | 14.8115 | 2.7953 | 1471.1015 | 0 | 3.6518 | 1471.1015 | 1514.384
DEER-SFAM-CZ09-V1-eSA-17-LL-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-LL | 14.5756 | 3.0128 | 1547.3372 | 0 | 3.6518 | 1547.3372 | 1570.9868
DEER-SFAM-CZ09-V1-eSA-17-LM-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-LM | 14.4632 | 2.9089 | 1534.3193 | 0 | 3.6518 | 1534.3193 | 1554.7452
DEER-SFAM-CZ09-V1-eSA-17-TH-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-TH | 16.0546 | 2.7298 | 1527.5172 | 0 | 3.6518 | 1527.5172 | 1560.3566
DEER-SFAM-CZ09-V1-eSA-17-TL-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-TL | 16.2858 | 2.575 | 1449.3578 | 0 | 3.6518 | 1449.3578 | 1500.7316
DEER-SFAM-CZ09-V1-eSA-17-TM-s2 | 17 | CZ09 | V1 | CZ09-V1-eSA-17 | CZ09-V1-eSA-17-TM | 15.8919 | 3.0335 | 1741.1057 | 0 | 3.6518 | 1741.1057 | 1758.2093
DEER-SFAM-CZ09-V1-eSA-18-LH-s2 | 18 | CZ09 | V1 | CZ09-V1-eSA-18 | CZ09-V1-eSA-18-LH | 15.4259 | 2.793 | 1452.0278 | 0 | 3.6518 | 1452.0278 | 1480.4712
DEER-SFAM-CZ09-V1-eSA-18-LL-s2 | 18 | CZ09 | V1 | CZ09-V1-eSA-18 | CZ09-V1-eSA-18-LL | 15.7585 | 2.6661 | 1397.3529 | 0 | 3.6518 | 1397.3529 | 1434.466
DEER-SFAM-CZ09-V1-eSA-18-TH-s2 | 18 | CZ09 | V1 | CZ09-V1-eSA-18 | CZ09-V1-eSA-18-TH | 16.6345 | 2.5533 | 1479.3645 | 0 | 3.6518 | 1479.3645 | 1501.7286
DEER-SFAM-CZ09-V1-eSA-18-TL-s2 | 18 | CZ09 | V1 | CZ09-V1-eSA-18 | CZ09-V1-eSA-18-TL | 16.0192 | 2.9628 | 1603.1688 | 0 | 3.6518 | 1603.1688 | 1627.5786
DEER-SFAM-CZ09-V1-eSA-18-TM-s2 | 18 | CZ09 | V1 | CZ09-V1-eSA-18 | CZ09-V1-eSA-18-TM | 16.1473 | 2.6382 | 1511.7992 | 0 | 3.6518 | 1511.7992 | 1534.624
DEER-SFAM-CZ09-V1-eSH-10-HH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-HH | 10.2423 | 3.9549 | 2027.1858 | 1608.5864 | 3.6518 | 3635.7722 | 2194.6407
DEER-SFAM-CZ09-V1-eSH-10-HL-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-HL | 9.9112 | 4.1622 | 2106.5911 | 1627.2324 | 3.6518 | 3733.8235 | 2273.9108
DEER-SFAM-CZ09-V1-eSH-10-HM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-HM | 10.2339 | 4.0786 | 2064.0933 | 1556.6711 | 3.6518 | 3620.7644 | 2223.5771
DEER-SFAM-CZ09-V1-eSH-10-LH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-LH | 10.5394 | 3.7012 | 1982.714 | 1710.3686 | 3.6518 | 3693.0826 | 2156.2412
DEER-SFAM-CZ09-V1-eSH-10-LL-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-LL | 10.2179 | 3.9412 | 2059.1403 | 1592.8124 | 3.6518 | 3651.9528 | 2238.1985
DEER-SFAM-CZ09-V1-eSH-10-LM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-LM | 10.3826 | 3.893 | 2019.3694 | 1585.1216 | 3.6518 | 3604.4911 | 2183.2926
DEER-SFAM-CZ09-V1-eSH-10-MH-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-MH | 10.5851 | 3.8434 | 1990.8128 | 1674.1635 | 3.6518 | 3664.9763 | 2175.1305
DEER-SFAM-CZ09-V1-eSH-10-ML-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-ML | 10.1868 | 4.1556 | 2070.4885 | 1484.0491 | 3.6518 | 3554.5376 | 2234.1896
DEER-SFAM-CZ09-V1-eSH-10-MM-s1 | 10 | CZ09 | V1 | CZ09-V1-eSH-10 | CZ09-V1-eSH-10-MM | 10.1321 | 4.0475 | 2088.4879 | 1618.1425 | 3.6518 | 3706.6304 | 2244.2288
DEER-SFAM-CZ09-V1-eSH-13-HH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-HH | 11.9861 | 3.3152 | 1678.5367 | 1531.8717 | 3.6518 | 3210.4084 | 1831.2724
DEER-SFAM-CZ09-V1-eSH-13-HL-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-HL | 12.8007 | 3.3721 | 1585.8753 | 1321.0792 | 3.6518 | 2906.9545 | 1737.6266
DEER-SFAM-CZ09-V1-eSH-13-HM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-HM | 12.201 | 3.3341 | 1657.4241 | 1364.5801 | 3.6518 | 3022.0043 | 1794.5625
DEER-SFAM-CZ09-V1-eSH-13-LH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-LH | 13.3809 | 2.9759 | 1539.183 | 1587.3839 | 3.6518 | 3126.5669 | 1770.5224
DEER-SFAM-CZ09-V1-eSH-13-LL-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-LL | 13.6506 | 3.1353 | 1533.0606 | 1392.8523 | 3.6518 | 2925.9129 | 1672.0046
DEER-SFAM-CZ09-V1-eSH-13-LM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-LM | 12.802 | 3.1417 | 1599.3532 | 1251.0067 | 3.6518 | 2850.3599 | 1759.4493
DEER-SFAM-CZ09-V1-eSH-13-MH-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-MH | 13.4823 | 3.084 | 1531.2307 | 1546.7069 | 3.6518 | 3077.9376 | 1685.9645
DEER-SFAM-CZ09-V1-eSH-13-ML-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-ML | 12.6203 | 3.3176 | 1616.178 | 1454.5273 | 3.6518 | 3070.7053 | 1774.8528
DEER-SFAM-CZ09-V1-eSH-13-MM-s1 | 13 | CZ09 | V1 | CZ09-V1-eSH-13 | CZ09-V1-eSH-13-MM | 13.1479 | 3.3047 | 1584.0006 | 1439.0765 | 3.6518 | 3023.0771 | 1707.555
DEER-SFAM-CZ09-V1-eSH-14-HH-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-HH | 12.6742 | 3.1424 | 1591.031 | 1392.494 | 3.6518 | 2983.5251 | 1707.2395
DEER-SFAM-CZ09-V1-eSH-14-HL-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-HL | 12.9329 | 3.1419 | 1555.2163 | 1360.594 | 3.6518 | 2915.8103 | 1695.4645
DEER-SFAM-CZ09-V1-eSH-14-HM-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-HM | 12.8684 | 3.0171 | 1554.5416 | 1349.4536 | 3.6518 | 2903.9951 | 1653.5868
DEER-SFAM-CZ09-V1-eSH-14-MH-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-MH | 14.2029 | 2.8023 | 1441.4794 | 1431.4699 | 3.6518 | 2872.9493 | 1592.878
DEER-SFAM-CZ09-V1-eSH-14-ML-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-ML | 14.3806 | 3.0202 | 1434.3384 | 1497.8326 | 3.6518 | 2932.171 | 1625.7181
DEER-SFAM-CZ09-V1-eSH-14-MM-s1 | 14 | CZ09 | V1 | CZ09-V1-eSH-14 | CZ09-V1-eSH-14-MM | 14.0029 | 2.9571 | 1450.6443 | 1329.1054 | 3.6518 | 2779.7497 | 1582.9664
DEER-SFAM-CZ09-V1-eSH-15-HH-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-HH | 13.7425 | 2.7656 | 1436.9016 | 1599.1464 | 3.6518 | 3036.048 | 1545.8607
DEER-SFAM-CZ09-V1-eSH-15-HL-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-HL | 14.0586 | 3.0136 | 1441.7964 | 1175.8825 | 3.6518 | 2617.6789 | 1549.0607
DEER-SFAM-CZ09-V1-eSH-15-HM-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-HM | 14.9878 | 2.8788 | 1366.6857 | 1214.8487 | 3.6518 | 2581.5344 | 1474.4319
DEER-SFAM-CZ09-V1-eSH-15-MH-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-MH | 14.9852 | 2.8463 | 1367.5974 | 1433.3422 | 3.6518 | 2800.9396 | 1472.2724
DEER-SFAM-CZ09-V1-eSH-15-ML-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-ML | 15.2982 | 2.8705 | 1344.2865 | 1314.0708 | 3.6518 | 2658.3573 | 1451.9959
DEER-SFAM-CZ09-V1-eSH-15-MM-s1 | 15 | CZ09 | V1 | CZ09-V1-eSH-15 | CZ09-V1-eSH-15-MM | 15.1365 | 2.8486 | 1365.1423 | 1386.3832 | 3.6518 | 2751.5255 | 1478.4654
DEER-SFAM-CZ09-V1-eSH-16-CH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-CH | 14.7536 | 3.1045 | 1686.9169 | 1432.4505 | 3.6518 | 3119.3674 | 1775.4167
DEER-SFAM-CZ09-V1-eSH-16-CL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-CL | 14.8772 | 3.1319 | 1703.5602 | 1328.0063 | 3.6518 | 3031.5665 | 1795.8703
DEER-SFAM-CZ09-V1-eSH-16-LH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-LH | 14.1367 | 2.7978 | 1527.1699 | 1568.1627 | 3.6518 | 3095.3327 | 1635.7212
DEER-SFAM-CZ09-V1-eSH-16-LL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-LL | 13.9231 | 3.064 | 1585.599 | 1408.0135 | 3.6518 | 2993.6125 | 1672.2957
DEER-SFAM-CZ09-V1-eSH-16-LM-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-LM | 13.7371 | 2.9063 | 1581.4823 | 1565.1051 | 3.6518 | 3146.5874 | 1702.909
DEER-SFAM-CZ09-V1-eSH-16-TH-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-TH | 14.9404 | 2.966 | 1633.1459 | 1803.3438 | 3.6518 | 3436.4897 | 1719.6395
DEER-SFAM-CZ09-V1-eSH-16-TL-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-TL | 14.267 | 3.3806 | 1828.3709 | 1792.2528 | 3.6518 | 3620.6237 | 1905.606
DEER-SFAM-CZ09-V1-eSH-16-TM-s2 | 16 | CZ09 | V1 | CZ09-V1-eSH-16 | CZ09-V1-eSH-16-TM | 14.4362 | 3.3205 | 1807.1746 | 1825.0625 | 3.6518 | 3632.2372 | 1886.494
DEER-SFAM-CZ09-V1-eSH-17-CM-s2 | 17 | CZ09 | V1 | CZ09-V1-eSH-17 | CZ09-V1-eSH-17-CM | 15.7214 | 2.9755 | 1610.2861 | 1519.2171 | 3.6518 | 3129.5032 | 1718.3561
DEER-SFAM-CZ09-V1-eSH-17-LM-s2 | 17 | CZ09 | V1 | CZ09-V1-eSH-17 | CZ09-V1-eSH-17-LM | 14.6844 | 2.9352 | 1553.7921 | 1369.4475 | 3.6518 | 2923.2396 | 1602.6192
DEER-SFAM-CZ09-V1-eSH-17-TH-s2 | 17 | CZ09 | V1 | CZ09-V1-eSH-17 | CZ09-V1-eSH-17-TH | 15.9098 | 2.7742 | 1532.5198 | 1797.3016 | 3.6518 | 3329.8214 | 1625.2636
DEER-SFAM-CZ09-V1-eSH-17-TL-s2 | 17 | CZ09 | V1 | CZ09-V1-eSH-17 | CZ09-V1-eSH-17-TL | 15.7851 | 2.8462 | 1546.7643 | 1779.1259 | 3.6518 | 3325.8902 | 1638.3948
DEER-SFAM-CZ09-V1-eSH-18-LH-s2 | 18 | CZ09 | V1 | CZ09-V1-eSH-18 | CZ09-V1-eSH-18-LH | 15.6167 | 2.7213 | 1423.4572 | 1575.2065 | 3.6518 | 2998.6637 | 1502.0032
DEER-SFAM-CZ09-V1-eSH-18-LL-s2 | 18 | CZ09 | V1 | CZ09-V1-eSH-18 | CZ09-V1-eSH-18-LL | 14.9962 | 2.7656 | 1462.4823 | 1406.0712 | 3.6518 | 2868.5536 | 1537.3439
DEER-SFAM-CZ09-V1-eSH-18-LM-s2 | 18 | CZ09 | V1 | CZ09-V1-eSH-18 | CZ09-V1-eSH-18-LM | 15.4807 | 2.8408 | 1448.0558 | 1661.651 | 3.6518 | 3109.7068 | 1538.0396
DEER-SFAM-CZ09-V1-eSH-18-TM-s2 | 18 | CZ09 | V1 | CZ09-V1-eSH-18 | CZ09-V1-eSH-18-TM | 16.9168 | 2.7985 | 1469.6186 | 1767.1832 | 3.6518 | 3236.8019 | 1607.0275
DEER-SFAM-CZ09-V2-eSA-10-HH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-HH | 9.7796 | 3.7207 | 2124.0586 | 0 | 3.3462 | 2124.0586 | 2164.7561
DEER-SFAM-CZ09-V2-eSA-10-HL-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-HL | 9.294 | 4.0629 | 2199.5187 | 0 | 3.3462 | 2199.5187 | 2240.2549
DEER-SFAM-CZ09-V2-eSA-10-HM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-HM | 9.3013 | 3.5824 | 2145.2312 | 0 | 3.3462 | 2145.2312 | 2185.9604
DEER-SFAM-CZ09-V2-eSA-10-LH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-LH | 10.6637 | 3.5381 | 1974.26 | 0 | 3.3462 | 1974.26 | 2015.0352
DEER-SFAM-CZ09-V2-eSA-10-LL-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-LL | 9.5242 | 3.8882 | 2145.3149 | 0 | 3.3462 | 2145.3149 | 2186.06
DEER-SFAM-CZ09-V2-eSA-10-LM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-LM | 10.4863 | 3.6029 | 1998.4734 | 0 | 3.3462 | 1998.4734 | 2039.2504
DEER-SFAM-CZ09-V2-eSA-10-MH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-MH | 10.4679 | 3.4579 | 1999.585 | 0 | 3.3462 | 1999.585 | 2040.3465
DEER-SFAM-CZ09-V2-eSA-10-ML-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-ML | 9.413 | 3.9429 | 2198.8565 | 0 | 3.3462 | 2198.8565 | 2239.5932
DEER-SFAM-CZ09-V2-eSA-10-MM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSA-10 | CZ09-V2-eSA-10-MM | 10.3736 | 3.5985 | 1974.5995 | 0 | 3.3462 | 1974.5995 | 2015.3402
DEER-SFAM-CZ09-V2-eSA-13-HH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-HH | 12.2165 | 3.0532 | 1642.5311 | 0 | 3.3462 | 1642.5311 | 1679.252
DEER-SFAM-CZ09-V2-eSA-13-HL-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-HL | 12.7738 | 3.1463 | 1588.2007 | 0 | 3.3462 | 1588.2007 | 1620.3375
DEER-SFAM-CZ09-V2-eSA-13-HM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-HM | 12.3118 | 3.284 | 1642.1827 | 0 | 3.5578 | 1642.1827 | 1678.9064
DEER-SFAM-CZ09-V2-eSA-13-LH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-LH | 13.4222 | 2.7621 | 1526.3436 | 0 | 3.3462 | 1526.3436 | 1567.0912
DEER-SFAM-CZ09-V2-eSA-13-LL-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-LL | 12.8385 | 3.0114 | 1612.8042 | 0 | 3.3462 | 1612.8042 | 1653.4595
DEER-SFAM-CZ09-V2-eSA-13-LM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-LM | 12.9391 | 2.8737 | 1591.6022 | 0 | 3.3462 | 1591.6022 | 1632.3114
DEER-SFAM-CZ09-V2-eSA-13-MH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-MH | 13.4438 | 2.8285 | 1563.636 | 0 | 3.3462 | 1563.636 | 1604.3654
DEER-SFAM-CZ09-V2-eSA-13-ML-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-ML | 12.3597 | 3.1072 | 1604.5454 | 0 | 3.3462 | 1604.5454 | 1645.1469
DEER-SFAM-CZ09-V2-eSA-13-MM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSA-13 | CZ09-V2-eSA-13-MM | 13.3432 | 2.9989 | 1555.8848 | 0 | 3.3462 | 1555.8848 | 1596.6074
DEER-SFAM-CZ09-V2-eSA-14-HH-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-HH | 12.611 | 2.9527 | 1567.7638 | 0 | 3.3462 | 1567.7638 | 1601.8977
DEER-SFAM-CZ09-V2-eSA-14-HL-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-HL | 13.9073 | 2.9209 | 1487.8582 | 0 | 3.3462 | 1487.8582 | 1512.9589
DEER-SFAM-CZ09-V2-eSA-14-HM-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-HM | 13.7732 | 2.9172 | 1495.3476 | 0 | 3.3462 | 1495.3476 | 1533.8611
DEER-SFAM-CZ09-V2-eSA-14-MH-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-MH | 13.7954 | 2.6805 | 1519.9885 | 0 | 3.3462 | 1519.9885 | 1546.7465
DEER-SFAM-CZ09-V2-eSA-14-ML-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-ML | 13.5902 | 2.8442 | 1477.3168 | 0 | 3.3462 | 1477.3168 | 1520.0566
DEER-SFAM-CZ09-V2-eSA-14-MM-s1 | 14 | CZ09 | V2 | CZ09-V2-eSA-14 | CZ09-V2-eSA-14-MM | 13.8263 | 2.6897 | 1482.8067 | 0 | 3.3462 | 1482.8067 | 1512.1453
DEER-SFAM-CZ09-V2-eSA-15-HH-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-HH | 14.0343 | 2.7867 | 1429.6618 | 0 | 3.5578 | 1429.6618 | 1458.1339
DEER-SFAM-CZ09-V2-eSA-15-HL-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-HL | 14.8236 | 2.7754 | 1383.9926 | 0 | 3.5578 | 1383.9926 | 1419.4742
DEER-SFAM-CZ09-V2-eSA-15-HM-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-HM | 13.9514 | 2.669 | 1425.7646 | 0 | 3.5578 | 1425.7646 | 1454.341
DEER-SFAM-CZ09-V2-eSA-15-MH-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-MH | 14.4289 | 2.6834 | 1399.2203 | 0 | 3.3462 | 1399.2203 | 1420.4262
DEER-SFAM-CZ09-V2-eSA-15-ML-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-ML | 14.8132 | 2.6908 | 1403.7516 | 0 | 3.3462 | 1403.7516 | 1432.257
DEER-SFAM-CZ09-V2-eSA-15-MM-s1 | 15 | CZ09 | V2 | CZ09-V2-eSA-15 | CZ09-V2-eSA-15-MM | 14.8186 | 2.6697 | 1373.7733 | 0 | 3.3462 | 1373.7733 | 1399.7752
DEER-SFAM-CZ09-V2-eSA-16-CH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-CH | 14.4704 | 2.8877 | 1683.1002 | 0 | 3.3462 | 1683.1002 | 1699.4388
DEER-SFAM-CZ09-V2-eSA-16-CL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-CL | 14.7927 | 3.0165 | 1606.0359 | 0 | 3.5578 | 1606.0359 | 1626.7266
DEER-SFAM-CZ09-V2-eSA-16-CM-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-CM | 14.4882 | 3.04 | 1655.799 | 0 | 3.5578 | 1655.799 | 1677.6275
DEER-SFAM-CZ09-V2-eSA-16-LH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-LH | 14.4021 | 2.6114 | 1488.7267 | 0 | 3.3462 | 1488.7267 | 1516.755
DEER-SFAM-CZ09-V2-eSA-16-LL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-LL | 13.8372 | 2.9058 | 1580.7671 | 0 | 3.3462 | 1580.7671 | 1599.25
DEER-SFAM-CZ09-V2-eSA-16-LM-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-LM | 14.0132 | 2.8028 | 1561.8752 | 0 | 3.3462 | 1561.8752 | 1578.6353
DEER-SFAM-CZ09-V2-eSA-16-NM-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-NM | 15.5542 | 2.5634 | 1425.8902 | 0 | 3.3462 | 1425.8902 | 1442.3265
DEER-SFAM-CZ09-V2-eSA-16-TH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-TH | 14.1777 | 3.0431 | 1757.7865 | 0 | 3.3462 | 1757.7865 | 1768.2854
DEER-SFAM-CZ09-V2-eSA-16-TL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSA-16 | CZ09-V2-eSA-16-TL | 14.8271 | 2.6909 | 1632.9553 | 0 | 3.3462 | 1632.9553 | 1644.3372
DEER-SFAM-CZ09-V2-eSA-17-CH-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-CH | 15.3705 | 2.7573 | 1554.6781 | 0 | 3.3462 | 1554.6781 | 1575.3449
DEER-SFAM-CZ09-V2-eSA-17-CL-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-CL | 15.3099 | 2.8093 | 1555.9197 | 0 | 3.3462 | 1555.9197 | 1576.5816
DEER-SFAM-CZ09-V2-eSA-17-CM-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-CM | 15.4078 | 2.7957 | 1576.1346 | 0 | 3.3462 | 1576.1346 | 1592.4244
DEER-SFAM-CZ09-V2-eSA-17-LH-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-LH | 14.9011 | 2.5609 | 1438.9724 | 0 | 3.3462 | 1438.9724 | 1460.9493
DEER-SFAM-CZ09-V2-eSA-17-LL-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-LL | 14.6207 | 2.7743 | 1514.4805 | 0 | 3.3462 | 1514.4805 | 1526.5066
DEER-SFAM-CZ09-V2-eSA-17-LM-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-LM | 14.5175 | 2.6806 | 1505.6192 | 0 | 3.3462 | 1505.6192 | 1515.9973
DEER-SFAM-CZ09-V2-eSA-17-TH-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-TH | 16.0673 | 2.529 | 1482.4595 | 0 | 3.3462 | 1482.4595 | 1499.2682
DEER-SFAM-CZ09-V2-eSA-17-TL-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-TL | 16.3534 | 2.3899 | 1399.3589 | 0 | 3.3462 | 1399.3589 | 1425.5963
DEER-SFAM-CZ09-V2-eSA-17-TM-s2 | 17 | CZ09 | V2 | CZ09-V2-eSA-17 | CZ09-V2-eSA-17-TM | 15.9778 | 2.9046 | 1663.0108 | 0 | 3.5578 | 1663.0108 | 1671.8411
DEER-SFAM-CZ09-V2-eSA-18-LH-s2 | 18 | CZ09 | V2 | CZ09-V2-eSA-18 | CZ09-V2-eSA-18-LH | 15.4978 | 2.5729 | 1418.3322 | 0 | 3.3462 | 1418.3322 | 1432.7853
DEER-SFAM-CZ09-V2-eSA-18-LL-s2 | 18 | CZ09 | V2 | CZ09-V2-eSA-18 | CZ09-V2-eSA-18-LL | 15.8309 | 2.4576 | 1369.4834 | 0 | 3.3462 | 1369.4834 | 1388.3431
DEER-SFAM-CZ09-V2-eSA-18-TH-s2 | 18 | CZ09 | V2 | CZ09-V2-eSA-18 | CZ09-V2-eSA-18-TH | 16.7104 | 2.3648 | 1431.1671 | 0 | 3.3462 | 1431.1671 | 1442.6101
DEER-SFAM-CZ09-V2-eSA-18-TL-s2 | 18 | CZ09 | V2 | CZ09-V2-eSA-18 | CZ09-V2-eSA-18-TL | 16.0884 | 2.7345 | 1538.722 | 0 | 3.3462 | 1538.722 | 1551.2451
DEER-SFAM-CZ09-V2-eSA-18-TM-s2 | 18 | CZ09 | V2 | CZ09-V2-eSA-18 | CZ09-V2-eSA-18-TM | 16.1689 | 2.4414 | 1465.9354 | 0 | 3.3462 | 1465.9354 | 1477.6135
DEER-SFAM-CZ09-V2-eSH-10-HH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-HH | 10.1796 | 3.675 | 2034.8634 | 810.3089 | 3.3462 | 2845.1723 | 2118.0255
DEER-SFAM-CZ09-V2-eSH-10-HL-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-HL | 9.8627 | 3.866 | 2110.0597 | 815.9037 | 3.3462 | 2925.9634 | 2192.9704
DEER-SFAM-CZ09-V2-eSH-10-HM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-HM | 10.2587 | 3.7729 | 2058.8242 | 788.3666 | 3.3462 | 2847.1908 | 2137.8902
DEER-SFAM-CZ09-V2-eSH-10-LH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-LH | 10.5355 | 3.4319 | 1983.6232 | 860.4476 | 3.3462 | 2844.0708 | 2069.6732
DEER-SFAM-CZ09-V2-eSH-10-LL-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-LL | 10.201 | 3.6481 | 2056.2635 | 801.452 | 3.3462 | 2857.7155 | 2145.2421
DEER-SFAM-CZ09-V2-eSH-10-LM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-LM | 10.387 | 3.6149 | 2018.0527 | 801.4677 | 3.3462 | 2819.5204 | 2099.6429
DEER-SFAM-CZ09-V2-eSH-10-MH-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-MH | 10.569 | 3.561 | 1990.6395 | 840.3983 | 3.3462 | 2831.0378 | 2082.0061
DEER-SFAM-CZ09-V2-eSH-10-ML-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-ML | 10.1712 | 3.8593 | 2070.0938 | 747.2527 | 3.3462 | 2817.3464 | 2151.7007
DEER-SFAM-CZ09-V2-eSH-10-MM-s1 | 10 | CZ09 | V2 | CZ09-V2-eSH-10 | CZ09-V2-eSH-10-MM | 10.1642 | 3.7321 | 2079.0957 | 812.7933 | 3.3462 | 2891.889 | 2156.5497
DEER-SFAM-CZ09-V2-eSH-13-HH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-HH | 12.0076 | 3.0531 | 1687.648 | 773.8433 | 3.3462 | 2461.4913 | 1763.4987
DEER-SFAM-CZ09-V2-eSH-13-HL-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-HL | 12.7415 | 3.2708 | 1600.5454 | 663.0607 | 3.5578 | 2263.6061 | 1676
DEER-SFAM-CZ09-V2-eSH-13-HM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-HM | 12.2265 | 3.0656 | 1665.631 | 688.2523 | 3.3462 | 2353.8833 | 1733.8536
DEER-SFAM-CZ09-V2-eSH-13-LH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-LH | 13.3305 | 2.7724 | 1543.4485 | 793.1651 | 3.3462 | 2336.6136 | 1657.6793
DEER-SFAM-CZ09-V2-eSH-13-LL-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-LL | 13.6827 | 2.9189 | 1532.4363 | 699.1155 | 3.3462 | 2231.5518 | 1601.5221
DEER-SFAM-CZ09-V2-eSH-13-LM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-LM | 12.7552 | 2.9257 | 1605.8922 | 625.3631 | 3.3462 | 2231.2553 | 1685.3231
DEER-SFAM-CZ09-V2-eSH-13-MH-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-MH | 13.3367 | 3.0029 | 1550.1199 | 785.2281 | 3.5578 | 2335.348 | 1626.8359
DEER-SFAM-CZ09-V2-eSH-13-ML-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-ML | 12.6047 | 3.0954 | 1622.1831 | 721.0825 | 3.3462 | 2343.2657 | 1700.7551
DEER-SFAM-CZ09-V2-eSH-13-MM-s1 | 13 | CZ09 | V2 | CZ09-V2-eSH-13 | CZ09-V2-eSH-13-MM | 13.1546 | 3.0866 | 1591.7672 | 723.798 | 3.3462 | 2315.5652 | 1653.131
DEER-SFAM-CZ09-V2-eSH-14-HH-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-HH | 12.6924 | 2.8968 | 1595.5196 | 703.0016 | 3.3462 | 2298.5213 | 1653.2604
DEER-SFAM-CZ09-V2-eSH-14-HL-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-HL | 12.9419 | 2.8916 | 1560.7494 | 681.8005 | 3.3462 | 2242.5498 | 1630.2704
DEER-SFAM-CZ09-V2-eSH-14-HM-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-HM | 12.8908 | 2.7767 | 1559.3988 | 679.8163 | 3.3462 | 2239.2151 | 1608.6276
DEER-SFAM-CZ09-V2-eSH-14-MH-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-MH | 14.1616 | 2.6109 | 1445.6158 | 717.6469 | 3.3462 | 2163.2626 | 1520.6752
DEER-SFAM-CZ09-V2-eSH-14-ML-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-ML | 14.3314 | 2.8094 | 1435.5471 | 738.274 | 3.3462 | 2173.8211 | 1529.9261
DEER-SFAM-CZ09-V2-eSH-14-MM-s1 | 14 | CZ09 | V2 | CZ09-V2-eSH-14 | CZ09-V2-eSH-14-MM | 13.9302 | 2.7641 | 1458.4792 | 664.8632 | 3.3462 | 2123.3424 | 1524.0248
DEER-SFAM-CZ09-V2-eSH-15-HH-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-HH | 13.7974 | 2.5476 | 1439.5299 | 793.4951 | 3.3462 | 2233.025 | 1493.3782
DEER-SFAM-CZ09-V2-eSH-15-HL-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-HL | 14.0627 | 2.7964 | 1449.0178 | 591.5679 | 3.3462 | 2040.5857 | 1502.2881
DEER-SFAM-CZ09-V2-eSH-15-HM-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-HM | 14.8298 | 2.7687 | 1383.2537 | 617.1519 | 3.5578 | 2000.4056 | 1436.6267
DEER-SFAM-CZ09-V2-eSH-15-MH-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-MH | 14.984 | 2.6621 | 1370.7181 | 708.4731 | 3.3462 | 2079.1911 | 1422.3343
DEER-SFAM-CZ09-V2-eSH-15-ML-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-ML | 15.2518 | 2.6762 | 1345.7618 | 650.9267 | 3.3462 | 1996.6885 | 1398.9864
DEER-SFAM-CZ09-V2-eSH-15-MM-s1 | 15 | CZ09 | V2 | CZ09-V2-eSH-15 | CZ09-V2-eSH-15-MM | 15.0767 | 2.6534 | 1372.7068 | 694.0628 | 3.3462 | 2066.7696 | 1428.9706
DEER-SFAM-CZ09-V2-eSH-16-CH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-CH | 14.7198 | 2.8453 | 1635.1953 | 688.1741 | 3.3462 | 2323.3695 | 1678.5524
DEER-SFAM-CZ09-V2-eSH-16-CL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-CL | 14.8271 | 2.891 | 1652.877 | 639.0966 | 3.3462 | 2291.9736 | 1698.3494
DEER-SFAM-CZ09-V2-eSH-16-LH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-LH | 14.2323 | 2.5786 | 1495.2416 | 768.3129 | 3.3462 | 2263.5545 | 1549.0434
DEER-SFAM-CZ09-V2-eSH-16-LL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-LL | 13.9574 | 2.8226 | 1557.171 | 683.8258 | 3.3462 | 2240.9968 | 1600.3138
DEER-SFAM-CZ09-V2-eSH-16-LM-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-LM | 13.8177 | 2.6695 | 1550.2313 | 763.6447 | 3.3462 | 2313.8759 | 1610.4035
DEER-SFAM-CZ09-V2-eSH-16-TH-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-TH | 15.0771 | 2.7451 | 1571.1855 | 867.1533 | 3.3462 | 2438.3388 | 1611.981
DEER-SFAM-CZ09-V2-eSH-16-TL-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-TL | 14.295 | 3.117 | 1751.8254 | 845.6 | 3.3462 | 2597.4254 | 1787.7796
DEER-SFAM-CZ09-V2-eSH-16-TM-s2 | 16 | CZ09 | V2 | CZ09-V2-eSH-16 | CZ09-V2-eSH-16-TM | 14.4574 | 3.0604 | 1732.261 | 862.7067 | 3.3462 | 2594.9677 | 1769.0717
DEER-SFAM-CZ09-V2-eSH-17-CM-s2 | 17 | CZ09 | V2 | CZ09-V2-eSH-17 | CZ09-V2-eSH-17-CM | 15.6643 | 2.7469 | 1562.6243 | 710.8453 | 3.3462 | 2273.4696 | 1614.6333
DEER-SFAM-CZ09-V2-eSH-17-LM-s2 | 17 | CZ09 | V2 | CZ09-V2-eSH-17 | CZ09-V2-eSH-17-LM | 14.698 | 2.6976 | 1526.7147 | 666.3936 | 3.3462 | 2193.1083 | 1551.0022
DEER-SFAM-CZ09-V2-eSH-17-TH-s2 | 17 | CZ09 | V2 | CZ09-V2-eSH-17 | CZ09-V2-eSH-17-TH | 15.9691 | 2.5662 | 1480.9886 | 861.9793 | 3.3462 | 2342.9679 | 1524.4372
DEER-SFAM-CZ09-V2-eSH-17-TL-s2 | 17 | CZ09 | V2 | CZ09-V2-eSH-17 | CZ09-V2-eSH-17-TL | 15.8664 | 2.6348 | 1493.5325 | 848.9197 | 3.3462 | 2342.4522 | 1536.5371
DEER-SFAM-CZ09-V2-eSH-18-LH-s2 | 18 | CZ09 | V2 | CZ09-V2-eSH-18 | CZ09-V2-eSH-18-LH | 15.6406 | 2.4945 | 1394.906 | 743.2134 | 3.3462 | 2138.1193 | 1433.5127
DEER-SFAM-CZ09-V2-eSH-18-LL-s2 | 18 | CZ09 | V2 | CZ09-V2-eSH-18 | CZ09-V2-eSH-18-LL | 14.9999 | 2.5371 | 1437.7349 | 677.9943 | 3.3462 | 2115.7292 | 1474.8925
DEER-SFAM-CZ09-V2-eSH-18-LM-s2 | 18 | CZ09 | V2 | CZ09-V2-eSH-18 | CZ09-V2-eSH-18-LM | 15.5442 | 2.5954 | 1415.8316 | 780.2461 | 3.3462 | 2196.0777 | 1459.7978
DEER-SFAM-CZ09-V2-eSH-18-TM-s2 | 18 | CZ09 | V2 | CZ09-V2-eSH-18 | CZ09-V2-eSH-18-TM | 16.9454 | 2.5986 | 1425.0601 | 841.0413 | 3.3462 | 2266.1014 | 1489.1485
DEER-SFAM-CZ09-V3-eSA-10-HH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-HH | 9.841 | 4.0239 | 2553.2685 | 0 | 3.6 | 2553.2685 | 2575.6104
DEER-SFAM-CZ09-V3-eSA-10-HL-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-HL | 9.2449 | 4.7493 | 2702.8055 | 0 | 4.1 | 2702.8055 | 2725.1969
DEER-SFAM-CZ09-V3-eSA-10-HM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-HM | 9.2644 | 4.2364 | 2647.4796 | 0 | 4.1 | 2647.4796 | 2669.8672
DEER-SFAM-CZ09-V3-eSA-10-LH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-LH | 10.388 | 3.887 | 2450.2087 | 0 | 3.6 | 2450.2087 | 2472.5949
DEER-SFAM-CZ09-V3-eSA-10-LL-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-LL | 9.4481 | 4.5596 | 2646.66 | 0 | 4.1 | 2646.66 | 2669.0555
DEER-SFAM-CZ09-V3-eSA-10-LM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-LM | 10.2769 | 3.9376 | 2466.2434 | 0 | 3.6 | 2466.2434 | 2488.6306
DEER-SFAM-CZ09-V3-eSA-10-MH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-MH | 10.2723 | 3.7901 | 2465.4093 | 0 | 3.6 | 2465.4093 | 2487.7879
DEER-SFAM-CZ09-V3-eSA-10-ML-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-ML | 9.3927 | 4.2554 | 2685.2427 | 0 | 3.6 | 2685.2427 | 2707.6073
DEER-SFAM-CZ09-V3-eSA-10-MM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSA-10 | CZ09-V3-eSA-10-MM | 10.1698 | 3.9413 | 2447.1734 | 0 | 3.6 | 2447.1734 | 2469.5405
DEER-SFAM-CZ09-V3-eSA-13-HH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-HH | 12.0927 | 3.6172 | 2040.6451 | 0 | 4.1 | 2040.6451 | 2060.8292
DEER-SFAM-CZ09-V3-eSA-13-HL-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-HL | 12.5073 | 3.732 | 1976.6912 | 0 | 4.1 | 1976.6912 | 1994.3562
DEER-SFAM-CZ09-V3-eSA-13-HM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-HM | 12.244 | 3.6684 | 2026.6987 | 0 | 4.1 | 2026.6987 | 2046.8754
DEER-SFAM-CZ09-V3-eSA-13-LH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-LH | 13.0141 | 3.2861 | 1910.5797 | 0 | 4.1 | 1910.5797 | 1932.9767
DEER-SFAM-CZ09-V3-eSA-13-LL-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-LL | 12.6782 | 3.2994 | 1981.8292 | 0 | 3.6 | 1981.8292 | 2004.1465
DEER-SFAM-CZ09-V3-eSA-13-LM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-LM | 12.7159 | 3.1617 | 1966.8847 | 0 | 3.6 | 1966.8847 | 1989.2336
DEER-SFAM-CZ09-V3-eSA-13-MH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-MH | 13.0912 | 3.3419 | 1940.7898 | 0 | 4.1 | 1940.7898 | 1963.1774
DEER-SFAM-CZ09-V3-eSA-13-ML-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-ML | 12.3442 | 3.3938 | 1964.4116 | 0 | 3.6 | 1964.4116 | 1986.7013
DEER-SFAM-CZ09-V3-eSA-13-MM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSA-13 | CZ09-V3-eSA-13-MM | 13.1795 | 3.5187 | 1907.8255 | 0 | 4.1 | 1907.8255 | 1930.2101
DEER-SFAM-CZ09-V3-eSA-14-HH-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-HH | 12.5748 | 3.241 | 1924.4302 | 0 | 3.6 | 1924.4302 | 1943.1699
DEER-SFAM-CZ09-V3-eSA-14-HL-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-HL | 13.5255 | 3.4349 | 1855.672 | 0 | 4.1 | 1855.672 | 1869.4695
DEER-SFAM-CZ09-V3-eSA-14-HM-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-HM | 13.2833 | 3.4834 | 1883.2273 | 0 | 4.1 | 1883.2273 | 1904.3967
DEER-SFAM-CZ09-V3-eSA-14-MH-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-MH | 13.5614 | 2.9408 | 1869.5008 | 0 | 3.6 | 1869.5008 | 1884.1908
DEER-SFAM-CZ09-V3-eSA-14-ML-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-ML | 13.2294 | 3.3942 | 1850.7435 | 0 | 4.1 | 1850.7435 | 1874.2359
DEER-SFAM-CZ09-V3-eSA-14-MM-s1 | 14 | CZ09 | V3 | CZ09-V3-eSA-14 | CZ09-V3-eSA-14-MM | 13.6004 | 2.9591 | 1831.6696 | 0 | 3.6 | 1831.6696 | 1847.7763
DEER-SFAM-CZ09-V3-eSA-15-HH-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-HH | 13.9846 | 3.1178 | 1764.8512 | 0 | 4.1 | 1764.8512 | 1780.4941
DEER-SFAM-CZ09-V3-eSA-15-HL-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-HL | 14.5204 | 3.1344 | 1716.6684 | 0 | 4.1 | 1716.6684 | 1736.1629
DEER-SFAM-CZ09-V3-eSA-15-HM-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-HM | 13.9534 | 3.0125 | 1757.2272 | 0 | 4.1 | 1757.2272 | 1772.9274
DEER-SFAM-CZ09-V3-eSA-15-MH-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-MH | 14.1698 | 2.9872 | 1733.618 | 0 | 3.6 | 1733.618 | 1745.2601
DEER-SFAM-CZ09-V3-eSA-15-ML-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-ML | 14.6161 | 2.9536 | 1725.4418 | 0 | 3.6 | 1725.4418 | 1741.0894
DEER-SFAM-CZ09-V3-eSA-15-MM-s1 | 15 | CZ09 | V3 | CZ09-V3-eSA-15 | CZ09-V3-eSA-15-MM | 14.3732 | 3.176 | 1721.5476 | 0 | 4.1 | 1721.5476 | 1735.8402
DEER-SFAM-CZ09-V3-eSA-16-CH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-CH | 14.5077 | 3.4127 | 1965.8968 | 0 | 4.1 | 1965.8968 | 1974.8528
DEER-SFAM-CZ09-V3-eSA-16-CL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-CL | 14.9186 | 3.3024 | 1862.3364 | 0 | 4.1 | 1862.3364 | 1873.657
DEER-SFAM-CZ09-V3-eSA-16-CM-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-CM | 14.5515 | 3.406 | 1924.692 | 0 | 4.1 | 1924.692 | 1936.6214
DEER-SFAM-CZ09-V3-eSA-16-LH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-LH | 14.6681 | 2.8388 | 1741.227 | 0 | 3.6 | 1741.227 | 1756.6206
DEER-SFAM-CZ09-V3-eSA-16-LL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-LL | 14.0841 | 3.1529 | 1838.6927 | 0 | 3.6 | 1838.6927 | 1848.833
DEER-SFAM-CZ09-V3-eSA-16-LM-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-LM | 14.1412 | 3.0328 | 1829.7693 | 0 | 3.6 | 1829.7693 | 1838.965
DEER-SFAM-CZ09-V3-eSA-16-NM-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-NM | 15.7073 | 2.7395 | 1666.7891 | 0 | 3.6 | 1666.7891 | 1675.8042
DEER-SFAM-CZ09-V3-eSA-16-TH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-TH | 14.3629 | 3.301 | 1977.7179 | 0 | 3.6 | 1977.7179 | 1983.4754
DEER-SFAM-CZ09-V3-eSA-16-TL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSA-16 | CZ09-V3-eSA-16-TL | 15.226 | 3.1649 | 1847.6672 | 0 | 4.1 | 1847.6672 | 1853.9218
DEER-SFAM-CZ09-V3-eSA-17-CH-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-CH | 15.4363 | 3.2493 | 1819.9785 | 0 | 4.1 | 1819.9785 | 1831.2941
DEER-SFAM-CZ09-V3-eSA-17-CL-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-CL | 15.4259 | 3.2958 | 1816.0416 | 0 | 4.1 | 1816.0416 | 1827.3548
DEER-SFAM-CZ09-V3-eSA-17-CM-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-CM | 15.5187 | 3.2848 | 1831.9707 | 0 | 4.1 | 1831.9707 | 1840.9002
DEER-SFAM-CZ09-V3-eSA-17-LH-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-LH | 15.1332 | 2.7697 | 1686.829 | 0 | 3.6 | 1686.829 | 1698.8931
DEER-SFAM-CZ09-V3-eSA-17-LL-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-LL | 14.8382 | 3.0066 | 1758.5415 | 0 | 3.6 | 1758.5415 | 1765.1441
DEER-SFAM-CZ09-V3-eSA-17-LM-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-LM | 14.7063 | 2.9105 | 1760.9573 | 0 | 3.6 | 1760.9573 | 1766.6519
DEER-SFAM-CZ09-V3-eSA-17-TH-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-TH | 16.2145 | 2.7565 | 1701.0269 | 0 | 3.6 | 1701.0269 | 1710.2451
DEER-SFAM-CZ09-V3-eSA-17-TL-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-TL | 16.8106 | 2.8808 | 1612.5003 | 0 | 4.1 | 1612.5003 | 1626.862
DEER-SFAM-CZ09-V3-eSA-17-TM-s2 | 17 | CZ09 | V3 | CZ09-V3-eSA-17 | CZ09-V3-eSA-17-TM | 16.3157 | 3.2379 | 1833.4902 | 0 | 4.1 | 1833.4902 | 1838.3518
DEER-SFAM-CZ09-V3-eSA-18-LH-s2 | 18 | CZ09 | V3 | CZ09-V3-eSA-18 | CZ09-V3-eSA-18-LH | 15.7448 | 2.788 | 1647.1907 | 0 | 3.6 | 1647.1907 | 1655.1203
DEER-SFAM-CZ09-V3-eSA-18-LL-s2 | 18 | CZ09 | V3 | CZ09-V3-eSA-18 | CZ09-V3-eSA-18-LL | 16.0027 | 2.6771 | 1603.939 | 0 | 3.6 | 1603.939 | 1614.2848
DEER-SFAM-CZ09-V3-eSA-18-TH-s2 | 18 | CZ09 | V3 | CZ09-V3-eSA-18 | CZ09-V3-eSA-18-TH | 16.7914 | 2.7803 | 1669.448 | 0 | 4.1 | 1669.448 | 1675.7322
DEER-SFAM-CZ09-V3-eSA-18-TL-s2 | 18 | CZ09 | V3 | CZ09-V3-eSA-18 | CZ09-V3-eSA-18-TL | 16.2935 | 3.2282 | 1761.6355 | 0 | 4.1 | 1761.6355 | 1768.5127
DEER-SFAM-CZ09-V3-eSA-18-TM-s2 | 18 | CZ09 | V3 | CZ09-V3-eSA-18 | CZ09-V3-eSA-18-TM | 16.2997 | 2.6584 | 1683.826 | 0 | 3.6 | 1683.826 | 1690.2293
DEER-SFAM-CZ09-V3-eSH-10-HH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-HH | 9.8256 | 4.3397 | 2542 | 440.9654 | 4.1 | 2982.9654 | 2586.3654
DEER-SFAM-CZ09-V3-eSH-10-HL-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-HL | 9.5769 | 4.5378 | 2617.7237 | 441.9945 | 4.1 | 3059.7182 | 2661.9182
DEER-SFAM-CZ09-V3-eSH-10-HM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-HM | 10.1423 | 4.0861 | 2519.9094 | 429.8405 | 3.6 | 2949.7499 | 2561.9499
DEER-SFAM-CZ09-V3-eSH-10-LH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-LH | 10.383 | 3.7567 | 2439.9657 | 464.2734 | 3.6 | 2904.2391 | 2485.7391
DEER-SFAM-CZ09-V3-eSH-10-LL-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-LL | 9.9271 | 4.3048 | 2551.6639 | 434.0533 | 4.1 | 2985.7172 | 2599.1172
DEER-SFAM-CZ09-V3-eSH-10-LM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-LM | 10.1005 | 4.2429 | 2509.6952 | 436.8342 | 4.1 | 2946.5294 | 2553.3294
DEER-SFAM-CZ09-V3-eSH-10-MH-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-MH | 10.3926 | 3.8952 | 2450.2792 | 452.3596 | 3.6 | 2902.6388 | 2498.8388
DEER-SFAM-CZ09-V3-eSH-10-ML-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-ML | 9.8985 | 4.5902 | 2571.671 | 405.6663 | 4.1 | 2977.3373 | 2615.3373
DEER-SFAM-CZ09-V3-eSH-10-MM-s1 | 10 | CZ09 | V3 | CZ09-V3-eSH-10 | CZ09-V3-eSH-10-MM | 10.1233 | 4.035 | 2523.8871 | 438.5641 | 3.6 | 2962.4512 | 2565.2512
DEER-SFAM-CZ09-V3-eSH-13-HH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-HH | 11.871 | 3.5966 | 2090.9237 | 423.4795 | 4.1 | 2514.4032 | 2131.4032
DEER-SFAM-CZ09-V3-eSH-13-HL-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-HL | 12.5913 | 3.7753 | 1986.4385 | 358.3443 | 4.1 | 2344.7828 | 2026.6828
DEER-SFAM-CZ09-V3-eSH-13-HM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-HM | 12.1284 | 3.5882 | 2053.1292 | 376.0884 | 4.1 | 2429.2176 | 2089.6176
DEER-SFAM-CZ09-V3-eSH-13-LH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-LH | 13.0554 | 3.0629 | 1913.3194 | 424.4887 | 3.6 | 2337.8081 | 1973.6081
DEER-SFAM-CZ09-V3-eSH-13-LL-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-LL | 13.3737 | 3.4443 | 1897.0287 | 378.9846 | 4.1 | 2276.0133 | 1933.9133
DEER-SFAM-CZ09-V3-eSH-13-LM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-LM | 12.5123 | 3.228 | 1989.2849 | 336.1404 | 3.6 | 2325.4253 | 2031.6253
DEER-SFAM-CZ09-V3-eSH-13-MH-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-MH | 12.9869 | 3.4061 | 1930.2305 | 426.5897 | 4.1 | 2356.8202 | 1971.0202
DEER-SFAM-CZ09-V3-eSH-13-ML-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-ML | 12.3968 | 3.4244 | 2010.5209 | 384.1345 | 3.6 | 2394.6554 | 2052.2554
DEER-SFAM-CZ09-V3-eSH-13-MM-s1 | 13 | CZ09 | V3 | CZ09-V3-eSH-13 | CZ09-V3-eSH-13-MM | 12.8397 | 3.6408 | 1975.4447 | 392.9339 | 4.1 | 2368.3786 | 2008.2786
DEER-SFAM-CZ09-V3-eSH-14-HH-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-HH | 12.5751 | 3.4146 | 1973.0772 | 383.9382 | 4.1 | 2357.0154 | 2003.9154
DEER-SFAM-CZ09-V3-eSH-14-HL-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-HL | 12.882 | 3.3894 | 1922.9214 | 368.71 | 4.1 | 2291.6314 | 1959.9314
DEER-SFAM-CZ09-V3-eSH-14-HM-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-HM | 12.7886 | 3.2632 | 1929.184 | 369.9908 | 4.1 | 2299.1748 | 1955.4748
DEER-SFAM-CZ09-V3-eSH-14-MH-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-MH | 13.8929 | 2.8808 | 1791.122 | 385.7206 | 3.6 | 2176.8426 | 1830.9426
DEER-SFAM-CZ09-V3-eSH-14-ML-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-ML | 13.8239 | 3.3334 | 1799.7783 | 391.9738 | 4.1 | 2191.7521 | 1849.5521
DEER-SFAM-CZ09-V3-eSH-14-MM-s1 | 14 | CZ09 | V3 | CZ09-V3-eSH-14 | CZ09-V3-eSH-14-MM | 13.6334 | 3.0574 | 1812.0006 | 356.6087 | 3.6 | 2168.6093 | 1846.8093
DEER-SFAM-CZ09-V3-eSH-15-HH-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-HH | 13.7207 | 2.9909 | 1783.4665 | 428.708 | 4.1 | 2212.1745 | 1811.9745
DEER-SFAM-CZ09-V3-eSH-15-HL-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-HL | 13.9666 | 3.2859 | 1787.1522 | 321.8557 | 4.1 | 2109.0079 | 1815.6079
DEER-SFAM-CZ09-V3-eSH-15-HM-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-HM | 14.4573 | 3.1305 | 1722.7493 | 337.5494 | 4.1 | 2060.2987 | 1751.0987
DEER-SFAM-CZ09-V3-eSH-15-MH-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-MH | 14.4634 | 3.1681 | 1725.7491 | 378.4727 | 4.1 | 2104.2218 | 1753.0218
DEER-SFAM-CZ09-V3-eSH-15-ML-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-ML | 14.7713 | 3.1589 | 1684.2768 | 346.6634 | 4.1 | 2030.9402 | 1712.4402
DEER-SFAM-CZ09-V3-eSH-15-MM-s1 | 15 | CZ09 | V3 | CZ09-V3-eSH-15 | CZ09-V3-eSH-15-MM | 14.6796 | 3.099 | 1711.5779 | 375.5861 | 4.1 | 2087.164 | 1741.564
DEER-SFAM-CZ09-V3-eSH-16-CH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-CH | 14.7826 | 3.2697 | 1910.9606 | 351.0401 | 4.1 | 2262.0007 | 1933.5007
DEER-SFAM-CZ09-V3-eSH-16-CL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-CL | 14.8871 | 3.4285 | 1925.0906 | 325.7977 | 4.1 | 2250.8883 | 1948.8883
DEER-SFAM-CZ09-V3-eSH-16-LH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-LH | 14.4817 | 2.8067 | 1754.3468 | 402.8774 | 3.6 | 2157.2242 | 1782.6242
DEER-SFAM-CZ09-V3-eSH-16-LL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-LL | 14.1004 | 3.0535 | 1827.7308 | 354.639 | 3.6 | 2182.3698 | 1850.4698
DEER-SFAM-CZ09-V3-eSH-16-LM-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-LM | 14.0345 | 2.9011 | 1820.1697 | 399.2075 | 3.6 | 2219.3772 | 1851.7772
DEER-SFAM-CZ09-V3-eSH-16-TH-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-TH | 15.3433 | 3.1968 | 1814.7267 | 441.4414 | 4.1 | 2256.1681 | 1835.3681
DEER-SFAM-CZ09-V3-eSH-16-TL-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-TL | 14.3922 | 3.388 | 1981.39 | 414.7784 | 3.6 | 2396.1684 | 1999.3684
DEER-SFAM-CZ09-V3-eSH-16-TM-s2 | 16 | CZ09 | V3 | CZ09-V3-eSH-16 | CZ09-V3-eSH-16-TM | 14.6479 | 3.5959 | 1977.802 | 423.8327 | 4.1 | 2401.6347 | 1995.8347
DEER-SFAM-CZ09-V3-eSH-17-CM-s2 | 17 | CZ09 | V3 | CZ09-V3-eSH-17 | CZ09-V3-eSH-17-CM | 15.7211 | 3.2577 | 1820.8098 | 353.0441 | 4.1 | 2173.8539 | 1847.4539
DEER-SFAM-CZ09-V3-eSH-17-LM-s2 | 17 | CZ09 | V3 | CZ09-V3-eSH-17 | CZ09-V3-eSH-17-LM | 14.852 | 2.904 | 1774.4006 | 346.1005 | 3.6 | 2120.5011 | 1787.2011
DEER-SFAM-CZ09-V3-eSH-17-TH-s2 | 17 | CZ09 | V3 | CZ09-V3-eSH-17 | CZ09-V3-eSH-17-TH | 16.1399 | 3.0129 | 1722.1196 | 434.4761 | 4.1 | 2156.5957 | 1743.7957
DEER-SFAM-CZ09-V3-eSH-17-TL-s2 | 17 | CZ09 | V3 | CZ09-V3-eSH-17 | CZ09-V3-eSH-17-TL | 16.0898 | 3.0785 | 1731.489 | 425.6295 | 4.1 | 2157.1185 | 1753.0185
DEER-SFAM-CZ09-V3-eSH-18-LH-s2 | 18 | CZ09 | V3 | CZ09-V3-eSH-18 | CZ09-V3-eSH-18-LH | 15.7852 | 2.6964 | 1632.9022 | 379.285 | 3.6 | 2012.1872 | 1653.0872
DEER-SFAM-CZ09-V3-eSH-18-LL-s2 | 18 | CZ09 | V3 | CZ09-V3-eSH-18 | CZ09-V3-eSH-18-LL | 15.104 | 2.7585 | 1696.3737 | 350.6406 | 3.6 | 2047.0143 | 1715.9143
DEER-SFAM-CZ09-V3-eSH-18-LM-s2 | 18 | CZ09 | V3 | CZ09-V3-eSH-18 | CZ09-V3-eSH-18-LM | 15.7691 | 2.7591 | 1646.6527 | 395.8112 | 3.6 | 2042.4639 | 1669.5639
DEER-SFAM-CZ09-V3-eSH-18-TM-s2 | 18 | CZ09 | V3 | CZ09-V3-eSH-18 | CZ09-V3-eSH-18-TM | 17.0495 | 2.838 | 1635.1252 | 413.6432 | 3.6 | 2048.7684 | 1666.6684
DEER-SFAM-CZ09-V4-eSA-10-HH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-HH | 9.7795 | 4.4629 | 2709.8769 | 0 | 4.1 | 2709.8769 | 2726.0571
DEER-SFAM-CZ09-V4-eSA-10-HL-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-HL | 9.2517 | 5.1118 | 2847.8725 | 0 | 4.5 | 2847.8725 | 2864.0809
DEER-SFAM-CZ09-V4-eSA-10-HM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-HM | 9.2642 | 4.5883 | 2790.6782 | 0 | 4.5 | 2790.6782 | 2806.884
DEER-SFAM-CZ09-V4-eSA-10-LH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-LH | 10.3316 | 4.315 | 2590.3906 | 0 | 4.1 | 2590.3906 | 2606.6028
DEER-SFAM-CZ09-V4-eSA-10-LL-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-LL | 9.4485 | 4.8991 | 2789.4987 | 0 | 4.5 | 2789.4987 | 2805.7103
DEER-SFAM-CZ09-V4-eSA-10-LM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-LM | 10.2271 | 4.3676 | 2606.0768 | 0 | 4.1 | 2606.0768 | 2622.29
DEER-SFAM-CZ09-V4-eSA-10-MH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-MH | 10.1848 | 4.2129 | 2615.0749 | 0 | 4.1 | 2615.0749 | 2631.2815
DEER-SFAM-CZ09-V4-eSA-10-ML-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-ML | 9.3272 | 5.015 | 2849.993 | 0 | 4.5 | 2849.993 | 2866.2015
DEER-SFAM-CZ09-V4-eSA-10-MM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSA-10 | CZ09-V4-eSA-10-MM | 10.1292 | 4.3658 | 2580.9254 | 0 | 4.1 | 2580.9254 | 2597.1239
DEER-SFAM-CZ09-V4-eSA-13-HH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-HH | 12.0551 | 3.892 | 2155.1132 | 0 | 4.5 | 2155.1132 | 2169.724
DEER-SFAM-CZ09-V4-eSA-13-HL-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-HL | 12.5232 | 3.9892 | 2076.7701 | 0 | 4.5 | 2076.7701 | 2089.5569
DEER-SFAM-CZ09-V4-eSA-13-HM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-HM | 12.2412 | 3.9379 | 2133.5288 | 0 | 4.5 | 2133.5288 | 2148.1339
DEER-SFAM-CZ09-V4-eSA-13-LH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-LH | 12.9835 | 3.529 | 2015.6331 | 0 | 4.5 | 2015.6331 | 2031.8458
DEER-SFAM-CZ09-V4-eSA-13-LL-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-LL | 12.6455 | 3.6524 | 2088.7041 | 0 | 4.1 | 2088.7041 | 2104.8666
DEER-SFAM-CZ09-V4-eSA-13-LM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-LM | 12.6476 | 3.5084 | 2078.0782 | 0 | 4.1 | 2078.0782 | 2094.2634
DEER-SFAM-CZ09-V4-eSA-13-MH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-MH | 13.0814 | 3.59 | 2045.8663 | 0 | 4.5 | 2045.8663 | 2062.0721
DEER-SFAM-CZ09-V4-eSA-13-ML-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-ML | 12.2617 | 3.9095 | 2080.5914 | 0 | 4.5 | 2080.5914 | 2096.7463
DEER-SFAM-CZ09-V4-eSA-13-MM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSA-13 | CZ09-V4-eSA-13-MM | 13.1763 | 3.7678 | 2009.8308 | 0 | 4.5 | 2009.8308 | 2026.0339
DEER-SFAM-CZ09-V4-eSA-14-HH-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-HH | 12.5158 | 3.5997 | 2034.2378 | 0 | 4.1 | 2034.2378 | 2047.8087
DEER-SFAM-CZ09-V4-eSA-14-HL-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-HL | 13.5309 | 3.6991 | 1952.1209 | 0 | 4.5 | 1952.1209 | 1962.1086
DEER-SFAM-CZ09-V4-eSA-14-HM-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-HM | 13.3002 | 3.7415 | 1979.092 | 0 | 4.5 | 1979.092 | 1994.4162
DEER-SFAM-CZ09-V4-eSA-14-MH-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-MH | 13.4732 | 3.2699 | 1978.9529 | 0 | 4.1 | 1978.9529 | 1989.5912
DEER-SFAM-CZ09-V4-eSA-14-ML-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-ML | 13.2377 | 3.6384 | 1946.5782 | 0 | 4.5 | 1946.5782 | 1963.5837
DEER-SFAM-CZ09-V4-eSA-14-MM-s1 | 14 | CZ09 | V4 | CZ09-V4-eSA-14 | CZ09-V4-eSA-14-MM | 13.5181 | 3.2841 | 1935.9211 | 0 | 4.1 | 1935.9211 | 1947.5855
DEER-SFAM-CZ09-V4-eSA-15-HH-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-HH | 13.9593 | 3.3515 | 1860.1796 | 0 | 4.5 | 1860.1796 | 1871.5027
DEER-SFAM-CZ09-V4-eSA-15-HL-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-HL | 14.5168 | 3.3641 | 1806.5877 | 0 | 4.5 | 1806.5877 | 1820.6985
DEER-SFAM-CZ09-V4-eSA-15-HM-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-HM | 13.92 | 3.2388 | 1852.3385 | 0 | 4.5 | 1852.3385 | 1863.7031
DEER-SFAM-CZ09-V4-eSA-15-MH-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-MH | 13.984 | 3.4534 | 1847.766 | 0 | 4.5 | 1847.766 | 1856.2033
DEER-SFAM-CZ09-V4-eSA-15-ML-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-ML | 14.5159 | 3.397 | 1827.576 | 0 | 4.5 | 1827.576 | 1838.9189
DEER-SFAM-CZ09-V4-eSA-15-MM-s1 | 15 | CZ09 | V4 | CZ09-V4-eSA-15 | CZ09-V4-eSA-15-MM | 14.3877 | 3.3947 | 1809.2076 | 0 | 4.5 | 1809.2076 | 1819.5535
DEER-SFAM-CZ09-V4-eSA-16-CH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-CH | 14.5652 | 3.6719 | 2070.4969 | 0 | 4.5 | 2070.4969 | 2076.986
DEER-SFAM-CZ09-V4-eSA-16-CL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-CL | 14.9681 | 3.5312 | 1962.8728 | 0 | 4.5 | 1962.8728 | 1971.075
DEER-SFAM-CZ09-V4-eSA-16-CM-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-CM | 14.5998 | 3.6564 | 2029.0922 | 0 | 4.5 | 2029.0922 | 2037.7365
DEER-SFAM-CZ09-V4-eSA-16-LH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-LH | 14.4664 | 3.2717 | 1867.3838 | 0 | 4.5 | 1867.3838 | 1878.5476
DEER-SFAM-CZ09-V4-eSA-16-LL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-LL | 14.0499 | 3.4619 | 1942.6042 | 0 | 4.1 | 1942.6042 | 1949.9497
DEER-SFAM-CZ09-V4-eSA-16-LM-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-LM | 14.1046 | 3.3386 | 1932.7712 | 0 | 4.1 | 1932.7712 | 1939.4328
DEER-SFAM-CZ09-V4-eSA-16-NM-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-NM | 15.7441 | 3.0272 | 1754.4272 | 0 | 4.1 | 1754.4272 | 1760.958
DEER-SFAM-CZ09-V4-eSA-16-TH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-TH | 14.3369 | 3.7966 | 2125.0799 | 0 | 4.5 | 2125.0799 | 2129.2572
DEER-SFAM-CZ09-V4-eSA-16-TL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSA-16 | CZ09-V4-eSA-16-TL | 15.2649 | 3.4111 | 1947.2077 | 0 | 4.5 | 1947.2077 | 1951.7383
DEER-SFAM-CZ09-V4-eSA-17-CH-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-CH | 15.4958 | 3.4966 | 1916.5203 | 0 | 4.5 | 1916.5203 | 1924.7186
DEER-SFAM-CZ09-V4-eSA-17-CL-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-CL | 15.4947 | 3.5384 | 1911.5455 | 0 | 4.5 | 1911.5455 | 1919.7423
DEER-SFAM-CZ09-V4-eSA-17-CM-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-CM | 15.5833 | 3.5318 | 1929.8489 | 0 | 4.5 | 1929.8489 | 1936.3188
DEER-SFAM-CZ09-V4-eSA-17-LH-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-LH | 15.0763 | 3.0534 | 1783.4473 | 0 | 4.1 | 1783.4473 | 1792.188
DEER-SFAM-CZ09-V4-eSA-17-LL-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-LL | 14.8184 | 3.3087 | 1856.5109 | 0 | 4.1 | 1856.5109 | 1861.2951
DEER-SFAM-CZ09-V4-eSA-17-LM-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-LM | 14.6793 | 3.2005 | 1860.3517 | 0 | 4.1 | 1860.3517 | 1864.477
DEER-SFAM-CZ09-V4-eSA-17-TH-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-TH | 16.0773 | 3.2089 | 1834.2824 | 0 | 4.5 | 1834.2824 | 1840.9689
DEER-SFAM-CZ09-V4-eSA-17-TL-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-TL | 16.9255 | 3.1171 | 1697.3097 | 0 | 4.5 | 1697.3097 | 1707.7172
DEER-SFAM-CZ09-V4-eSA-17-TM-s2 | 17 | CZ09 | V4 | CZ09-V4-eSA-17 | CZ09-V4-eSA-17-TM | 16.3372 | 3.4816 | 1936.0985 | 0 | 4.5 | 1936.0985 | 1939.6218
DEER-SFAM-CZ09-V4-eSA-18-LH-s2 | 18 | CZ09 | V4 | CZ09-V4-eSA-18 | CZ09-V4-eSA-18-LH | 15.6967 | 3.0667 | 1742.0138 | 0 | 4.1 | 1742.0138 | 1747.7581
DEER-SFAM-CZ09-V4-eSA-18-LL-s2 | 18 | CZ09 | V4 | CZ09-V4-eSA-18 | CZ09-V4-eSA-18-LL | 16.0062 | 2.9664 | 1690.6597 | 0 | 4.1 | 1690.6597 | 1698.1546
DEER-SFAM-CZ09-V4-eSA-18-TH-s2 | 18 | CZ09 | V4 | CZ09-V4-eSA-18 | CZ09-V4-eSA-18-TH | 16.7535 | 2.9849 | 1766.2153 | 0 | 4.5 | 1766.2153 | 1770.7667
DEER-SFAM-CZ09-V4-eSA-18-TL-s2 | 18 | CZ09 | V4 | CZ09-V4-eSA-18 | CZ09-V4-eSA-18-TL | 16.3242 | 3.4726 | 1857.3637 | 0 | 4.5 | 1857.3637 | 1862.3463
DEER-SFAM-CZ09-V4-eSA-18-TM-s2 | 18 | CZ09 | V4 | CZ09-V4-eSA-18 | CZ09-V4-eSA-18-TM | 16.168 | 3.0884 | 1814.8157 | 0 | 4.5 | 1814.8157 | 1819.46
DEER-SFAM-CZ09-V4-eSH-10-HH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-HH | 9.7909 | 4.681 | 2684.1588 | 322.7656 | 4.5 | 3006.9244 | 2716.5244
DEER-SFAM-CZ09-V4-eSH-10-HL-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-HL | 9.5642 | 4.8833 | 2761.4586 | 322.8996 | 4.5 | 3084.3582 | 2793.6582
DEER-SFAM-CZ09-V4-eSH-10-HM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-HM | 10.0059 | 4.7528 | 2686.1262 | 316.211 | 4.5 | 3002.3372 | 2716.8372
DEER-SFAM-CZ09-V4-eSH-10-LH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-LH | 10.2923 | 4.1722 | 2586.3944 | 340.9976 | 4.1 | 2927.392 | 2619.792
DEER-SFAM-CZ09-V4-eSH-10-LL-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-LL | 9.9126 | 4.6125 | 2690.9831 | 318.2333 | 4.5 | 3009.2164 | 2725.6164
DEER-SFAM-CZ09-V4-eSH-10-LM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-LM | 10.0771 | 4.5263 | 2649.3282 | 320.7428 | 4.5 | 2970.071 | 2681.171
DEER-SFAM-CZ09-V4-eSH-10-MH-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-MH | 10.2154 | 4.5415 | 2619.9687 | 333.3721 | 4.5 | 2953.3408 | 2655.4408
DEER-SFAM-CZ09-V4-eSH-10-ML-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-ML | 9.8995 | 4.9254 | 2706.9006 | 296.8951 | 4.5 | 3003.7957 | 2738.7957
DEER-SFAM-CZ09-V4-eSH-10-MM-s1 | 10 | CZ09 | V4 | CZ09-V4-eSH-10 | CZ09-V4-eSH-10-MM | 10.0769 | 4.4818 | 2667.1286 | 320.985 | 4.1 | 2988.1136 | 2697.3136
DEER-SFAM-CZ09-V4-eSH-13-HH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-HH | 11.8497 | 3.875 | 2207.1732 | 310.0263 | 4.5 | 2517.1995 | 2236.6995
DEER-SFAM-CZ09-V4-eSH-13-HL-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-HL | 12.5741 | 4.0569 | 2090.0507 | 262.1614 | 4.5 | 2352.2121 | 2119.4121
DEER-SFAM-CZ09-V4-eSH-13-HM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-HM | 12.1176 | 3.8605 | 2166.4131 | 274.6235 | 4.5 | 2441.0366 | 2193.0366
DEER-SFAM-CZ09-V4-eSH-13-LH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-LH | 12.8283 | 3.5746 | 2044.5522 | 313.6693 | 4.5 | 2358.2215 | 2088.6215
DEER-SFAM-CZ09-V4-eSH-13-LL-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-LL | 13.3588 | 3.7032 | 1999.6838 | 276.9194 | 4.5 | 2276.6032 | 2026.6032
DEER-SFAM-CZ09-V4-eSH-13-LM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-LM | 12.4523 | 3.5802 | 2100.2723 | 245.7733 | 4.1 | 2346.0456 | 2131.1456
DEER-SFAM-CZ09-V4-eSH-13-MH-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-MH | 12.9559 | 3.6733 | 2034.9805 | 312.8302 | 4.5 | 2347.8107 | 2064.7107
DEER-SFAM-CZ09-V4-eSH-13-ML-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-ML | 12.3713 | 3.7899 | 2119.6425 | 280.8441 | 4.1 | 2400.4866 | 2150.0866
DEER-SFAM-CZ09-V4-eSH-13-MM-s1 | 13 | CZ09 | V4 | CZ09-V4-eSH-13 | CZ09-V4-eSH-13-MM | 12.8501 | 3.9137 | 2078.7281 | 287.6193 | 4.5 | 2366.3474 | 2102.6474
DEER-SFAM-CZ09-V4-eSH-14-HH-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-HH | 12.5655 | 3.676 | 2081.2229 | 280.7935 | 4.5 | 2362.0164 | 2103.7164
DEER-SFAM-CZ09-V4-eSH-14-HL-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-HL | 12.8883 | 3.6432 | 2025.6554 | 269.6935 | 4.5 | 2295.3489 | 2052.6489
DEER-SFAM-CZ09-V4-eSH-14-HM-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-HM | 12.7722 | 3.5103 | 2034.0375 | 270.9839 | 4.5 | 2305.0214 | 2053.2214
DEER-SFAM-CZ09-V4-eSH-14-MH-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-MH | 13.8002 | 3.1956 | 1896.044 | 283.5793 | 4.1 | 2179.6233 | 1925.1233
DEER-SFAM-CZ09-V4-eSH-14-ML-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-ML | 13.8423 | 3.5756 | 1891.6245 | 286.6246 | 4.5 | 2178.2491 | 1927.9491
DEER-SFAM-CZ09-V4-eSH-14-MM-s1 | 14 | CZ09 | V4 | CZ09-V4-eSH-14 | CZ09-V4-eSH-14-MM | 13.5042 | 3.5183 | 1921.0867 | 262.5266 | 4.5 | 2183.6133 | 1946.5133
DEER-SFAM-CZ09-V4-eSH-15-HH-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-HH | 13.6905 | 3.2176 | 1882.6067 | 313.4001 | 4.5 | 2196.0068 | 1903.4068
DEER-SFAM-CZ09-V4-eSH-15-HL-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-HL | 13.9583 | 3.5287 | 1882.2813 | 235.5497 | 4.5 | 2117.831 | 1903.031
DEER-SFAM-CZ09-V4-eSH-15-HM-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-HM | 14.459 | 3.3635 | 1811.5038 | 246.7665 | 4.5 | 2058.2703 | 1832.1703
DEER-SFAM-CZ09-V4-eSH-15-MH-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-MH | 14.4667 | 3.3905 | 1813.4135 | 275.6856 | 4.5 | 2089.0991 | 1833.2991
DEER-SFAM-CZ09-V4-eSH-15-ML-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-ML | 14.7917 | 3.3813 | 1771.6375 | 253.4514 | 4.5 | 2025.0889 | 1792.1889
DEER-SFAM-CZ09-V4-eSH-15-MM-s1 | 15 | CZ09 | V4 | CZ09-V4-eSH-15 | CZ09-V4-eSH-15-MM | 14.6853 | 3.3335 | 1800.5247 | 274.48 | 4.5 | 2075.0047 | 1822.4047
DEER-SFAM-CZ09-V4-eSH-16-CH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-CH | 14.8228 | 3.5031 | 2016.3878 | 257.1101 | 4.5 | 2273.4979 | 2032.8979
DEER-SFAM-CZ09-V4-eSH-16-CL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-CL | 14.9443 | 3.6887 | 2028.2687 | 238.1273 | 4.5 | 2266.396 | 2045.696
DEER-SFAM-CZ09-V4-eSH-16-LH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-LH | 14.3626 | 3.1103 | 1865.2384 | 297.3598 | 4.1 | 2162.5982 | 1885.8982
DEER-SFAM-CZ09-V4-eSH-16-LL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-LL | 14.086 | 3.3612 | 1929.6196 | 260.1143 | 4.1 | 2189.7339 | 1946.2339
DEER-SFAM-CZ09-V4-eSH-16-LM-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-LM | 13.9476 | 3.2009 | 1930.9116 | 294.4949 | 4.1 | 2225.4065 | 1954.0065
DEER-SFAM-CZ09-V4-eSH-16-TH-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-TH | 15.3163 | 3.4211 | 1919.4066 | 325.4075 | 4.5 | 2244.8141 | 1934.5141
DEER-SFAM-CZ09-V4-eSH-16-TL-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-TL | 14.5724 | 3.9393 | 2099.5827 | 303.748 | 4.5 | 2403.3307 | 2112.5307
DEER-SFAM-CZ09-V4-eSH-16-TM-s2 | 16 | CZ09 | V4 | CZ09-V4-eSH-16 | CZ09-V4-eSH-16-TM | 14.7126 | 3.8709 | 2079.5727 | 310.3742 | 4.5 | 2389.9469 | 2092.7469
DEER-SFAM-CZ09-V4-eSH-17-CM-s2 | 17 | CZ09 | V4 | CZ09-V4-eSH-17 | CZ09-V4-eSH-17-CM | 15.7841 | 3.5052 | 1918.184 | 257.7379 | 4.5 | 2175.9219 | 1937.6219
DEER-SFAM-CZ09-V4-eSH-17-LM-s2 | 17 | CZ09 | V4 | CZ09-V4-eSH-17 | CZ09-V4-eSH-17-LM | 14.6958 | 3.4008 | 1895.1778 | 255.0647 | 4.5 | 2150.2425 | 1904.5425
DEER-SFAM-CZ09-V4-eSH-17-TH-s2 | 17 | CZ09 | V4 | CZ09-V4-eSH-17 | CZ09-V4-eSH-17-TH | 16.1435 | 3.2304 | 1817.771 | 320.1651 | 4.5 | 2137.9361 | 1833.6361
DEER-SFAM-CZ09-V4-eSH-17-TL-s2 | 17 | CZ09 | V4 | CZ09-V4-eSH-17 | CZ09-V4-eSH-17-TL | 16.0967 | 3.2975 | 1827.164 | 313.261 | 4.5 | 2140.425 | 1842.925
DEER-SFAM-CZ09-V4-eSH-18-LH-s2 | 18 | CZ09 | V4 | CZ09-V4-eSH-18 | CZ09-V4-eSH-18-LH | 15.7621 | 2.9792 | 1725.2867 | 278.0524 | 4.1 | 2003.3391 | 1740.0391
DEER-SFAM-CZ09-V4-eSH-18-LL-s2 | 18 | CZ09 | V4 | CZ09-V4-eSH-18 | CZ09-V4-eSH-18-LL | 15.0903 | 3.0496 | 1790.4754 | 256.8784 | 4.1 | 2047.3538 | 1804.7538
DEER-SFAM-CZ09-V4-eSH-18-LM-s2 | 18 | CZ09 | V4 | CZ09-V4-eSH-18 | CZ09-V4-eSH-18-LM | 15.7481 | 3.0365 | 1738.9867 | 290.5433 | 4.1 | 2029.53 | 1755.73
DEER-SFAM-CZ09-V4-eSH-18-TM-s2 | 18 | CZ09 | V4 | CZ09-V4-eSH-18 | CZ09-V4-eSH-18-TM | 17.1197 | 3.132 | 1727.1963 | 304.7297 | 4.1 | 2031.926 | 1750.026
DEER-SFAM-CZ10-V1-eSA-10-HH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-HH | 9.4461 | 4.4253 | 2788.1003 | 0 | 3.6518 | 2788.1003 | 2886.9935
DEER-SFAM-CZ10-V1-eSA-10-HL-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-HL | 8.8325 | 4.9866 | 2918.9022 | 0 | 3.6518 | 2918.9022 | 3017.8799
DEER-SFAM-CZ10-V1-eSA-10-HM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-HM | 8.842 | 4.5765 | 2838.7816 | 0 | 3.6518 | 2838.7816 | 2937.7439
DEER-SFAM-CZ10-V1-eSA-10-LH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-LH | 10.2626 | 4.2148 | 2677.6716 | 0 | 3.6518 | 2677.6716 | 2776.7327
DEER-SFAM-CZ10-V1-eSA-10-LL-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-LL | 9.2451 | 4.607 | 2796.794 | 0 | 3.6518 | 2796.794 | 2895.791
DEER-SFAM-CZ10-V1-eSA-10-LM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-LM | 10.0907 | 4.2742 | 2690.8312 | 0 | 3.6518 | 2690.8312 | 2789.8963
DEER-SFAM-CZ10-V1-eSA-10-MH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-MH | 10.0696 | 4.1043 | 2689.2673 | 0 | 3.6518 | 2689.2673 | 2788.2993
DEER-SFAM-CZ10-V1-eSA-10-ML-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-ML | 9.0449 | 4.698 | 2882.3138 | 0 | 3.6518 | 2882.3138 | 2981.2935
DEER-SFAM-CZ10-V1-eSA-10-MM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSA-10 | CZ10-V1-eSA-10-MM | 9.8623 | 3.9871 | 2666.2102 | 0 | 3.3147 | 2666.2102 | 2765.105
DEER-SFAM-CZ10-V1-eSA-13-HH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-HH | 11.9134 | 3.7017 | 2166.1527 | 0 | 3.6518 | 2166.1527 | 2255.3735
DEER-SFAM-CZ10-V1-eSA-13-HL-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-HL | 11.8977 | 3.8936 | 2180.9165 | 0 | 3.6518 | 2180.9165 | 2259.0001
DEER-SFAM-CZ10-V1-eSA-13-HM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-HM | 11.8395 | 3.8287 | 2160.6665 | 0 | 3.6518 | 2160.6665 | 2249.8543
DEER-SFAM-CZ10-V1-eSA-13-LH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-LH | 12.809 | 3.3321 | 2055.0974 | 0 | 3.6518 | 2055.0974 | 2154.1003
DEER-SFAM-CZ10-V1-eSA-13-LL-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-LL | 12.2416 | 3.6218 | 2160.3729 | 0 | 3.6518 | 2160.3729 | 2259.176
DEER-SFAM-CZ10-V1-eSA-13-LM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-LM | 12.2349 | 3.462 | 2146.0473 | 0 | 3.6518 | 2146.0473 | 2244.9664
DEER-SFAM-CZ10-V1-eSA-13-MH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-MH | 12.7299 | 3.5779 | 2110.9714 | 0 | 3.6518 | 2110.9714 | 2209.9346
DEER-SFAM-CZ10-V1-eSA-13-ML-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-ML | 11.6125 | 3.7631 | 2152.3524 | 0 | 3.6518 | 2152.3524 | 2251.0076
DEER-SFAM-CZ10-V1-eSA-13-MM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSA-13 | CZ10-V1-eSA-13-MM | 12.6266 | 3.6285 | 2083.032 | 0 | 3.6518 | 2083.032 | 2181.9798
DEER-SFAM-CZ10-V1-eSA-14-HH-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-HH | 11.8406 | 3.5841 | 2103.5218 | 0 | 3.6518 | 2103.5218 | 2186.4609
DEER-SFAM-CZ10-V1-eSA-14-HL-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-HL | 13.1062 | 3.5917 | 2011.8375 | 0 | 3.6518 | 2011.8375 | 2072.8264
DEER-SFAM-CZ10-V1-eSA-14-HM-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-HM | 12.8209 | 3.5957 | 2080.5631 | 0 | 3.6518 | 2080.5631 | 2174.1377
DEER-SFAM-CZ10-V1-eSA-14-MH-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-MH | 13.4121 | 2.9603 | 2010.5943 | 0 | 3.3147 | 2010.5943 | 2075.5449
DEER-SFAM-CZ10-V1-eSA-14-ML-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-ML | 12.6925 | 3.4874 | 2023.8546 | 0 | 3.6518 | 2023.8546 | 2127.7026
DEER-SFAM-CZ10-V1-eSA-14-MM-s1 | 14 | CZ10 | V1 | CZ10-V1-eSA-14 | CZ10-V1-eSA-14-MM | 13.257 | 2.9935 | 1979.8442 | 0 | 3.3147 | 1979.8442 | 2051.0592
DEER-SFAM-CZ10-V1-eSA-15-HH-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-HH | 13.4613 | 3.3089 | 1891.3922 | 0 | 3.6518 | 1891.3922 | 1960.5367
DEER-SFAM-CZ10-V1-eSA-15-HL-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-HL | 14.0671 | 3.3673 | 1852.0321 | 0 | 3.6518 | 1852.0321 | 1938.206
DEER-SFAM-CZ10-V1-eSA-15-HM-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-HM | 13.448 | 3.191 | 1873.4952 | 0 | 3.6518 | 1873.4952 | 1942.8938
DEER-SFAM-CZ10-V1-eSA-15-MH-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-MH | 13.3352 | 3.3358 | 1937.2223 | 0 | 3.6518 | 1937.2223 | 1988.744
DEER-SFAM-CZ10-V1-eSA-15-ML-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-ML | 14.0332 | 3.2594 | 1896.0502 | 0 | 3.6518 | 1896.0502 | 1965.327
DEER-SFAM-CZ10-V1-eSA-15-MM-s1 | 15 | CZ10 | V1 | CZ10-V1-eSA-15 | CZ10-V1-eSA-15-MM | 13.869 | 3.2919 | 1889.1338 | 0 | 3.6518 | 1889.1338 | 1952.3098
DEER-SFAM-CZ10-V1-eSA-16-CH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-CH | 13.8071 | 3.5066 | 2308.1639 | 0 | 3.6518 | 2308.1639 | 2347.3008
DEER-SFAM-CZ10-V1-eSA-16-CL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-CL | 14.0076 | 3.5789 | 2172.6217 | 0 | 3.6518 | 2172.6217 | 2222.3661
DEER-SFAM-CZ10-V1-eSA-16-CM-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-CM | 13.7581 | 3.6007 | 2242.9786 | 0 | 3.6518 | 2242.9786 | 2295.5096
DEER-SFAM-CZ10-V1-eSA-16-LH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-LH | 13.7801 | 3.2968 | 1975.4014 | 0 | 3.6518 | 1975.4014 | 2042.9493
DEER-SFAM-CZ10-V1-eSA-16-LL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-LL | 13.2068 | 3.6201 | 2107.9128 | 0 | 3.6518 | 2107.9128 | 2152.5246
DEER-SFAM-CZ10-V1-eSA-16-LM-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-LM | 13.362 | 3.4729 | 2082.4263 | 0 | 3.6518 | 2082.4263 | 2122.8596
DEER-SFAM-CZ10-V1-eSA-16-NM-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-NM | 14.8858 | 3.2512 | 1879.291 | 0 | 3.6518 | 1879.291 | 1918.9275
DEER-SFAM-CZ10-V1-eSA-16-TH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-TH | 13.1706 | 3.8215 | 2440.1757 | 0 | 3.6518 | 2440.1757 | 2465.2105
DEER-SFAM-CZ10-V1-eSA-16-TL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSA-16 | CZ10-V1-eSA-16-TL | 13.9585 | 3.5847 | 2211.8673 | 0 | 3.6518 | 2211.8673 | 2239.0568
DEER-SFAM-CZ10-V1-eSA-17-CH-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-CH | 14.5925 | 3.389 | 2135.9907 | 0 | 3.6518 | 2135.9907 | 2185.7034
DEER-SFAM-CZ10-V1-eSA-17-CL-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-CL | 14.5032 | 3.4619 | 2129.7055 | 0 | 3.6518 | 2129.7055 | 2179.4082
DEER-SFAM-CZ10-V1-eSA-17-CM-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-CM | 14.6081 | 3.4388 | 2160.7657 | 0 | 3.6518 | 2160.7657 | 2199.785
DEER-SFAM-CZ10-V1-eSA-17-LH-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-LH | 14.2408 | 2.9726 | 1905.0486 | 0 | 3.3147 | 1905.0486 | 1958.0213
DEER-SFAM-CZ10-V1-eSA-17-LL-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-LL | 13.8817 | 3.471 | 2031.8716 | 0 | 3.6518 | 2031.8716 | 2060.8594
DEER-SFAM-CZ10-V1-eSA-17-LM-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-LM | 13.7924 | 3.3423 | 2010.016 | 0 | 3.6518 | 2010.016 | 2035.0543
DEER-SFAM-CZ10-V1-eSA-17-TH-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-TH | 14.9693 | 3.2143 | 2033.2379 | 0 | 3.6518 | 2033.2379 | 2073.4689
DEER-SFAM-CZ10-V1-eSA-17-TL-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-TL | 15.256 | 3.2747 | 1903.0159 | 0 | 3.6518 | 1903.0159 | 1965.9683
DEER-SFAM-CZ10-V1-eSA-17-TM-s2 | 17 | CZ10 | V1 | CZ10-V1-eSA-17 | CZ10-V1-eSA-17-TM | 15.1527 | 3.4455 | 2281.3452 | 0 | 3.6518 | 2281.3452 | 2302.2795
DEER-SFAM-CZ10-V1-eSA-18-LH-s2 | 18 | CZ10 | V1 | CZ10-V1-eSA-18 | CZ10-V1-eSA-18-LH | 14.734 | 3.2118 | 1894.4849 | 0 | 3.6518 | 1894.4849 | 1929.3534
DEER-SFAM-CZ10-V1-eSA-18-LL-s2 | 18 | CZ10 | V1 | CZ10-V1-eSA-18 | CZ10-V1-eSA-18-LL | 15.0037 | 3.1206 | 1831.9046 | 0 | 3.6518 | 1831.9046 | 1877.4027
DEER-SFAM-CZ10-V1-eSA-18-TH-s2 | 18 | CZ10 | V1 | CZ10-V1-eSA-18 | CZ10-V1-eSA-18-TH | 15.647 | 3.0479 | 1959.9954 | 0 | 3.6518 | 1959.9954 | 1987.4051
DEER-SFAM-CZ10-V1-eSA-18-TL-s2 | 18 | CZ10 | V1 | CZ10-V1-eSA-18 | CZ10-V1-eSA-18-TL | 14.9505 | 3.4624 | 2159.9323 | 0 | 3.6518 | 2159.9323 | 2189.7919
DEER-SFAM-CZ10-V1-eSA-18-TM-s2 | 18 | CZ10 | V1 | CZ10-V1-eSA-18 | CZ10-V1-eSA-18-TM | 15.0605 | 3.1336 | 2007.6729 | 0 | 3.6518 | 2007.6729 | 2035.6401
DEER-SFAM-CZ10-V1-eSH-10-HH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-HH | 9.8035 | 4.4563 | 2681.8724 | 2160.7313 | 3.6518 | 4842.6037 | 2907.0638
DEER-SFAM-CZ10-V1-eSH-10-HL-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-HL | 9.4581 | 4.6614 | 2785.9328 | 2186.9946 | 3.6518 | 4972.9274 | 3007.662
DEER-SFAM-CZ10-V1-eSH-10-HM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-HM | 9.8602 | 4.5467 | 2744.6388 | 2107.5487 | 3.6518 | 4852.1875 | 2957.7034
DEER-SFAM-CZ10-V1-eSH-10-LH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-LH | 10.1743 | 4.0951 | 2647.6186 | 2268.3632 | 3.6518 | 4915.9819 | 2879.8281
DEER-SFAM-CZ10-V1-eSH-10-LL-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-LL | 9.864 | 4.461 | 2712.3829 | 2217.4896 | 3.6518 | 4929.8726 | 2954.3438
DEER-SFAM-CZ10-V1-eSH-10-LM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-LM | 10.0983 | 4.2852 | 2652.0088 | 2178.0398 | 3.6518 | 4830.0486 | 2873.2275
DEER-SFAM-CZ10-V1-eSH-10-MH-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-MH | 10.1838 | 4.2837 | 2678.4955 | 2252.1036 | 3.6518 | 4930.5992 | 2925.1708
DEER-SFAM-CZ10-V1-eSH-10-ML-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-ML | 9.7499 | 4.6958 | 2766.5426 | 2082.4121 | 3.6518 | 4848.9546 | 2989.8209
DEER-SFAM-CZ10-V1-eSH-10-MM-s1 | 10 | CZ10 | V1 | CZ10-V1-eSH-10 | CZ10-V1-eSH-10-MM | 9.8427 | 4.4442 | 2765.4904 | 2195.0807 | 3.6518 | 4960.5711 | 2973.8504
DEER-SFAM-CZ10-V1-eSH-13-HH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-HH | 11.3175 | 3.8012 | 2255.7994 | 2087.0825 | 3.6518 | 4342.8819 | 2461.1701
DEER-SFAM-CZ10-V1-eSH-13-HL-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-HL | 12.4394 | 3.8382 | 2131.9502 | 1817.0544 | 3.6518 | 3949.0046 | 2336.2638
DEER-SFAM-CZ10-V1-eSH-13-HM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-HM | 11.5986 | 3.7729 | 2210.5926 | 1860.4092 | 3.6518 | 4071.0018 | 2395.5065
DEER-SFAM-CZ10-V1-eSH-13-LH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-LH | 12.6563 | 3.3511 | 2093.9292 | 2269.7557 | 3.6518 | 4363.6849 | 2404.6962
DEER-SFAM-CZ10-V1-eSH-13-LL-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-LL | 13.0735 | 3.5248 | 2052.5871 | 1921.0877 | 3.6518 | 3973.6748 | 2240.4608
DEER-SFAM-CZ10-V1-eSH-13-LM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-LM | 12.1586 | 3.2555 | 2150.4408 | 1682.4905 | 3.3147 | 3832.9313 | 2362.9025
DEER-SFAM-CZ10-V1-eSH-13-MH-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-MH | 12.8057 | 3.5117 | 2061.3212 | 2119.1857 | 3.6518 | 4180.5069 | 2267.5986
DEER-SFAM-CZ10-V1-eSH-13-ML-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-ML | 11.8106 | 3.7805 | 2218.0641 | 1983.4044 | 3.6518 | 4201.4684 | 2429.6361
DEER-SFAM-CZ10-V1-eSH-13-MM-s1 | 13 | CZ10 | V1 | CZ10-V1-eSH-13 | CZ10-V1-eSH-13-MM | 12.4145 | 3.7556 | 2162.1593 | 1959.0623 | 3.6518 | 4121.2216 | 2325.9205
DEER-SFAM-CZ10-V1-eSH-14-HH-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-HH | 11.9592 | 3.6329 | 2134.0849 | 1907.9427 | 3.6518 | 4042.0276 | 2290.3292
DEER-SFAM-CZ10-V1-eSH-14-HL-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-HL | 12.313 | 3.5917 | 2069.2963 | 1903.5646 | 3.6518 | 3972.8609 | 2257.7093
DEER-SFAM-CZ10-V1-eSH-14-HM-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-HM | 12.2841 | 3.4522 | 2061.9516 | 1879.6828 | 3.6518 | 3941.6344 | 2195.7909
DEER-SFAM-CZ10-V1-eSH-14-MH-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-MH | 13.4709 | 3.1592 | 1954.0141 | 2044.7114 | 3.6518 | 3998.7255 | 2158.777
DEER-SFAM-CZ10-V1-eSH-14-ML-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-ML | 13.5016 | 3.4574 | 1974.4368 | 2179.3741 | 3.6518 | 4153.8109 | 2233.3803
DEER-SFAM-CZ10-V1-eSH-14-MM-s1 | 14 | CZ10 | V1 | CZ10-V1-eSH-14 | CZ10-V1-eSH-14-MM | 13.1987 | 3.3538 | 1973.2937 | 1853.3288 | 3.6518 | 3826.6225 | 2150.1294
DEER-SFAM-CZ10-V1-eSH-15-HH-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-HH | 13.1746 | 3.1757 | 1904.8383 | 2316.4275 | 3.6518 | 4221.2658 | 2051.7682
DEER-SFAM-CZ10-V1-eSH-15-HL-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-HL | 13.4924 | 3.3971 | 1914.3796 | 1622.4113 | 3.6518 | 3536.7909 | 2058.0076
DEER-SFAM-CZ10-V1-eSH-15-HM-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-HM | 14.2077 | 3.2851 | 1836.1167 | 1678.3359 | 3.6518 | 3514.4526 | 1979.9886
DEER-SFAM-CZ10-V1-eSH-15-MH-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-MH | 13.9674 | 3.2924 | 1905.5662 | 2001.1755 | 3.6518 | 3906.7417 | 2045.7932
DEER-SFAM-CZ10-V1-eSH-15-ML-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-ML | 14.3693 | 3.2911 | 1848.8033 | 1879.8896 | 3.6518 | 3728.693 | 1994.3249
DEER-SFAM-CZ10-V1-eSH-15-MM-s1 | 15 | CZ10 | V1 | CZ10-V1-eSH-15 | CZ10-V1-eSH-15-MM | 14.3704 | 3.2582 | 1832.1009 | 1977.4555 | 3.6518 | 3809.5564 | 1985.2977
DEER-SFAM-CZ10-V1-eSH-16-CH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-CH | 13.9956 | 3.4703 | 2218.7461 | 2211.3808 | 3.6518 | 4430.1269 | 2360.2633
DEER-SFAM-CZ10-V1-eSH-16-CL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-CL | 14.1303 | 3.5356 | 2281.1108 | 2047.9579 | 3.6518 | 4329.0687 | 2426.2073
DEER-SFAM-CZ10-V1-eSH-16-LH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-LH | 13.5214 | 3.2636 | 1999.1369 | 2326.4556 | 3.6518 | 4325.5926 | 2150.037
DEER-SFAM-CZ10-V1-eSH-16-LL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-LL | 13.2794 | 3.5011 | 2078.9797 | 2129.1724 | 3.6518 | 4208.1522 | 2199.139
DEER-SFAM-CZ10-V1-eSH-16-LM-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-LM | 13.2269 | 3.1265 | 2045.7877 | 2386.6046 | 3.3147 | 4432.3923 | 2219.5532
DEER-SFAM-CZ10-V1-eSH-16-TH-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-TH | 14.1134 | 3.5636 | 2144.3305 | 2804.5183 | 3.6518 | 4948.8488 | 2303.4762
DEER-SFAM-CZ10-V1-eSH-16-TL-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-TL | 13.3223 | 3.8956 | 2435.8857 | 2768.6109 | 3.6518 | 5204.4966 | 2580.1754
DEER-SFAM-CZ10-V1-eSH-16-TM-s2 | 16 | CZ10 | V1 | CZ10-V1-eSH-16 | CZ10-V1-eSH-16-TM | 13.5111 | 3.8204 | 2403.4717 | 2801.5193 | 3.6518 | 5204.991 | 2551.7814
DEER-SFAM-CZ10-V1-eSH-17-CM-s2 | 17 | CZ10 | V1 | CZ10-V1-eSH-17 | CZ10-V1-eSH-17-CM | 14.9104 | 3.3686 | 2158.2141 | 2257.8357 | 3.6518 | 4416.0498 | 2319.1259
DEER-SFAM-CZ10-V1-eSH-17-LM-s2 | 17 | CZ10 | V1 | CZ10-V1-eSH-17 | CZ10-V1-eSH-17-LM | 13.9373 | 3.3798 | 2062.8291 | 2055.0891 | 3.6518 | 4117.9181 | 2130.242
DEER-SFAM-CZ10-V1-eSH-17-TH-s2 | 17 | CZ10 | V1 | CZ10-V1-eSH-17 | CZ10-V1-eSH-17-TH | 14.9066 | 3.3233 | 2025.6139 | 2800.0586 | 3.6518 | 4825.6725 | 2196.0924
DEER-SFAM-CZ10-V1-eSH-17-TL-s2 | 17 | CZ10 | V1 | CZ10-V1-eSH-17 | CZ10-V1-eSH-17-TL | 14.798 | 3.4018 | 2045.7688 | 2789.6612 | 3.6518 | 4835.4299 | 2214.4123
DEER-SFAM-CZ10-V1-eSH-18-LH-s2 | 18 | CZ10 | V1 | CZ10-V1-eSH-18 | CZ10-V1-eSH-18-LH | 14.7683 | 2.9213 | 1867.865 | 2489.1659 | 3.3147 | 4357.0309 | 1991.694
DEER-SFAM-CZ10-V1-eSH-18-LL-s2 | 18 | CZ10 | V1 | CZ10-V1-eSH-18 | CZ10-V1-eSH-18-LL | 14.1419 | 2.999 | 1929.6317 | 2216.6182 | 3.3147 | 4146.2499 | 2038.8862
DEER-SFAM-CZ10-V1-eSH-18-LM-s2 | 18 | CZ10 | V1 | CZ10-V1-eSH-18 | CZ10-V1-eSH-18-LM | 14.6665 | 3.2638 | 1910.6644 | 2620.5352 | 3.6518 | 4531.1996 | 2050.3427
DEER-SFAM-CZ10-V1-eSH-18-TM-s2 | 18 | CZ10 | V1 | CZ10-V1-eSH-18 | CZ10-V1-eSH-18-TM | 15.5181 | 3.0225 | 1949.3077 | 2799.1923 | 3.3147 | 4748.5 | 2195.1855
DEER-SFAM-CZ10-V2-eSA-10-HH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-HH | 9.4518 | 4.0268 | 2698.2567 | 0 | 3.3462 | 2698.2567 | 2752.9891
DEER-SFAM-CZ10-V2-eSA-10-HL-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-HL | 8.8153 | 4.5101 | 2836.0265 | 0 | 3.3462 | 2836.0265 | 2890.8079
DEER-SFAM-CZ10-V2-eSA-10-HM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-HM | 8.8386 | 4.1271 | 2754.5598 | 0 | 3.3462 | 2754.5598 | 2809.3322
DEER-SFAM-CZ10-V2-eSA-10-LH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-LH | 10.179 | 3.8615 | 2597.6629 | 0 | 3.3462 | 2597.6629 | 2652.4934
DEER-SFAM-CZ10-V2-eSA-10-LL-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-LL | 9.2138 | 4.1828 | 2722.916 | 0 | 3.3462 | 2722.916 | 2777.7092
DEER-SFAM-CZ10-V2-eSA-10-LM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-LM | 10.0235 | 3.9061 | 2609.463 | 0 | 3.3462 | 2609.463 | 2664.2957
DEER-SFAM-CZ10-V2-eSA-10-MH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-MH | 10.0078 | 3.7595 | 2608.6637 | 0 | 3.3462 | 2608.6637 | 2663.4776
DEER-SFAM-CZ10-V2-eSA-10-ML-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-ML | 9.0045 | 4.2754 | 2803.2789 | 0 | 3.3462 | 2803.2789 | 2858.0617
DEER-SFAM-CZ10-V2-eSA-10-MM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSA-10 | CZ10-V2-eSA-10-MM | 9.9019 | 3.4266 | 2569.8693 | 0 | 2.8462 | 2569.8693 | 2624.5737
DEER-SFAM-CZ10-V2-eSA-13-HH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-HH | 11.9235 | 3.3924 | 2112.1587 | 0 | 3.3462 | 2112.1587 | 2161.5403
DEER-SFAM-CZ10-V2-eSA-13-HL-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-HL | 11.8919 | 3.5831 | 2118.6322 | 0 | 3.3462 | 2118.6322 | 2161.8496
DEER-SFAM-CZ10-V2-eSA-13-HM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-HM | 11.8008 | 3.4896 | 2108.3997 | 0 | 3.3462 | 2108.3997 | 2157.7624
DEER-SFAM-CZ10-V2-eSA-13-LH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-LH | 12.7693 | 3.0601 | 1994.3226 | 0 | 3.3462 | 1994.3226 | 2049.1193
DEER-SFAM-CZ10-V2-eSA-13-LL-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-LL | 12.1945 | 3.3226 | 2102.2435 | 0 | 3.3462 | 2102.2435 | 2156.922
DEER-SFAM-CZ10-V2-eSA-13-LM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-LM | 12.174 | 3.1805 | 2089.0746 | 0 | 3.3462 | 2089.0746 | 2143.8217
DEER-SFAM-CZ10-V2-eSA-13-MH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-MH | 12.7022 | 3.282 | 2045.1746 | 0 | 3.3462 | 2045.1746 | 2099.9472
DEER-SFAM-CZ10-V2-eSA-13-ML-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-ML | 11.6127 | 3.4457 | 2090.3188 | 0 | 3.3462 | 2090.3188 | 2144.9206
DEER-SFAM-CZ10-V2-eSA-13-MM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSA-13 | CZ10-V2-eSA-13-MM | 12.6359 | 3.3194 | 2016.0247 | 0 | 3.3462 | 2016.0247 | 2070.7891
DEER-SFAM-CZ10-V2-eSA-14-HH-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-HH | 11.8326 | 3.2905 | 2043.2103 | 0 | 3.3462 | 2043.2103 | 2089.1142
DEER-SFAM-CZ10-V2-eSA-14-HL-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-HL | 13.0575 | 3.3024 | 1954.3824 | 0 | 3.3462 | 1954.3824 | 1988.1382
DEER-SFAM-CZ10-V2-eSA-14-HM-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-HM | 12.7552 | 3.3023 | 2020.9375 | 0 | 3.3462 | 2020.9375 | 2072.7298
DEER-SFAM-CZ10-V2-eSA-14-MH-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-MH | 13.1095 | 2.9573 | 1983.3975 | 0 | 3.3462 | 1983.3975 | 2019.3833
DEER-SFAM-CZ10-V2-eSA-14-ML-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-ML | 12.6691 | 3.2149 | 1967.8917 | 0 | 3.3462 | 1967.8917 | 2025.368
DEER-SFAM-CZ10-V2-eSA-14-MM-s1 | 14 | CZ10 | V2 | CZ10-V2-eSA-14 | CZ10-V2-eSA-14-MM | 13.1486 | 2.7705 | 1929.1914 | 0 | 3.0578 | 1929.1914 | 1968.6053
DEER-SFAM-CZ10-V2-eSA-15-HH-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-HH | 13.4325 | 3.0168 | 1844.155 | 0 | 3.3462 | 1844.155 | 1882.4255
DEER-SFAM-CZ10-V2-eSA-15-HL-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-HL | 13.9252 | 3.2215 | 1811.5005 | 0 | 3.5578 | 1811.5005 | 1859.2172
DEER-SFAM-CZ10-V2-eSA-15-HM-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-HM | 13.4693 | 2.9065 | 1824.1102 | 0 | 3.3462 | 1824.1102 | 1862.5206
DEER-SFAM-CZ10-V2-eSA-15-MH-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-MH | 13.2856 | 3.0762 | 1881.9751 | 0 | 3.3462 | 1881.9751 | 1910.4922
DEER-SFAM-CZ10-V2-eSA-15-ML-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-ML | 13.9848 | 2.9932 | 1843.4143 | 0 | 3.3462 | 1843.4143 | 1881.753
DEER-SFAM-CZ10-V2-eSA-15-MM-s1 | 15 | CZ10 | V2 | CZ10-V2-eSA-15 | CZ10-V2-eSA-15-MM | 13.8087 | 3.026 | 1834.7363 | 0 | 3.3462 | 1834.7363 | 1869.703
DEER-SFAM-CZ10-V2-eSA-16-CH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-CH | 13.8 | 3.2107 | 2167.9404 | 0 | 3.3462 | 2167.9404 | 2189.9253
DEER-SFAM-CZ10-V2-eSA-16-CL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-CL | 14.0539 | 3.2132 | 2038.1406 | 0 | 3.3462 | 2038.1406 | 2065.9786
DEER-SFAM-CZ10-V2-eSA-16-CM-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-CM | 13.7766 | 3.2727 | 2104.8799 | 0 | 3.3462 | 2104.8799 | 2134.2649
DEER-SFAM-CZ10-V2-eSA-16-LH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-LH | 13.8591 | 2.9817 | 1876.9064 | 0 | 3.3462 | 1876.9064 | 1914.5659
DEER-SFAM-CZ10-V2-eSA-16-LL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-LL | 13.2879 | 3.2818 | 1995.9413 | 0 | 3.3462 | 1995.9413 | 2020.81
DEER-SFAM-CZ10-V2-eSA-16-LM-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-LM | 13.3927 | 3.1478 | 1976.5929 | 0 | 3.3462 | 1976.5929 | 1999.1445
DEER-SFAM-CZ10-V2-eSA-16-NM-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-NM | 14.973 | 2.9079 | 1780.9913 | 0 | 3.3462 | 1780.9913 | 1803.1058
DEER-SFAM-CZ10-V2-eSA-16-TH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-TH | 13.2304 | 3.4797 | 2267.9332 | 0 | 3.3462 | 2267.9332 | 2282.0556
DEER-SFAM-CZ10-V2-eSA-16-TL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSA-16 | CZ10-V2-eSA-16-TL | 14.0881 | 3.2245 | 2050.7323 | 0 | 3.3462 | 2050.7323 | 2066.0521
DEER-SFAM-CZ10-V2-eSA-17-CH-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-CH | 14.6037 | 3.1 | 2008.2839 | 0 | 3.3462 | 2008.2839 | 2036.1059
DEER-SFAM-CZ10-V2-eSA-17-CL-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-CL | 14.5275 | 3.162 | 1999.8169 | 0 | 3.3462 | 1999.8169 | 2027.6328
DEER-SFAM-CZ10-V2-eSA-17-CM-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-CM | 14.6282 | 3.1422 | 2026.374 | 0 | 3.3462 | 2026.374 | 2048.2929
DEER-SFAM-CZ10-V2-eSA-17-LH-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-LH | 14.234 | 2.9194 | 1831.8879 | 0 | 3.3462 | 1831.8879 | 1861.4318
DEER-SFAM-CZ10-V2-eSA-17-LL-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-LL | 13.9526 | 3.1487 | 1921.7347 | 0 | 3.3462 | 1921.7347 | 1937.9166
DEER-SFAM-CZ10-V2-eSA-17-LM-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-LM | 13.8513 | 3.0433 | 1909.2355 | 0 | 3.3462 | 1909.2355 | 1923.2005
DEER-SFAM-CZ10-V2-eSA-17-TH-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-TH | 14.9541 | 2.9286 | 1918.0412 | 0 | 3.3462 | 1918.0412 | 1940.6545
DEER-SFAM-CZ10-V2-eSA-17-TL-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-TL | 15.3609 | 2.9149 | 1786.3995 | 0 | 3.3462 | 1786.3995 | 1821.729
DEER-SFAM-CZ10-V2-eSA-17-TM-s2 | 17 | CZ10 | V2 | CZ10-V2-eSA-17 | CZ10-V2-eSA-17-TM | 15.2546 | 3.1439 | 2094.8687 | 0 | 3.3462 | 2094.8687 | 2106.7437
DEER-SFAM-CZ10-V2-eSA-18-LH-s2 | 18 | CZ10 | V2 | CZ10-V2-eSA-18 | CZ10-V2-eSA-18-LH | 14.8095 | 2.9151 | 1792.5639 | 0 | 3.3462 | 1792.5639 | 1812.0116
DEER-SFAM-CZ10-V2-eSA-18-LL-s2 | 18 | CZ10 | V2 | CZ10-V2-eSA-18 | CZ10-V2-eSA-18-LL | 15.0577 | 2.8292 | 1739.1123 | 0 | 3.3462 | 1739.1123 | 1764.4883
DEER-SFAM-CZ10-V2-eSA-18-TH-s2 | 18 | CZ10 | V2 | CZ10-V2-eSA-18 | CZ10-V2-eSA-18-TH | 15.6881 | 2.7645 | 1841.8244 | 0 | 3.3462 | 1841.8244 | 1857.2263
DEER-SFAM-CZ10-V2-eSA-18-TL-s2 | 18 | CZ10 | V2 | CZ10-V2-eSA-18 | CZ10-V2-eSA-18-TL | 15.0264 | 3.1771 | 2013.8992 | 0 | 3.3462 | 2013.8992 | 2030.7359
DEER-SFAM-CZ10-V2-eSA-18-TM-s2 | 18 | CZ10 | V2 | CZ10-V2-eSA-18 | CZ10-V2-eSA-18-TM | 15.0654 | 2.8521 | 1890.9229 | 0 | 3.3462 | 1890.9229 | 1906.6377
DEER-SFAM-CZ10-V2-eSH-10-HH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-HH | 9.718 | 4.0915 | 2613.5276 | 1206.1797 | 3.3462 | 3819.7073 | 2736.8424
DEER-SFAM-CZ10-V2-eSH-10-HL-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-HL | 9.3783 | 4.247 | 2712.8664 | 1216.7502 | 3.3462 | 3929.6165 | 2833.9245
DEER-SFAM-CZ10-V2-eSH-10-HM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-HM | 9.834 | 4.1779 | 2659.2744 | 1187.2774 | 3.3462 | 3846.5519 | 2775.6483
DEER-SFAM-CZ10-V2-eSH-10-LH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-LH | 10.125 | 3.7544 | 2572.85 | 1258.3903 | 3.3462 | 3831.2403 | 2699.8362
DEER-SFAM-CZ10-V2-eSH-10-LL-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-LL | 9.8052 | 4.0768 | 2631.4459 | 1234.1491 | 3.3462 | 3865.595 | 2764.0376
DEER-SFAM-CZ10-V2-eSH-10-LM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-LM | 10.0604 | 3.9341 | 2573.015 | 1220.816 | 3.3462 | 3793.8309 | 2694.5042
DEER-SFAM-CZ10-V2-eSH-10-MH-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-MH | 10.125 | 3.9194 | 2598.6728 | 1248.6995 | 3.3462 | 3847.3723 | 2733.4878
DEER-SFAM-CZ10-V2-eSH-10-ML-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-ML | 9.7091 | 4.2962 | 2681.1699 | 1164.642 | 3.3462 | 3845.8118 | 2804.063
DEER-SFAM-CZ10-V2-eSH-10-MM-s1 | 10 | CZ10 | V2 | CZ10-V2-eSH-10 | CZ10-V2-eSH-10-MM | 9.8123 | 4.0543 | 2681.2537 | 1221.602 | 3.3462 | 3902.8557 | 2795.5481
DEER-SFAM-CZ10-V2-eSH-13-HH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-HH | 11.3129 | 3.453 | 2195.7792 | 1155.6019 | 3.3462 | 3351.3811 | 2308.2861
DEER-SFAM-CZ10-V2-eSH-13-HL-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-HL | 12.3891 | 3.5442 | 2076.1478 | 1008.2924 | 3.3462 | 3084.4403 | 2188.1171
DEER-SFAM-CZ10-V2-eSH-13-HM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-HM | 11.5956 | 3.4187 | 2151.5122 | 1039.0593 | 3.3462 | 3190.5715 | 2253.0166
DEER-SFAM-CZ10-V2-eSH-13-LH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-LH | 12.5811 | 3.0828 | 2035.48 | 1198.0996 | 3.3462 | 3233.5796 | 2204.582
DEER-SFAM-CZ10-V2-eSH-13-LL-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-LL | 13.0512 | 3.2583 | 1989.0632 | 1057.8953 | 3.3462 | 3046.9585 | 2092.1152
DEER-SFAM-CZ10-V2-eSH-13-LM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-LM | 11.931 | 3.2488 | 2116.9026 | 923.5488 | 3.3462 | 3040.4514 | 2233.2644
DEER-SFAM-CZ10-V2-eSH-13-MH-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-MH | 12.7339 | 3.2438 | 2005.9843 | 1171.5421 | 3.3462 | 3177.5264 | 2118.5851
DEER-SFAM-CZ10-V2-eSH-13-ML-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-ML | 11.7618 | 3.4852 | 2161.447 | 1080.0204 | 3.3462 | 3241.4674 | 2276.8934
DEER-SFAM-CZ10-V2-eSH-13-MM-s1 | 13 | CZ10 | V2 | CZ10-V2-eSH-13 | CZ10-V2-eSH-13-MM | 12.3867 | 3.4604 | 2098.9765 | 1092.1816 | 3.3462 | 3191.1581 | 2188.6791
DEER-SFAM-CZ10-V2-eSH-14-HH-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-HH | 11.9569 | 3.2939 | 2077.3471 | 1059.976 | 3.3462 | 3137.3231 | 2162.9984
DEER-SFAM-CZ10-V2-eSH-14-HL-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-HL | 12.3036 | 3.2555 | 2015.2406 | 1043.8104 | 3.3462 | 3059.051 | 2118.1886
DEER-SFAM-CZ10-V2-eSH-14-HM-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-HM | 12.2787 | 3.1287 | 2008.5828 | 1038.9062 | 3.3462 | 3047.489 | 2081.9724
DEER-SFAM-CZ10-V2-eSH-14-MH-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-MH | 13.4087 | 2.9062 | 1899.0522 | 1093.2082 | 3.3462 | 2992.2604 | 2011.0518
DEER-SFAM-CZ10-V2-eSH-14-ML-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-ML | 13.4331 | 3.173 | 1911.2143 | 1137.1955 | 3.3462 | 3048.4098 | 2051.7977
DEER-SFAM-CZ10-V2-eSH-14-MM-s1 | 14 | CZ10 | V2 | CZ10-V2-eSH-14 | CZ10-V2-eSH-14-MM | 13.1362 | 3.0882 | 1919.6151 | 1014.8657 | 3.3462 | 2934.4807 | 2016.1766
DEER-SFAM-CZ10-V2-eSH-15-HH-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-HH | 13.1932 | 2.8905 | 1854.765 | 1197.7199 | 3.3462 | 3052.4849 | 1934.9285
DEER-SFAM-CZ10-V2-eSH-15-HL-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-HL | 13.4957 | 3.1074 | 1866.9627 | 904.5638 | 3.3462 | 2771.5265 | 1945.6275
DEER-SFAM-CZ10-V2-eSH-15-HM-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-HM | 14.0064 | 3.1359 | 1802.7346 | 939.3266 | 3.5578 | 2742.0612 | 1881.238
DEER-SFAM-CZ10-V2-eSH-15-MH-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-MH | 13.9053 | 3.0207 | 1850.2131 | 1059.9157 | 3.3462 | 2910.1288 | 1926.3242
DEER-SFAM-CZ10-V2-eSH-15-ML-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-ML | 14.3139 | 3.0133 | 1789.8597 | 1006.4737 | 3.3462 | 2796.3333 | 1869.0488
DEER-SFAM-CZ10-V2-eSH-15-MM-s1 | 15 | CZ10 | V2 | CZ10-V2-eSH-15 | CZ10-V2-eSH-15-MM | 14.2736 | 2.9924 | 1786.5074 | 1070.3591 | 3.3462 | 2856.8665 | 1870.4267
DEER-SFAM-CZ10-V2-eSH-16-CH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-CH | 13.9982 | 3.1262 | 2085.3352 | 1147.0892 | 3.3462 | 3232.4244 | 2158.967
DEER-SFAM-CZ10-V2-eSH-16-CL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-CL | 14.1192 | 3.2443 | 2140.0672 | 1065.6783 | 3.3462 | 3205.7455 | 2215.8083
DEER-SFAM-CZ10-V2-eSH-16-LH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-LH | 13.5859 | 2.9692 | 1904.1252 | 1174.4484 | 3.3462 | 3078.5736 | 1984.2695
DEER-SFAM-CZ10-V2-eSH-16-LL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-LL | 13.3139 | 3.1744 | 1976.0758 | 1074.1292 | 3.3462 | 3050.205 | 2040.2673
DEER-SFAM-CZ10-V2-eSH-16-LM-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-LM | 13.1709 | 3.0775 | 1976.9983 | 1176.5207 | 3.3462 | 3153.519 | 2066.5998
DEER-SFAM-CZ10-V2-eSH-16-TH-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-TH | 14.2203 | 3.2198 | 2006.8764 | 1458.7059 | 3.3462 | 3465.5823 | 2084.9486
DEER-SFAM-CZ10-V2-eSH-16-TL-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-TL | 13.3598 | 3.5595 | 2267.8958 | 1432.3176 | 3.3462 | 3700.2133 | 2339.6183
DEER-SFAM-CZ10-V2-eSH-16-TM-s2 | 16 | CZ10 | V2 | CZ10-V2-eSH-16 | CZ10-V2-eSH-16-TM | 13.54 | 3.491 | 2238.7226 | 1450.6315 | 3.3462 | 3689.3541 | 2312.7973
DEER-SFAM-CZ10-V2-eSH-17-CM-s2 | 17 | CZ10 | V2 | CZ10-V2-eSH-17 | CZ10-V2-eSH-17-CM | 14.8942 | 3.0913 | 2025.7271 | 1142.0926 | 3.3462 | 3167.8197 | 2107.4015
DEER-SFAM-CZ10-V2-eSH-17-LM-s2 | 17 | CZ10 | V2 | CZ10-V2-eSH-17 | CZ10-V2-eSH-17-LM | 13.9688 | 3.0793 | 1955.6444 | 1040.6907 | 3.3462 | 2996.3351 | 1991.7049
DEER-SFAM-CZ10-V2-eSH-17-TH-s2 | 17 | CZ10 | V2 | CZ10-V2-eSH-17 | CZ10-V2-eSH-17-TH | 14.9537 | 3.0098 | 1902.47 | 1454.9891 | 3.3462 | 3357.4591 | 1987.8641
DEER-SFAM-CZ10-V2-eSH-17-TL-s2 | 17 | CZ10 | V2 | CZ10-V2-eSH-17 | CZ10-V2-eSH-17-TL | 14.8613 | 3.079 | 1920.4712 | 1445.3498 | 3.3462 | 3365.8209 | 2004.3992
DEER-SFAM-CZ10-V2-eSH-18-LH-s2 | 18 | CZ10 | V2 | CZ10-V2-eSH-18 | CZ10-V2-eSH-18-LH | 14.7275 | 2.8741 | 1793.3343 | 1226.3887 | 3.3462 | 3019.7231 | 1852.6888
DEER-SFAM-CZ10-V2-eSH-18-LL-s2 | 18 | CZ10 | V2 | CZ10-V2-eSH-18 | CZ10-V2-eSH-18-LL | 14.1013 | 2.955 | 1854.6752 | 1077.4165 | 3.3462 | 2932.0917 | 1910.1158
DEER-SFAM-CZ10-V2-eSH-18-LM-s2 | 18 | CZ10 | V2 | CZ10-V2-eSH-18 | CZ10-V2-eSH-18-LM | 14.7347 | 2.9431 | 1808.4252 | 1300.747 | 3.3462 | 3109.1722 | 1876.7721
DEER-SFAM-CZ10-V2-eSH-18-TM-s2 | 18 | CZ10 | V2 | CZ10-V2-eSH-18 | CZ10-V2-eSH-18-TM | 15.5233 | 2.9965 | 1878.5377 | 1457.5925 | 3.3462 | 3336.1302 | 2006.4979
DEER-SFAM-CZ10-V3-eSA-10-HH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-HH | 9.4163 | 4.2879 | 3151.266 | 0 | 3.6 | 3151.266 | 3184.6959
DEER-SFAM-CZ10-V3-eSA-10-HL-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-HL | 8.8175 | 4.7325 | 3328.6161 | 0 | 3.6 | 3328.6161 | 3362.077
DEER-SFAM-CZ10-V3-eSA-10-HM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-HM | 8.8595 | 4.3343 | 3239.5522 | 0 | 3.6 | 3239.5522 | 3273.0072
DEER-SFAM-CZ10-V3-eSA-10-LH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-LH | 9.8744 | 4.1547 | 3084.7223 | 0 | 3.6 | 3084.7223 | 3118.215
DEER-SFAM-CZ10-V3-eSA-10-LL-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-LL | 9.1861 | 4.4035 | 3209.316 | 0 | 3.6 | 3209.316 | 3242.7843
DEER-SFAM-CZ10-V3-eSA-10-LM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-LM | 9.7765 | 4.1873 | 3088.5841 | 0 | 3.6 | 3088.5841 | 3122.0779
DEER-SFAM-CZ10-V3-eSA-10-MH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-MH | 9.7711 | 4.047 | 3086.736 | 0 | 3.6 | 3086.736 | 3120.2178
DEER-SFAM-CZ10-V3-eSA-10-ML-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-ML | 8.9613 | 4.5137 | 3295.0704 | 0 | 3.6 | 3295.0704 | 3328.5322
DEER-SFAM-CZ10-V3-eSA-10-MM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSA-10 | CZ10-V3-eSA-10-MM | 9.5268 | 4.153 | 3111.6291 | 0 | 3.6 | 3111.6291 | 3145.094
DEER-SFAM-CZ10-V3-eSA-13-HH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-HH | 11.7263 | 3.9423 | 2527.8974 | 0 | 4.1 | 2527.8974 | 2558.0945
DEER-SFAM-CZ10-V3-eSA-13-HL-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-HL | 11.6771 | 3.8801 | 2518.4887 | 0 | 3.6 | 2518.4887 | 2544.8863
DEER-SFAM-CZ10-V3-eSA-13-HM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-HM | 11.6661 | 3.9703 | 2508.9036 | 0 | 4.1 | 2508.9036 | 2539.0907
DEER-SFAM-CZ10-V3-eSA-13-LH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-LH | 12.5311 | 3.3102 | 2362.5008 | 0 | 3.6 | 2362.5008 | 2395.9712
DEER-SFAM-CZ10-V3-eSA-13-LL-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-LL | 11.9487 | 3.5834 | 2494.0377 | 0 | 3.6 | 2494.0377 | 2527.434
DEER-SFAM-CZ10-V3-eSA-13-LM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-LM | 11.9059 | 3.447 | 2482.9827 | 0 | 3.6 | 2482.9827 | 2516.422
DEER-SFAM-CZ10-V3-eSA-13-MH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-MH | 12.3044 | 3.819 | 2441.6056 | 0 | 4.1 | 2441.6056 | 2475.0999
DEER-SFAM-CZ10-V3-eSA-13-ML-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-ML | 11.566 | 3.6817 | 2465.0139 | 0 | 3.6 | 2465.0139 | 2498.3639
DEER-SFAM-CZ10-V3-eSA-13-MM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSA-13 | CZ10-V3-eSA-13-MM | 12.4398 | 3.8243 | 2379.9438 | 0 | 4.1 | 2379.9438 | 2413.4337
DEER-SFAM-CZ10-V3-eSA-14-HH-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-HH | 11.8193 | 3.532 | 2404.3085 | 0 | 3.6 | 2404.3085 | 2432.3462
DEER-SFAM-CZ10-V3-eSA-14-HL-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-HL | 12.6595 | 3.8238 | 2332.7402 | 0 | 4.1 | 2332.7402 | 2353.3831
DEER-SFAM-CZ10-V3-eSA-14-HM-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-HM | 12.4086 | 3.5611 | 2409.6667 | 0 | 3.6 | 2409.6667 | 2441.3022
DEER-SFAM-CZ10-V3-eSA-14-MH-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-MH | 12.7713 | 3.2093 | 2356.2148 | 0 | 3.6 | 2356.2148 | 2378.1945
DEER-SFAM-CZ10-V3-eSA-14-ML-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-ML | 12.4458 | 3.4896 | 2341.4247 | 0 | 3.6 | 2341.4247 | 2376.5313
DEER-SFAM-CZ10-V3-eSA-14-MM-s1 | 14 | CZ10 | V3 | CZ10-V3-eSA-14 | CZ10-V3-eSA-14-MM | 12.7227 | 3.2297 | 2316.261 | 0 | 3.6 | 2316.261 | 2340.3599
DEER-SFAM-CZ10-V3-eSA-15-HH-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-HH | 13.2668 | 3.4548 | 2200.2925 | 0 | 4.1 | 2200.2925 | 2223.6955
DEER-SFAM-CZ10-V3-eSA-15-HL-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-HL | 13.5822 | 3.5859 | 2159.7945 | 0 | 4.1 | 2159.7945 | 2188.9611
DEER-SFAM-CZ10-V3-eSA-15-HM-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-HM | 13.3673 | 3.3299 | 2173.5725 | 0 | 4.1 | 2173.5725 | 2197.0615
DEER-SFAM-CZ10-V3-eSA-15-MH-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-MH | 13.0567 | 3.3425 | 2231.0211 | 0 | 3.6 | 2231.0211 | 2248.44
DEER-SFAM-CZ10-V3-eSA-15-ML-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-ML | 13.6881 | 3.2351 | 2186.5697 | 0 | 3.6 | 2186.5697 | 2209.986
DEER-SFAM-CZ10-V3-eSA-15-MM-s1 | 15 | CZ10 | V3 | CZ10-V3-eSA-15 | CZ10-V3-eSA-15-MM | 13.5145 | 3.2618 | 2179.3544 | 0 | 3.6 | 2179.3544 | 2200.7128
DEER-SFAM-CZ10-V3-eSA-16-CH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-CH | 13.7945 | 3.4334 | 2405.2404 | 0 | 3.6 | 2405.2404 | 2418.6192
DEER-SFAM-CZ10-V3-eSA-16-CL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-CL | 14.2519 | 3.5579 | 2273.4656 | 0 | 4.1 | 2273.4656 | 2290.408
DEER-SFAM-CZ10-V3-eSA-16-CM-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-CM | 13.9057 | 3.6817 | 2355.8705 | 0 | 4.1 | 2355.8705 | 2373.7323
DEER-SFAM-CZ10-V3-eSA-16-LH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-LH | 14.0252 | 3.1639 | 2120.2486 | 0 | 3.6 | 2120.2486 | 2143.2447
DEER-SFAM-CZ10-V3-eSA-16-LL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-LL | 13.4626 | 3.4405 | 2242.2596 | 0 | 3.6 | 2242.2596 | 2257.4394
DEER-SFAM-CZ10-V3-eSA-16-LM-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-LM | 13.4818 | 3.3005 | 2233.2135 | 0 | 3.6 | 2233.2135 | 2246.9806
DEER-SFAM-CZ10-V3-eSA-16-NM-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-NM | 15.0923 | 3.0517 | 2008.7425 | 0 | 3.6 | 2008.7425 | 2022.2384
DEER-SFAM-CZ10-V3-eSA-16-TH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-TH | 13.3128 | 3.662 | 2470.1886 | 0 | 3.6 | 2470.1886 | 2478.8032
DEER-SFAM-CZ10-V3-eSA-16-TL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSA-16 | CZ10-V3-eSA-16-TL | 14.4157 | 3.6342 | 2245.9515 | 0 | 4.1 | 2245.9515 | 2255.3218
DEER-SFAM-CZ10-V3-eSA-17-CH-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-CH | 14.7202 | 3.5942 | 2247.4019 | 0 | 4.1 | 2247.4019 | 2264.3374
DEER-SFAM-CZ10-V3-eSA-17-CL-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-CL | 14.6976 | 3.5946 | 2232.4278 | 0 | 4.1 | 2232.4278 | 2249.3594
DEER-SFAM-CZ10-V3-eSA-17-CM-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-CM | 14.792 | 3.5996 | 2254.5629 | 0 | 4.1 | 2254.5629 | 2267.9253
DEER-SFAM-CZ10-V3-eSA-17-LH-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-LH | 14.3855 | 3.0854 | 2069.7151 | 0 | 3.6 | 2069.7151 | 2087.7447
DEER-SFAM-CZ10-V3-eSA-17-LL-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-LL | 14.1138 | 3.3025 | 2153.4347 | 0 | 3.6 | 2153.4347 | 2163.3218
DEER-SFAM-CZ10-V3-eSA-17-LM-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-LM | 14.0038 | 3.2257 | 2152.1707 | 0 | 3.6 | 2152.1707 | 2160.697
DEER-SFAM-CZ10-V3-eSA-17-TH-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-TH | 14.981 | 3.1173 | 2131.8622 | 0 | 3.6 | 2131.8622 | 2145.66
DEER-SFAM-CZ10-V3-eSA-17-TL-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-TL | 15.7619 | 3.3207 | 1983.9125 | 0 | 4.1 | 1983.9125 | 2005.4142
DEER-SFAM-CZ10-V3-eSA-17-TM-s2 | 17 | CZ10 | V3 | CZ10-V3-eSA-17 | CZ10-V3-eSA-17-TM | 15.5544 | 3.6294 | 2247.9362 | 0 | 4.1 | 2247.9362 | 2255.2235
DEER-SFAM-CZ10-V3-eSA-18-LH-s2 | 18 | CZ10 | V3 | CZ10-V3-eSA-18 | CZ10-V3-eSA-18-LH | 14.9867 | 3.0595 | 2012.3685 | 0 | 3.6 | 2012.3685 | 2024.2398
DEER-SFAM-CZ10-V3-eSA-18-LL-s2 | 18 | CZ10 | V3 | CZ10-V3-eSA-18 | CZ10-V3-eSA-18-LL | 15.1769 | 3.0105 | 1969.8966 | 0 | 3.6 | 1969.8966 | 1985.385
DEER-SFAM-CZ10-V3-eSA-18-TH-s2 | 18 | CZ10 | V3 | CZ10-V3-eSA-18 | CZ10-V3-eSA-18-TH | 15.7064 | 3.1703 | 2073.5179 | 0 | 4.1 | 2073.5179 | 2082.9305
DEER-SFAM-CZ10-V3-eSA-18-TL-s2 | 18 | CZ10 | V3 | CZ10-V3-eSA-18 | CZ10-V3-eSA-18-TL | 15.1621 | 3.7064 | 2225.1768 | 0 | 4.1 | 2225.1768 | 2235.4633
DEER-SFAM-CZ10-V3-eSA-18-TM-s2 | 18 | CZ10 | V3 | CZ10-V3-eSA-18 | CZ10-V3-eSA-18-TM | 15.1085 | 3.0235 | 2099.9203 | 0 | 3.6 | 2099.9203 | 2109.5075
DEER-SFAM-CZ10-V3-eSH-10-HH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-HH | 9.3466 | 4.6969 | 3141.1397 | 740.3911 | 4.1 | 3881.5308 | 3214.3308
DEER-SFAM-CZ10-V3-eSH-10-HL-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-HL | 9.0842 | 4.8582 | 3239.1334 | 742.8663 | 4.1 | 3981.9997 | 3310.8997
DEER-SFAM-CZ10-V3-eSH-10-HM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-HM | 9.6473 | 4.4889 | 3135.4711 | 729.6448 | 3.6 | 3865.1159 | 3204.3159
DEER-SFAM-CZ10-V3-eSH-10-LH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-LH | 9.8865 | 4.0524 | 3049.6727 | 764.8037 | 3.6 | 3814.4764 | 3124.8764
DEER-SFAM-CZ10-V3-eSH-10-LL-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-LL | 9.5903 | 4.3444 | 3111.4434 | 747.9518 | 3.6 | 3859.3952 | 3189.9952
DEER-SFAM-CZ10-V3-eSH-10-LM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-LM | 9.8594 | 4.2048 | 3036.8399 | 744.6394 | 3.6 | 3781.4793 | 3109.0793
DEER-SFAM-CZ10-V3-eSH-10-MH-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-MH | 9.875 | 4.2177 | 3076.6689 | 756.2387 | 3.6 | 3832.9076 | 3156.4076
DEER-SFAM-CZ10-V3-eSH-10-ML-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-ML | 9.5002 | 4.5864 | 3167.2327 | 709.1534 | 3.6 | 3876.3861 | 3240.3861
DEER-SFAM-CZ10-V3-eSH-10-MM-s1 | 10 | CZ10 | V3 | CZ10-V3-eSH-10 | CZ10-V3-eSH-10-MM | 9.6346 | 4.3594 | 3154.1519 | 741.1941 | 3.6 | 3895.346 | 3222.146
DEER-SFAM-CZ10-V3-eSH-13-HH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-HH | 11.1672 | 3.9666 | 2615.4751 | 713.3096 | 4.1 | 3328.7847 | 2682.2847
DEER-SFAM-CZ10-V3-eSH-13-HL-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-HL | 12.0501 | 4.1701 | 2482.6757 | 614.2108 | 4.1 | 3096.8865 | 2549.1865
DEER-SFAM-CZ10-V3-eSH-13-HM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-HM | 11.4756 | 3.9076 | 2552.7086 | 640.4513 | 4.1 | 3193.1599 | 2613.1599
DEER-SFAM-CZ10-V3-eSH-13-LH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-LH | 12.2952 | 3.3453 | 2416.4999 | 714.8987 | 3.6 | 3131.3986 | 2515.5986
DEER-SFAM-CZ10-V3-eSH-13-LL-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-LL | 12.8447 | 3.5092 | 2339.0956 | 640.6345 | 3.6 | 2979.7301 | 2400.2301
DEER-SFAM-CZ10-V3-eSH-13-LM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-LM | 11.6727 | 3.5262 | 2517.6261 | 558.2843 | 3.6 | 3075.9104 | 2586.7104
DEER-SFAM-CZ10-V3-eSH-13-MH-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-MH | 12.2198 | 3.787 | 2418.9825 | 721.8979 | 4.1 | 3140.8804 | 2485.5804
DEER-SFAM-CZ10-V3-eSH-13-ML-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-ML | 11.4766 | 3.7916 | 2581.3217 | 645.9308 | 3.6 | 3227.2525 | 2649.5525
DEER-SFAM-CZ10-V3-eSH-13-MM-s1 | 13 | CZ10 | V3 | CZ10-V3-eSH-13 | CZ10-V3-eSH-13-MM | 12.1536 | 3.741 | 2478.9063 | 665.7692 | 3.6 | 3144.6755 | 2532.2755
DEER-SFAM-CZ10-V3-eSH-14-HH-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-HH | 11.8362 | 3.7744 | 2469.2313 | 653.4146 | 4.1 | 3122.6459 | 2520.1459
DEER-SFAM-CZ10-V3-eSH-14-HL-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-HL | 12.2323 | 3.709 | 2386.4982 | 634.5331 | 4.1 | 3021.0313 | 2447.4313
DEER-SFAM-CZ10-V3-eSH-14-HM-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-HM | 12.1775 | 3.5737 | 2387.4627 | 637.2182 | 4.1 | 3024.6809 | 2431.0809
DEER-SFAM-CZ10-V3-eSH-14-MH-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-MH | 13.1237 | 3.1549 | 2255.1578 | 657.1841 | 3.6 | 2912.3419 | 2321.2419
DEER-SFAM-CZ10-V3-eSH-14-ML-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-ML | 12.99 | 3.6736 | 2281.1151 | 671.1881 | 4.1 | 2952.3032 | 2363.3032
DEER-SFAM-CZ10-V3-eSH-14-MM-s1 | 14 | CZ10 | V3 | CZ10-V3-eSH-14 | CZ10-V3-eSH-14-MM | 12.8617 | 3.3477 | 2281.2652 | 611.6522 | 3.6 | 2892.9174 | 2338.3174
DEER-SFAM-CZ10-V3-eSH-15-HH-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-HH | 13.0953 | 3.3056 | 2209.5313 | 714.0881 | 4.1 | 2923.6194 | 2256.6194
DEER-SFAM-CZ10-V3-eSH-15-HL-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-HL | 13.3947 | 3.5533 | 2213.5538 | 555.3732 | 4.1 | 2768.927 | 2260.327
DEER-SFAM-CZ10-V3-eSH-15-HM-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-HM | 13.6062 | 3.4835 | 2154.9202 | 580.9558 | 4.1 | 2735.876 | 2201.276
DEER-SFAM-CZ10-V3-eSH-15-MH-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-MH | 13.5484 | 3.2668 | 2200.5752 | 627.6527 | 3.6 | 2828.2279 | 2245.1279
DEER-SFAM-CZ10-V3-eSH-15-ML-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-ML | 13.8844 | 3.4887 | 2134.3401 | 599.6043 | 4.1 | 2733.9444 | 2180.8444
DEER-SFAM-CZ10-V3-eSH-15-MM-s1 | 15 | CZ10 | V3 | CZ10-V3-eSH-15 | CZ10-V3-eSH-15-MM | 13.8002 | 3.4605 | 2142.0527 | 649.0421 | 4.1 | 2791.0948 | 2191.7948
DEER-SFAM-CZ10-V3-eSH-16-CH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-CH | 14.0942 | 3.5155 | 2337.5901 | 629.1713 | 4.1 | 2966.7614 | 2376.7614
DEER-SFAM-CZ10-V3-eSH-16-CL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-CL | 14.2215 | 3.8043 | 2379.0002 | 588.385 | 4.1 | 2967.3852 | 2420.0852
DEER-SFAM-CZ10-V3-eSH-16-LH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-LH | 13.7508 | 3.1576 | 2155.3269 | 665.4383 | 3.6 | 2820.7652 | 2201.8652
DEER-SFAM-CZ10-V3-eSH-16-LL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-LL | 13.4118 | 3.3606 | 2237.0377 | 607.1588 | 3.6 | 2844.1965 | 2274.4965
DEER-SFAM-CZ10-V3-eSH-16-LM-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-LM | 13.324 | 3.2554 | 2234.2742 | 662.0988 | 3.6 | 2896.373 | 2286.273
DEER-SFAM-CZ10-V3-eSH-16-TH-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-TH | 14.4038 | 3.6497 | 2239.8333 | 777.0943 | 4.1 | 3016.9276 | 2275.9276
DEER-SFAM-CZ10-V3-eSH-16-TL-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-TL | 13.3847 | 3.7691 | 2478.8404 | 763.6551 | 3.6 | 3242.4955 | 2513.4955
DEER-SFAM-CZ10-V3-eSH-16-TM-s2 | 16 | CZ10 | V3 | CZ10-V3-eSH-16 | CZ10-V3-eSH-16-TM | 13.5645 | 3.6957 | 2446.2309 | 776.3604 | 3.6 | 3222.5913 | 2481.8913
DEER-SFAM-CZ10-V3-eSH-17-CM-s2 | 17 | CZ10 | V3 | CZ10-V3-eSH-17 | CZ10-V3-eSH-17-CM | 14.9983 | 3.6222 | 2252.9576 | 610.9645 | 4.1 | 2863.9221 | 2296.1221
DEER-SFAM-CZ10-V3-eSH-17-LM-s2 | 17 | CZ10 | V3 | CZ10-V3-eSH-17 | CZ10-V3-eSH-17-LM | 14.1026 | 3.2552 | 2187.5344 | 591.1488 | 3.6 | 2778.6832 | 2208.5832
DEER-SFAM-CZ10-V3-eSH-17-TH-s2 | 17 | CZ10 | V3 | CZ10-V3-eSH-17 | CZ10-V3-eSH-17-TH | 15.0459 | 3.4395 | 2137.1168 | 775.442 | 4.1 | 2912.5588 | 2175.6588
DEER-SFAM-CZ10-V3-eSH-17-TL-s2 | 17 | CZ10 | V3 | CZ10-V3-eSH-17 | CZ10-V3-eSH-17-TL | 15.0162 | 3.5114 | 2149.3089 | 764.5893 | 4.1 | 2913.8982 | 2187.3982
DEER-SFAM-CZ10-V3-eSH-18-LH-s2 | 18 | CZ10 | V3 | CZ10-V3-eSH-18 | CZ10-V3-eSH-18-LH | 14.815 | 3.0383 | 2026.9488 | 657.8563 | 3.6 | 2684.8051 | 2060.5051
DEER-SFAM-CZ10-V3-eSH-18-LL-s2 | 18 | CZ10 | V3 | CZ10-V3-eSH-18 | CZ10-V3-eSH-18-LL | 14.1764 | 3.1265 | 2106.3057 | 602.8029 | 3.6 | 2709.1086 | 2138.5086
DEER-SFAM-CZ10-V3-eSH-18-LM-s2 | 18 | CZ10 | V3 | CZ10-V3-eSH-18 | CZ10-V3-eSH-18-LM | 14.8853 | 3.0897 | 2031.8843 | 685.3469 | 3.6 | 2717.2312 | 2070.0312
DEER-SFAM-CZ10-V3-eSH-18-TM-s2 | 18 | CZ10 | V3 | CZ10-V3-eSH-18 | CZ10-V3-eSH-18-TM | 15.4706 | 3.1776 | 2099.7173 | 764.3757 | 3.6 | 2864.093 | 2161.693
DEER-SFAM-CZ10-V4-eSA-10-HH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-HH | 9.3439 | 4.7632 | 3299.3495 | 0 | 4.1 | 3299.3495 | 3325.6981
DEER-SFAM-CZ10-V4-eSA-10-HL-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-HL | 8.7395 | 5.5316 | 3488.8886 | 0 | 4.5 | 3488.8886 | 3515.2799
DEER-SFAM-CZ10-V4-eSA-10-HM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-HM | 8.7656 | 5.1206 | 3401.5111 | 0 | 4.5 | 3401.5111 | 3427.8983
DEER-SFAM-CZ10-V4-eSA-10-LH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-LH | 9.8062 | 4.6203 | 3228.3374 | 0 | 4.1 | 3228.3374 | 3254.7345
DEER-SFAM-CZ10-V4-eSA-10-LL-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-LL | 9.1181 | 5.1395 | 3358.2235 | 0 | 4.5 | 3358.2235 | 3384.6198
DEER-SFAM-CZ10-V4-eSA-10-LM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-LM | 9.7168 | 4.6576 | 3229.6311 | 0 | 4.1 | 3229.6311 | 3256.0292
DEER-SFAM-CZ10-V4-eSA-10-MH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-MH | 9.6666 | 4.5091 | 3242.9421 | 0 | 4.1 | 3242.9421 | 3269.3312
DEER-SFAM-CZ10-V4-eSA-10-ML-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-ML | 8.9397 | 5.0385 | 3433.9969 | 0 | 4.1 | 3433.9969 | 3460.3707
DEER-SFAM-CZ10-V4-eSA-10-MM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSA-10 | CZ10-V4-eSA-10-MM | 9.4667 | 4.6399 | 3253.9539 | 0 | 4.1 | 3253.9539 | 3280.3301
DEER-SFAM-CZ10-V4-eSA-13-HH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-HH | 11.7106 | 4.2318 | 2629.2442 | 0 | 4.5 | 2629.2442 | 2653.034
DEER-SFAM-CZ10-V4-eSA-13-HL-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-HL | 11.5873 | 4.476 | 2634.9455 | 0 | 4.5 | 2634.9455 | 2655.7662
DEER-SFAM-CZ10-V4-eSA-13-HM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-HM | 11.6804 | 4.252 | 2606.013 | 0 | 4.5 | 2606.013 | 2629.7945
DEER-SFAM-CZ10-V4-eSA-13-LH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-LH | 12.2974 | 3.8503 | 2499.7288 | 0 | 4.5 | 2499.7288 | 2526.1266
DEER-SFAM-CZ10-V4-eSA-13-LL-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-LL | 11.9094 | 3.9704 | 2599.0747 | 0 | 4.1 | 2599.0747 | 2625.3974
DEER-SFAM-CZ10-V4-eSA-13-LM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-LM | 11.8261 | 3.8295 | 2599.236 | 0 | 4.1 | 2599.236 | 2625.592
DEER-SFAM-CZ10-V4-eSA-13-MH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-MH | 12.2918 | 4.1085 | 2544.1433 | 0 | 4.5 | 2544.1433 | 2570.5309
DEER-SFAM-CZ10-V4-eSA-13-ML-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-ML | 11.5303 | 4.0584 | 2569.916 | 0 | 4.1 | 2569.916 | 2596.2023
DEER-SFAM-CZ10-V4-eSA-13-MM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSA-13 | CZ10-V4-eSA-13-MM | 12.4228 | 4.067 | 2479.4576 | 0 | 4.5 | 2479.4576 | 2505.8412
DEER-SFAM-CZ10-V4-eSA-14-HH-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-HH | 11.7544 | 3.9015 | 2512.7907 | 0 | 4.1 | 2512.7907 | 2534.8898
DEER-SFAM-CZ10-V4-eSA-14-HL-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-HL | 12.6843 | 4.0773 | 2423.4481 | 0 | 4.5 | 2423.4481 | 2439.7111
DEER-SFAM-CZ10-V4-eSA-14-HM-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-HM | 12.2856 | 4.1271 | 2526.6439 | 0 | 4.5 | 2526.6439 | 2551.5946
DEER-SFAM-CZ10-V4-eSA-14-MH-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-MH | 12.6718 | 3.5711 | 2469.1298 | 0 | 4.1 | 2469.1298 | 2486.4541
DEER-SFAM-CZ10-V4-eSA-14-ML-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-ML | 12.3182 | 4.0456 | 2456.8616 | 0 | 4.5 | 2456.8616 | 2484.5513
DEER-SFAM-CZ10-V4-eSA-14-MM-s1 | 14 | CZ10 | V4 | CZ10-V4-eSA-14 | CZ10-V4-eSA-14-MM | 12.6308 | 3.5961 | 2424.6073 | 0 | 4.1 | 2424.6073 | 2443.6019
DEER-SFAM-CZ10-V4-eSA-15-HH-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-HH | 13.2535 | 3.706 | 2289.814 | 0 | 4.5 | 2289.814 | 2308.2516
DEER-SFAM-CZ10-V4-eSA-15-HL-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-HL | 13.63 | 3.8197 | 2239.9681 | 0 | 4.5 | 2239.9681 | 2262.9456
DEER-SFAM-CZ10-V4-eSA-15-HM-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-HM | 13.3513 | 3.5708 | 2260.5414 | 0 | 4.5 | 2260.5414 | 2279.0469
DEER-SFAM-CZ10-V4-eSA-15-MH-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-MH | 12.9655 | 3.7004 | 2334.9946 | 0 | 4.1 | 2334.9946 | 2348.724
DEER-SFAM-CZ10-V4-eSA-15-ML-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-ML | 13.6513 | 3.5685 | 2277.342 | 0 | 4.1 | 2277.342 | 2295.7987
DEER-SFAM-CZ10-V4-eSA-15-MM-s1 | 15 | CZ10 | V4 | CZ10-V4-eSA-15 | CZ10-V4-eSA-15-MM | 13.3684 | 3.7534 | 2287.9674 | 0 | 4.5 | 2287.9674 | 2304.8131
DEER-SFAM-CZ10-V4-eSA-16-CH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-CH | 13.9449 | 4.024 | 2519.8032 | 0 | 4.5 | 2519.8032 | 2530.3796
DEER-SFAM-CZ10-V4-eSA-16-CL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-CL | 14.3165 | 3.8002 | 2369.5275 | 0 | 4.5 | 2369.5275 | 2382.8985
DEER-SFAM-CZ10-V4-eSA-16-CM-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-CM | 13.9581 | 3.9316 | 2458.1499 | 0 | 4.5 | 2458.1499 | 2472.2484
DEER-SFAM-CZ10-V4-eSA-16-LH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-LH | 13.9702 | 3.4938 | 2220.6185 | 0 | 4.1 | 2220.6185 | 2238.7618
DEER-SFAM-CZ10-V4-eSA-16-LL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-LL | 13.4548 | 3.7774 | 2338.0044 | 0 | 4.1 | 2338.0044 | 2349.973
DEER-SFAM-CZ10-V4-eSA-16-LM-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-LM | 13.4605 | 3.6323 | 2331.9897 | 0 | 4.1 | 2331.9897 | 2342.8453
DEER-SFAM-CZ10-V4-eSA-16-NM-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-NM | 15.1868 | 3.3514 | 2084.8515 | 0 | 4.1 | 2084.8515 | 2095.494
DEER-SFAM-CZ10-V4-eSA-16-TH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-TH | 13.3719 | 4.0491 | 2594.936 | 0 | 4.1 | 2594.936 | 2601.736
DEER-SFAM-CZ10-V4-eSA-16-TL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSA-16 | CZ10-V4-eSA-16-TL | 14.4624 | 3.8915 | 2340.2041 | 0 | 4.5 | 2340.2041 | 2347.5918
DEER-SFAM-CZ10-V4-eSA-17-CH-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-CH | 14.7854 | 3.8482 | 2337.8401 | 0 | 4.5 | 2337.8401 | 2351.2061
DEER-SFAM-CZ10-V4-eSA-17-CL-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-CL | 14.7782 | 3.8397 | 2320.6857 | 0 | 4.5 | 2320.6857 | 2334.0483
DEER-SFAM-CZ10-V4-eSA-17-CM-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-CM | 14.8715 | 3.8486 | 2344.2249 | 0 | 4.5 | 2344.2249 | 2354.77
DEER-SFAM-CZ10-V4-eSA-17-LH-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-LH | 14.3526 | 3.4001 | 2162.9825 | 0 | 4.1 | 2162.9825 | 2177.2038
DEER-SFAM-CZ10-V4-eSA-17-LL-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-LL | 14.1151 | 3.628 | 2244.0746 | 0 | 4.1 | 2244.0746 | 2251.8703
DEER-SFAM-CZ10-V4-eSA-17-LM-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-LM | 13.9904 | 3.5474 | 2245.5852 | 0 | 4.1 | 2245.5852 | 2252.3077
DEER-SFAM-CZ10-V4-eSA-17-TH-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-TH | 14.9052 | 3.6295 | 2273.7858 | 0 | 4.5 | 2273.7858 | 2284.6815
DEER-SFAM-CZ10-V4-eSA-17-TL-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-TL | 15.8891 | 3.5563 | 2060.7398 | 0 | 4.5 | 2060.7398 | 2077.7133
DEER-SFAM-CZ10-V4-eSA-17-TM-s2 | 17 | CZ10 | V4 | CZ10-V4-eSA-17 | CZ10-V4-eSA-17-TM | 15.5783 | 3.892 | 2347.2388 | 0 | 4.5 | 2347.2388 | 2352.9846
DEER-SFAM-CZ10-V4-eSA-18-LH-s2 | 18 | CZ10 | V4 | CZ10-V4-eSA-18 | CZ10-V4-eSA-18-LH | 14.9563 | 3.36 | 2102.0936 | 0 | 4.1 | 2102.0936 | 2111.4541
DEER-SFAM-CZ10-V4-eSA-18-LL-s2 | 18 | CZ10 | V4 | CZ10-V4-eSA-18 | CZ10-V4-eSA-18-LL | 15.2017 | 3.3269 | 2051.9194 | 0 | 4.1 | 2051.9194 | 2064.1317
DEER-SFAM-CZ10-V4-eSA-18-TH-s2 | 18 | CZ10 | V4 | CZ10-V4-eSA-18 | CZ10-V4-eSA-18-TH | 15.6667 | 3.3957 | 2173.9932 | 0 | 4.5 | 2173.9932 | 2181.4133
DEER-SFAM-CZ10-V4-eSA-18-TL-s2 | 18 | CZ10 | V4 | CZ10-V4-eSA-18 | CZ10-V4-eSA-18-TL | 15.2063 | 3.9592 | 2322.6864 | 0 | 4.5 | 2322.6864 | 2330.803
DEER-SFAM-CZ10-V4-eSA-18-TM-s2 | 18 | CZ10 | V4 | CZ10-V4-eSA-18 | CZ10-V4-eSA-18-TM | 15.1091 | 3.3509 | 2209.621 | 0 | 4.1 | 2209.621 | 2217.184
DEER-SFAM-CZ10-V4-eSH-10-HH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-HH | 9.3372 | 5.0362 | 3274.4332 | 595.3154 | 4.5 | 3869.7486 | 3332.7486
DEER-SFAM-CZ10-V4-eSH-10-HL-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-HL | 9.0872 | 5.2184 | 3369.5711 | 595.386 | 4.5 | 3964.9571 | 3426.6571
DEER-SFAM-CZ10-V4-eSH-10-HM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-HM | 9.5854 | 4.9923 | 3280.9139 | 587.5456 | 4.1 | 3868.4595 | 3335.7595
DEER-SFAM-CZ10-V4-eSH-10-LH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-LH | 9.7847 | 4.5042 | 3204.8314 | 618.5223 | 4.1 | 3823.3537 | 3264.7537
DEER-SFAM-CZ10-V4-eSH-10-LL-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-LL | 9.4796 | 5.0825 | 3272.4928 | 604.7932 | 4.5 | 3877.286 | 3335.186
DEER-SFAM-CZ10-V4-eSH-10-LM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-LM | 9.6868 | 4.9043 | 3211.9522 | 605.1368 | 4.5 | 3817.089 | 3269.589
DEER-SFAM-CZ10-V4-eSH-10-MH-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-MH | 9.7932 | 4.6853 | 3224.6477 | 610.3359 | 4.1 | 3834.9836 | 3288.1836
DEER-SFAM-CZ10-V4-eSH-10-ML-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-ML | 9.4114 | 5.3635 | 3322.176 | 573.1329 | 4.5 | 3895.3089 | 3380.6089
DEER-SFAM-CZ10-V4-eSH-10-MM-s1 | 10 | CZ10 | V4 | CZ10-V4-eSH-10 | CZ10-V4-eSH-10-MM | 9.5769 | 4.8397 | 3296.6066 | 596.6557 | 4.1 | 3893.2623 | 3350.7623
DEER-SFAM-CZ10-V4-eSH-13-HH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-HH | 11.1443 | 4.2596 | 2723.6917 | 573.4286 | 4.5 | 3297.1203 | 2776.9203
DEER-SFAM-CZ10-V4-eSH-13-HL-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-HL | 12.0898 | 4.4556 | 2575.8567 | 491.8973 | 4.5 | 3067.754 | 2628.854
DEER-SFAM-CZ10-V4-eSH-13-HM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-HM | 11.4608 | 4.1933 | 2659.1651 | 513.9738 | 4.5 | 3173.1389 | 2707.3389
DEER-SFAM-CZ10-V4-eSH-13-LH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-LH | 12.1876 | 3.7172 | 2533.0119 | 577.7283 | 4.1 | 3110.7402 | 2612.0402
DEER-SFAM-CZ10-V4-eSH-13-LL-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-LL | 12.6901 | 4.0852 | 2461.3577 | 517.4977 | 4.5 | 2978.8554 | 2510.1554
DEER-SFAM-CZ10-V4-eSH-13-LM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-LM | 11.6033 | 3.9171 | 2631.5636 | 448.5924 | 4.1 | 3080.156 | 2686.556
DEER-SFAM-CZ10-V4-eSH-13-MH-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-MH | 12.2194 | 4.0554 | 2518.4939 | 582.0094 | 4.5 | 3100.5033 | 2571.5033
DEER-SFAM-CZ10-V4-eSH-13-ML-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-ML | 11.4411 | 4.2046 | 2690.1531 | 519.0512 | 4.1 | 3209.2043 | 2744.5043
DEER-SFAM-CZ10-V4-eSH-13-MM-s1 | 13 | CZ10 | V4 | CZ10-V4-eSH-13 | CZ10-V4-eSH-13-MM | 12.0141 | 4.3159 | 2608.7241 | 537.0991 | 4.5 | 3145.8232 | 2651.2232
DEER-SFAM-CZ10-V4-eSH-14-HH-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-HH | 11.8244 | 4.0505 | 2571.0807 | 524.3631 | 4.5 | 3095.4438 | 2611.6438
DEER-SFAM-CZ10-V4-eSH-14-HL-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-HL | 12.2473 | 3.9754 | 2479.4392 | 508.4497 | 4.5 | 2987.8889 | 2527.9889
DEER-SFAM-CZ10-V4-eSH-14-HM-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-HM | 12.1663 | 3.8322 | 2485.2958 | 512.9689 | 4.5 | 2998.2647 | 2520.0647
DEER-SFAM-CZ10-V4-eSH-14-MH-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-MH | 13.0123 | 3.5027 | 2364.0837 | 531.823 | 4.1 | 2895.9067 | 2416.8067
DEER-SFAM-CZ10-V4-eSH-14-ML-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-ML | 12.9949 | 3.9096 | 2372.1689 | 539.275 | 4.5 | 2911.4439 | 2437.7439
DEER-SFAM-CZ10-V4-eSH-14-MM-s1 | 14 | CZ10 | V4 | CZ10-V4-eSH-14 | CZ10-V4-eSH-14-MM | 12.7192 | 3.8765 | 2396.0339 | 493.9921 | 4.5 | 2890.026 | 2441.526
DEER-SFAM-CZ10-V4-eSH-15-HH-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-HH | 13.0717 | 3.5458 | 2301.2592 | 574.2519 | 4.5 | 2875.5111 | 2338.8111
DEER-SFAM-CZ10-V4-eSH-15-HL-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-HL | 13.3973 | 3.8003 | 2301.6241 | 445.2477 | 4.5 | 2746.8718 | 2338.8718
DEER-SFAM-CZ10-V4-eSH-15-HM-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-HM | 13.6425 | 3.7143 | 2236.828 | 465.7137 | 4.5 | 2702.5417 | 2273.7417
DEER-SFAM-CZ10-V4-eSH-15-MH-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-MH | 13.3665 | 3.7534 | 2316.1333 | 507.4542 | 4.5 | 2823.5875 | 2351.6875
DEER-SFAM-CZ10-V4-eSH-15-ML-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-ML | 13.8936 | 3.6962 | 2217.9923 | 482.1923 | 4.5 | 2700.1846 | 2255.0846
DEER-SFAM-CZ10-V4-eSH-15-MM-s1 | 15 | CZ10 | V4 | CZ10-V4-eSH-15 | CZ10-V4-eSH-15-MM | 13.8476 | 3.7025 | 2222.5202 | 522.1555 | 4.5 | 2744.6757 | 2262.1757
DEER-SFAM-CZ10-V4-eSH-16-CH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-CH | 14.1432 | 3.7676 | 2436.245 | 504.1194 | 4.5 | 2940.3644 | 2467.5644
DEER-SFAM-CZ10-V4-eSH-16-CL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-CL | 14.291 | 4.0784 | 2474.8906 | 470.1672 | 4.5 | 2945.0578 | 2507.7578
DEER-SFAM-CZ10-V4-eSH-16-LH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-LH | 13.634 | 3.4888 | 2266.2805 | 537.7338 | 4.1 | 2804.0143 | 2303.4143
DEER-SFAM-CZ10-V4-eSH-16-LL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-LL | 13.4136 | 3.7041 | 2332.6181 | 486.8963 | 4.1 | 2819.5144 | 2362.5144
DEER-SFAM-CZ10-V4-eSH-16-LM-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-LM | 13.2466 | 3.5986 | 2343.1677 | 534 | 4.1 | 2877.1677 | 2384.6677
DEER-SFAM-CZ10-V4-eSH-16-TH-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-TH | 14.3896 | 3.8916 | 2344.4132 | 625.2704 | 4.5 | 2969.6836 | 2373.1836
DEER-SFAM-CZ10-V4-eSH-16-TL-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-TL | 13.6137 | 4.345 | 2595.4056 | 605.7832 | 4.5 | 3201.1888 | 2620.4888
DEER-SFAM-CZ10-V4-eSH-16-TM-s2 | 16 | CZ10 | V4 | CZ10-V4-eSH-16 | CZ10-V4-eSH-16-TM | 13.7636 | 4.2687 | 2567.4297 | 617.9526 | 4.5 | 3185.3823 | 2593.0823
DEER-SFAM-CZ10-V4-eSH-17-CM-s2 | 17 | CZ10 | V4 | CZ10-V4-eSH-17 | CZ10-V4-eSH-17-CM | 15.0694 | 3.8846 | 2344.1165 | 487.0335 | 4.5 | 2831.15 | 2378.55
DEER-SFAM-CZ10-V4-eSH-17-LM-s2 | 17 | CZ10 | V4 | CZ10-V4-eSH-17 | CZ10-V4-eSH-17-LM | 14.0372 | 3.6405 | 2291.3053 | 474.9941 | 4.1 | 2766.2994 | 2308.0994
DEER-SFAM-CZ10-V4-eSH-17-TH-s2 | 17 | CZ10 | V4 | CZ10-V4-eSH-17 | CZ10-V4-eSH-17-TH | 15.0585 | 3.6783 | 2233.6906 | 623.8742 | 4.5 | 2857.5648 | 2264.2648
DEER-SFAM-CZ10-V4-eSH-17-TL-s2 | 17 | CZ10 | V4 | CZ10-V4-eSH-17 | CZ10-V4-eSH-17-TL | 15.0419 | 3.746 | 2243.9149 | 614.5781 | 4.5 | 2858.493 | 2274.193
DEER-SFAM-CZ10-V4-eSH-18-LH-s2 | 18 | CZ10 | V4 | CZ10-V4-eSH-18 | CZ10-V4-eSH-18-LH | 14.8011 | 3.3613 | 2116.0447 | 524.1878 | 4.1 | 2640.2325 | 2142.7325
DEER-SFAM-CZ10-V4-eSH-18-LL-s2 | 18 | CZ10 | V4 | CZ10-V4-eSH-18 | CZ10-V4-eSH-18-LL | 14.1676 | 3.4602 | 2197.3777 | 482.4973 | 4.1 | 2679.875 | 2223.075
DEER-SFAM-CZ10-V4-eSH-18-LM-s2 | 18 | CZ10 | V4 | CZ10-V4-eSH-18 | CZ10-V4-eSH-18-LM | 14.8744 | 3.4068 | 2119.7607 | 544.5907 | 4.1 | 2664.3514 | 2150.0514
DEER-SFAM-CZ10-V4-eSH-18-TM-s2 | 18 | CZ10 | V4 | CZ10-V4-eSH-18 | CZ10-V4-eSH-18-TM | 15.5967 | 3.511 | 2194.67 | 613.0126 | 4.1 | 2807.6826 | 2240.7826
DEER-SFAM-CZ11-V1-eSA-10-HH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-HH | 9.197 | 4.1222 | 3041.2074 | 0 | 3.5124 | 3041.2074 | 3272.8241
DEER-SFAM-CZ11-V1-eSA-10-HL-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-HL | 8.6359 | 4.6184 | 3198.7849 | 0 | 3.5124 | 3198.7849 | 3430.5569
DEER-SFAM-CZ11-V1-eSA-10-HM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-HM | 8.6908 | 4.4144 | 3113.6638 | 0 | 3.5124 | 3113.6638 | 3345.4064
DEER-SFAM-CZ11-V1-eSA-10-LH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-LH | 9.8251 | 4.0088 | 2998.0151 | 0 | 3.5124 | 2998.0151 | 3229.9433
DEER-SFAM-CZ11-V1-eSA-10-LL-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-LL | 9.0895 | 4.2629 | 3059.4397 | 0 | 3.5124 | 3059.4397 | 3291.2452
DEER-SFAM-CZ11-V1-eSA-10-LM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-LM | 9.6419 | 4.0476 | 3004.0686 | 0 | 3.5124 | 3004.0686 | 3236.0042
DEER-SFAM-CZ11-V1-eSA-10-MH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-MH | 9.6479 | 3.9011 | 2994.3971 | 0 | 3.5124 | 2994.3971 | 3226.2707
DEER-SFAM-CZ11-V1-eSA-10-ML-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-ML | 8.843 | 4.3532 | 3149.2325 | 0 | 3.5124 | 3149.2325 | 3381.0073
DEER-SFAM-CZ11-V1-eSA-10-MM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSA-10 | CZ11-V1-eSA-10-MM | 9.2268 | 4.0597 | 3024.747 | 0 | 3.5124 | 3024.747 | 3256.5366
DEER-SFAM-CZ11-V1-eSA-13-HH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-HH | 11.8892 | 3.4566 | 2387.0841 | 0 | 3.5124 | 2387.0841 | 2596.0002
DEER-SFAM-CZ11-V1-eSA-13-HL-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-HL | 11.2697 | 3.6898 | 2457.9611 | 0 | 3.5124 | 2457.9611 | 2640.807
DEER-SFAM-CZ11-V1-eSA-13-HM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-HM | 11.5756 | 3.5491 | 2383.3093 | 0 | 3.5124 | 2383.3093 | 2592.166
DEER-SFAM-CZ11-V1-eSA-13-LH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-LH | 12.2298 | 3.1561 | 2294.2375 | 0 | 3.5124 | 2294.2375 | 2526.0537
DEER-SFAM-CZ11-V1-eSA-13-LL-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-LL | 11.7308 | 3.4122 | 2406.9325 | 0 | 3.5124 | 2406.9325 | 2638.3833
DEER-SFAM-CZ11-V1-eSA-13-LM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-LM | 11.618 | 3.2842 | 2402.2667 | 0 | 3.5124 | 2402.2667 | 2633.9308
DEER-SFAM-CZ11-V1-eSA-13-MH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-MH | 12.3031 | 3.3481 | 2349.948 | 0 | 3.5124 | 2349.948 | 2581.6922
DEER-SFAM-CZ11-V1-eSA-13-ML-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-ML | 11.0744 | 3.5008 | 2405.8327 | 0 | 3.5124 | 2405.8327 | 2636.874
DEER-SFAM-CZ11-V1-eSA-13-MM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSA-13 | CZ11-V1-eSA-13-MM | 12.1449 | 3.3862 | 2305.4261 | 0 | 3.5124 | 2305.4261 | 2537.143
DEER-SFAM-CZ11-V1-eSA-14-HH-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-HH | 11.3562 | 3.3497 | 2341.5218 | 0 | 3.5124 | 2341.5218 | 2535.7493
DEER-SFAM-CZ11-V1-eSA-14-HL-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-HL | 12.6795 | 3.3509 | 2248.2034 | 0 | 3.5124 | 2248.2034 | 2391.0204
DEER-SFAM-CZ11-V1-eSA-14-HM-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-HM | 12.1758 | 3.4305 | 2359.5504 | 0 | 3.5124 | 2359.5504 | 2578.6568
DEER-SFAM-CZ11-V1-eSA-14-MH-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-MH | 12.6513 | 3.0521 | 2268.5226 | 0 | 3.5124 | 2268.5226 | 2420.7981
DEER-SFAM-CZ11-V1-eSA-14-ML-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-ML | 12.0172 | 3.3155 | 2280.7005 | 0 | 3.5124 | 2280.7005 | 2523.8841
DEER-SFAM-CZ11-V1-eSA-14-MM-s1 | 14 | CZ11 | V1 | CZ11-V1-eSA-14 | CZ11-V1-eSA-14-MM | 12.4168 | 3.085 | 2241.4939 | 0 | 3.5124 | 2241.4939 | 2408.4292
DEER-SFAM-CZ11-V1-eSA-15-HH-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-HH | 13.2232 | 3.0921 | 2084.1975 | 0 | 3.5124 | 2084.1975 | 2246.1031
DEER-SFAM-CZ11-V1-eSA-15-HL-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-HL | 13.6635 | 3.1459 | 2059.6849 | 0 | 3.5124 | 2059.6849 | 2261.4982
DEER-SFAM-CZ11-V1-eSA-15-HM-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-HM | 13.3342 | 3.0245 | 2054.8501 | 0 | 3.5124 | 2054.8501 | 2217.3595
DEER-SFAM-CZ11-V1-eSA-15-MH-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-MH | 12.6182 | 3.179 | 2184.8583 | 0 | 3.5124 | 2184.8583 | 2305.4948
DEER-SFAM-CZ11-V1-eSA-15-ML-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-ML | 13.4504 | 3.0758 | 2117.6677 | 0 | 3.5124 | 2117.6677 | 2279.9526
DEER-SFAM-CZ11-V1-eSA-15-MM-s1 | 15 | CZ11 | V1 | CZ11-V1-eSA-15 | CZ11-V1-eSA-15-MM | 13.1613 | 3.1322 | 2128.6411 | 0 | 3.5124 | 2128.6411 | 2276.5714
DEER-SFAM-CZ11-V1-eSA-16-CH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-CH | 13.6326 | 3.308 | 2478.0657 | 0 | 3.5124 | 2478.0657 | 2570.0637
DEER-SFAM-CZ11-V1-eSA-16-CL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-CL | 13.8109 | 3.3449 | 2321.4133 | 0 | 3.5124 | 2321.4133 | 2438.5389
DEER-SFAM-CZ11-V1-eSA-16-CM-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-CM | 13.5709 | 3.3285 | 2395.0949 | 0 | 3.5124 | 2395.0949 | 2518.8322
DEER-SFAM-CZ11-V1-eSA-16-LH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-LH | 13.6887 | 3.1065 | 2094.6759 | 0 | 3.5124 | 2094.6759 | 2253.1691
DEER-SFAM-CZ11-V1-eSA-16-LL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-LL | 13.1139 | 3.3329 | 2229.0913 | 0 | 3.5124 | 2229.0913 | 2333.3236
DEER-SFAM-CZ11-V1-eSA-16-LM-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-LM | 13.17 | 3.2155 | 2215.037 | 0 | 3.5124 | 2215.037 | 2309.4931
DEER-SFAM-CZ11-V1-eSA-16-NM-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-NM | 14.6385 | 3.0344 | 2005.7289 | 0 | 3.5124 | 2005.7289 | 2098.3286
DEER-SFAM-CZ11-V1-eSA-16-TH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-TH | 12.9349 | 3.5951 | 2591.4021 | 0 | 3.5124 | 2591.4021 | 2649.8825
DEER-SFAM-CZ11-V1-eSA-16-TL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSA-16 | CZ11-V1-eSA-16-TL | 13.8171 | 3.5035 | 2327.7586 | 0 | 3.5124 | 2327.7586 | 2391.0689
DEER-SFAM-CZ11-V1-eSA-17-CH-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-CH | 14.3806 | 3.1758 | 2289.4938 | 0 | 3.5124 | 2289.4938 | 2406.5323
DEER-SFAM-CZ11-V1-eSA-17-CL-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-CL | 14.2602 | 3.2155 | 2278.4824 | 0 | 3.5124 | 2278.4824 | 2395.4971
DEER-SFAM-CZ11-V1-eSA-17-CM-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-CM | 14.3823 | 3.2035 | 2312.079 | 0 | 3.5124 | 2312.079 | 2403.8012
DEER-SFAM-CZ11-V1-eSA-17-LH-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-LH | 13.9981 | 3.0427 | 2052.3118 | 0 | 3.5124 | 2052.3118 | 2176.591
DEER-SFAM-CZ11-V1-eSA-17-LL-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-LL | 13.727 | 3.2077 | 2153.8497 | 0 | 3.5124 | 2153.8497 | 2221.6273
DEER-SFAM-CZ11-V1-eSA-17-LM-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-LM | 13.6154 | 3.1787 | 2142.0656 | 0 | 3.5124 | 2142.0656 | 2200.5679
DEER-SFAM-CZ11-V1-eSA-17-TH-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-TH | 14.6714 | 3.0887 | 2184.4973 | 0 | 3.5124 | 2184.4973 | 2278.396
DEER-SFAM-CZ11-V1-eSA-17-TL-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-TL | 14.9916 | 3.3183 | 2026.0899 | 0 | 3.5124 | 2026.0899 | 2174.1581
DEER-SFAM-CZ11-V1-eSA-17-TM-s2 | 17 | CZ11 | V1 | CZ11-V1-eSA-17 | CZ11-V1-eSA-17-TM | 15.1077 | 3.2286 | 2395.2874 | 0 | 3.5124 | 2395.2874 | 2444.1031
DEER-SFAM-CZ11-V1-eSA-18-LH-s2 | 18 | CZ11 | V1 | CZ11-V1-eSA-18 | CZ11-V1-eSA-18-LH | 14.5814 | 2.9638 | 2004.8886 | 0 | 3.5124 | 2004.8886 | 2086.3452
DEER-SFAM-CZ11-V1-eSA-18-LL-s2 | 18 | CZ11 | V1 | CZ11-V1-eSA-18 | CZ11-V1-eSA-18-LL | 14.7592 | 2.9801 | 1961.2938 | 0 | 3.5124 | 1961.2938 | 2067.5866
DEER-SFAM-CZ11-V1-eSA-18-TH-s2 | 18 | CZ11 | V1 | CZ11-V1-eSA-18 | CZ11-V1-eSA-18-TH | 15.4253 | 2.9477 | 2091.9708 | 0 | 3.5124 | 2091.9708 | 2155.8634
DEER-SFAM-CZ11-V1-eSA-18-TL-s2 | 18 | CZ11 | V1 | CZ11-V1-eSA-18 | CZ11-V1-eSA-18-TL | 14.7688 | 3.2489 | 2298.6522 | 0 | 3.5124 | 2298.6522 | 2368.7062
DEER-SFAM-CZ11-V1-eSA-18-TM-s2 | 18 | CZ11 | V1 | CZ11-V1-eSA-18 | CZ11-V1-eSA-18-TM | 14.7249 | 3.043 | 2160.6207 | 0 | 3.5124 | 2160.6207 | 2225.8729
DEER-SFAM-CZ11-V1-eSH-10-HH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-HH | 9.5961 | 4.1302 | 2950.9303 | 5447.5607 | 3.5124 | 8398.4911 | 3501.8214
DEER-SFAM-CZ11-V1-eSH-10-HL-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-HL | 9.2515 | 4.3488 | 3059.756 | 5466.2129 | 3.5124 | 8525.969 | 3599.7883
DEER-SFAM-CZ11-V1-eSH-10-HM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-HM | 9.5867 | 4.2336 | 3046.3789 | 5272.6986 | 3.5124 | 8319.0775 | 3566.7349
DEER-SFAM-CZ11-V1-eSH-10-LH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-LH | 9.7964 | 3.8803 | 2942.2168 | 5788.8565 | 3.5124 | 8731.0732 | 3508.7553
DEER-SFAM-CZ11-V1-eSH-10-LL-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-LL | 9.6107 | 4.146 | 2997.715 | 5729.4565 | 3.5124 | 8727.1714 | 3590.1962
DEER-SFAM-CZ11-V1-eSH-10-LM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-LM | 9.8924 | 3.9741 | 2924.702 | 5534.2725 | 3.5124 | 8458.9745 | 3465.8387
DEER-SFAM-CZ11-V1-eSH-10-MH-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-MH | 9.7903 | 4.0477 | 2984.9559 | 5759.0726 | 3.5124 | 8744.0285 | 3587.4375
DEER-SFAM-CZ11-V1-eSH-10-ML-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-ML | 9.4728 | 4.3721 | 3076.3385 | 5341.8555 | 3.5124 | 8418.194 | 3624.8007
DEER-SFAM-CZ11-V1-eSH-10-MM-s1 | 10 | CZ11 | V1 | CZ11-V1-eSH-10 | CZ11-V1-eSH-10-MM | 9.5455 | 4.1615 | 3058.9868 | 5525.2611 | 3.5124 | 8584.2479 | 3567.3404
DEER-SFAM-CZ11-V1-eSH-13-HH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-HH | 11.0436 | 3.5968 | 2483.863 | 5485.3265 | 3.5124 | 7969.1895 | 2983.9138
DEER-SFAM-CZ11-V1-eSH-13-HL-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-HL | 12.3277 | 3.6046 | 2370.392 | 4736.9235 | 3.5124 | 7107.3154 | 2870.122
DEER-SFAM-CZ11-V1-eSH-13-HM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-HM | 11.3323 | 3.5383 | 2429.1224 | 4824.2499 | 3.5124 | 7253.3722 | 2881.1431
DEER-SFAM-CZ11-V1-eSH-13-LH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-LH | 12.044 | 3.1907 | 2344.9938 | 6220.3767 | 3.5124 | 8565.3705 | 3095.1336
DEER-SFAM-CZ11-V1-eSH-13-LL-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-LL | 12.7822 | 3.2952 | 2273.1455 | 5112.3162 | 3.5124 | 7385.4617 | 2732.0583
DEER-SFAM-CZ11-V1-eSH-13-LM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-LM | 11.3518 | 3.3579 | 2439.6606 | 4226.3258 | 3.5124 | 6665.9865 | 2957.997
DEER-SFAM-CZ11-V1-eSH-13-MH-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-MH | 12.4927 | 3.2861 | 2286.4267 | 5600.706 | 3.5124 | 7887.1327 | 2787.786
DEER-SFAM-CZ11-V1-eSH-13-ML-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-ML | 11.196 | 3.6005 | 2497.6227 | 5235.4889 | 3.5124 | 7733.1116 | 3013.4566
DEER-SFAM-CZ11-V1-eSH-13-MM-s1 | 13 | CZ11 | V1 | CZ11-V1-eSH-13 | CZ11-V1-eSH-13-MM | 11.9662 | 3.5309 | 2418.902 | 5021.4092 | 3.5124 | 7440.3112 | 2817.023
DEER-SFAM-CZ11-V1-eSH-14-HH-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-HH | 11.6815 | 3.4569 | 2350.222 | 5034.4974 | 3.5124 | 7384.7194 | 2731.2016
DEER-SFAM-CZ11-V1-eSH-14-HL-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-HL | 12.0498 | 3.4006 | 2276.5023 | 5138.697 | 3.5124 | 7415.1993 | 2735.8283
DEER-SFAM-CZ11-V1-eSH-14-HM-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-HM | 12.0641 | 3.2881 | 2262.6031 | 5035.6314 | 3.5124 | 7298.2346 | 2589.2987
DEER-SFAM-CZ11-V1-eSH-14-MH-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-MH | 12.8429 | 3 | 2185.1946 | 5636.9745 | 3.5124 | 7822.1691 | 2681.4061
DEER-SFAM-CZ11-V1-eSH-14-ML-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-ML | 12.8794 | 3.2592 | 2221.8672 | 6092.4274 | 3.5124 | 8314.2946 | 2850.7123
DEER-SFAM-CZ11-V1-eSH-14-MM-s1 | 14 | CZ11 | V1 | CZ11-V1-eSH-14 | CZ11-V1-eSH-14-MM | 12.5527 | 3.1815 | 2211.5655 | 5012.5753 | 3.5124 | 7224.1408 | 2642.2685
DEER-SFAM-CZ11-V1-eSH-15-HH-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-HH | 13.0486 | 3.026 | 2086.9187 | 6320.8255 | 3.5124 | 8407.7442 | 2438.6285
DEER-SFAM-CZ11-V1-eSH-15-HL-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-HL | 13.2259 | 3.1446 | 2109.5014 | 4259.6952 | 3.5124 | 6369.1966 | 2460.0914
DEER-SFAM-CZ11-V1-eSH-15-HM-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-HM | 13.8019 | 3.0627 | 2042.9872 | 4515.053 | 3.5124 | 6558.0402 | 2393.5878
DEER-SFAM-CZ11-V1-eSH-15-MH-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-MH | 13.3121 | 3.1353 | 2157.1437 | 5535.4648 | 3.5124 | 7692.6084 | 2498.1373
DEER-SFAM-CZ11-V1-eSH-15-ML-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-ML | 13.7112 | 3.1034 | 2079.223 | 5245.6995 | 3.5124 | 7324.9225 | 2434.7016
DEER-SFAM-CZ11-V1-eSH-15-MM-s1 | 15 | CZ11 | V1 | CZ11-V1-eSH-15 | CZ11-V1-eSH-15-MM | 13.9907 | 3.0358 | 2033.5439 | 5420.1825 | 3.5124 | 7453.7264 | 2405.8074
DEER-SFAM-CZ11-V1-eSH-16-CH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-CH | 13.777 | 3.2603 | 2370.31 | 5897.1196 | 3.5124 | 8267.4296 | 2743.8977
DEER-SFAM-CZ11-V1-eSH-16-CL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-CL | 13.9753 | 3.3478 | 2456.5729 | 5505.8273 | 3.5124 | 7962.4002 | 2842.2328
DEER-SFAM-CZ11-V1-eSH-16-LH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-LH | 13.3868 | 3.1028 | 2131.9261 | 6186.8964 | 3.5124 | 8318.8225 | 2524.5312
DEER-SFAM-CZ11-V1-eSH-16-LL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-LL | 13.0685 | 3.3002 | 2225.9438 | 5818.2785 | 3.5124 | 8044.2223 | 2548.7077
DEER-SFAM-CZ11-V1-eSH-16-LM-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-LM | 12.9547 | 3.2305 | 2217.0788 | 6289.6929 | 3.5124 | 8506.7717 | 2658.914
DEER-SFAM-CZ11-V1-eSH-16-TH-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-TH | 13.9782 | 3.4038 | 2289.932 | 7260.9425 | 3.5124 | 9550.8745 | 2716.704
DEER-SFAM-CZ11-V1-eSH-16-TL-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-TL | 13.0719 | 3.6167 | 2591.176 | 7205.1972 | 3.5124 | 9796.3733 | 2983.6318
DEER-SFAM-CZ11-V1-eSH-16-TM-s2 | 16 | CZ11 | V1 | CZ11-V1-eSH-16 | CZ11-V1-eSH-16-TM | 13.2719 | 3.5467 | 2555.0027 | 7263.9847 | 3.5124 | 9818.9874 | 2955.6517
DEER-SFAM-CZ11-V1-eSH-17-CM-s2 | 17 | CZ11 | V1 | CZ11-V1-eSH-17 | CZ11-V1-eSH-17-CM | 14.74 | 3.187 | 2324.7937 | 5976.642 | 3.5124 | 8301.4357 | 2750.1786
DEER-SFAM-CZ11-V1-eSH-17-LM-s2 | 17 | CZ11 | V1 | CZ11-V1-eSH-17 | CZ11-V1-eSH-17-LM | 13.8018 | 3.1408 | 2179.1493 | 5619.9064 | 3.5124 | 7799.0557 | 2359.805
DEER-SFAM-CZ11-V1-eSH-17-TH-s2 | 17 | CZ11 | V1 | CZ11-V1-eSH-17 | CZ11-V1-eSH-17-TH | 14.6733 | 3.1816 | 2171.8667 | 7243.4498 | 3.5124 | 9415.3166 | 2620.3528
DEER-SFAM-CZ11-V1-eSH-17-TL-s2 | 17 | CZ11 | V1 | CZ11-V1-eSH-17 | CZ11-V1-eSH-17-TL | 14.5677 | 3.2492 | 2196.6908 | 7244.3127 | 3.5124 | 9441.0035 | 2642.4812
DEER-SFAM-CZ11-V1-eSH-18-LH-s2 | 18 | CZ11 | V1 | CZ11-V1-eSH-18 | CZ11-V1-eSH-18-LH | 14.373 | 3.0254 | 2034.6872 | 6579.3531 | 3.5124 | 8614.0403 | 2358.9338
DEER-SFAM-CZ11-V1-eSH-18-LL-s2 | 18 | CZ11 | V1 | CZ11-V1-eSH-18 | CZ11-V1-eSH-18-LL | 13.7438 | 3.1285 | 2104.4138 | 5923.7116 | 3.5124 | 8028.1254 | 2386.0459
DEER-SFAM-CZ11-V1-eSH-18-LM-s2 | 18 | CZ11 | V1 | CZ11-V1-eSH-18 | CZ11-V1-eSH-18-LM | 14.4382 | 3.0634 | 2039.7567 | 6934.493 | 3.5124 | 8974.2496 | 2413.0132
DEER-SFAM-CZ11-V1-eSH-18-TM-s2 | 18 | CZ11 | V1 | CZ11-V1-eSH-18 | CZ11-V1-eSH-18-TM | 15.0806 | 3.1437 | 2158.3203 | 7305.9758 | 3.5124 | 9464.2961 | 2790.4206
DEER-SFAM-CZ11-V2-eSA-10-HH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-HH | 9.2818 | 3.607 | 2966.8645 | 0 | 3.074 | 2966.8645 | 3127.5073
DEER-SFAM-CZ11-V2-eSA-10-HL-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-HL | 8.7299 | 4.0428 | 3123.2068 | 0 | 3.074 | 3123.2068 | 3283.963
DEER-SFAM-CZ11-V2-eSA-10-HM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-HM | 8.779 | 3.8639 | 3039.3176 | 0 | 3.074 | 3039.3176 | 3200.0535
DEER-SFAM-CZ11-V2-eSA-10-LH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-LH | 9.831 | 3.5109 | 2920.4732 | 0 | 3.074 | 2920.4732 | 3081.3439
DEER-SFAM-CZ11-V2-eSA-10-LL-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-LL | 9.1553 | 3.737 | 2999.433 | 0 | 3.074 | 2999.433 | 3160.2158
DEER-SFAM-CZ11-V2-eSA-10-LM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-LM | 9.6651 | 3.5411 | 2927.0168 | 0 | 3.074 | 2927.0168 | 3087.8923
DEER-SFAM-CZ11-V2-eSA-10-MH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-MH | 9.695 | 3.4174 | 2913.2865 | 0 | 3.074 | 2913.2865 | 3074.1174
DEER-SFAM-CZ11-V2-eSA-10-ML-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-ML | 8.9028 | 3.8073 | 3083.4679 | 0 | 3.074 | 3083.4679 | 3244.2267
DEER-SFAM-CZ11-V2-eSA-10-MM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSA-10 | CZ11-V2-eSA-10-MM | 9.2919 | 3.5354 | 2949.0855 | 0 | 3.074 | 2949.0855 | 3109.8565
DEER-SFAM-CZ11-V2-eSA-13-HH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-HH | 11.928 | 3.2679 | 2365.6428 | 0 | 3.4592 | 2365.6428 | 2510.6646
DEER-SFAM-CZ11-V2-eSA-13-HL-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-HL | 11.3584 | 3.248 | 2400.8649 | 0 | 3.074 | 2400.8649 | 2527.6876
DEER-SFAM-CZ11-V2-eSA-13-HM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-HM | 11.588 | 3.3319 | 2356.5303 | 0 | 3.4592 | 2356.5303 | 2501.5134
DEER-SFAM-CZ11-V2-eSA-13-LH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-LH | 12.3207 | 2.7699 | 2235.0572 | 0 | 3.074 | 2235.0572 | 2395.8481
DEER-SFAM-CZ11-V2-eSA-13-LL-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-LL | 11.8016 | 2.9948 | 2354.469 | 0 | 3.074 | 2354.469 | 2514.9882
DEER-SFAM-CZ11-V2-eSA-13-LM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-LM | 11.6911 | 2.8861 | 2346.2543 | 0 | 3.074 | 2346.2543 | 2506.9315
DEER-SFAM-CZ11-V2-eSA-13-MH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-MH | 12.4311 | 2.9445 | 2284.0871 | 0 | 3.074 | 2284.0871 | 2444.8235
DEER-SFAM-CZ11-V2-eSA-13-ML-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-ML | 11.1675 | 3.0698 | 2349.7227 | 0 | 3.074 | 2349.7227 | 2509.9698
DEER-SFAM-CZ11-V2-eSA-13-MM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSA-13 | CZ11-V2-eSA-13-MM | 12.1766 | 3.1695 | 2266.3882 | 0 | 3.4592 | 2266.3882 | 2427.2387
DEER-SFAM-CZ11-V2-eSA-14-HH-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-HH | 11.4683 | 2.9384 | 2282.2682 | 0 | 3.074 | 2282.2682 | 2416.9842
DEER-SFAM-CZ11-V2-eSA-14-HL-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-HL | 12.6583 | 3.1474 | 2213.1713 | 0 | 3.4592 | 2213.1713 | 2312.3133
DEER-SFAM-CZ11-V2-eSA-14-HM-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-HM | 12.2207 | 3.016 | 2298.8119 | 0 | 3.074 | 2298.8119 | 2450.7875
DEER-SFAM-CZ11-V2-eSA-14-MH-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-MH | 12.7122 | 2.6841 | 2215.3544 | 0 | 3.074 | 2215.3544 | 2320.971
DEER-SFAM-CZ11-V2-eSA-14-ML-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-ML | 12.1017 | 2.92 | 2227.7867 | 0 | 3.074 | 2227.7867 | 2396.4574
DEER-SFAM-CZ11-V2-eSA-14-MM-s1 | 14 | CZ11 | V2 | CZ11-V2-eSA-14 | CZ11-V2-eSA-14-MM | 12.4964 | 2.7106 | 2187.2204 | 0 | 3.074 | 2187.2204 | 2303.0077
DEER-SFAM-CZ11-V2-eSA-15-HH-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-HH | 13.2272 | 2.9112 | 2062.819 | 0 | 3.4592 | 2062.819 | 2175.2096
DEER-SFAM-CZ11-V2-eSA-15-HL-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-HL | 13.6274 | 2.9617 | 2032.7752 | 0 | 3.4592 | 2032.7752 | 2172.8713
DEER-SFAM-CZ11-V2-eSA-15-HM-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-HM | 13.3738 | 2.8382 | 2033.4493 | 0 | 3.4592 | 2033.4493 | 2146.2604
DEER-SFAM-CZ11-V2-eSA-15-MH-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-MH | 12.7204 | 2.8013 | 2126.5279 | 0 | 3.074 | 2126.5279 | 2210.2052
DEER-SFAM-CZ11-V2-eSA-15-ML-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-ML | 13.5448 | 2.7018 | 2069.3649 | 0 | 3.074 | 2069.3649 | 2181.9164
DEER-SFAM-CZ11-V2-eSA-15-MM-s1 | 15 | CZ11 | V2 | CZ11-V2-eSA-15 | CZ11-V2-eSA-15-MM | 13.2295 | 2.7535 | 2074.7622 | 0 | 3.074 | 2074.7622 | 2177.3692
DEER-SFAM-CZ11-V2-eSA-16-CH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-CH | 13.7249 | 2.8918 | 2347.552 | 0 | 3.074 | 2347.552 | 2412.5011
DEER-SFAM-CZ11-V2-eSA-16-CL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-CL | 13.9782 | 3.0895 | 2227.5714 | 0 | 3.4592 | 2227.5714 | 2310.0338
DEER-SFAM-CZ11-V2-eSA-16-CM-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-CM | 13.6993 | 3.1029 | 2303.6217 | 0 | 3.4592 | 2303.6217 | 2390.7167
DEER-SFAM-CZ11-V2-eSA-16-LH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-LH | 13.8601 | 2.703 | 2006.9557 | 0 | 3.074 | 2006.9557 | 2118.0427
DEER-SFAM-CZ11-V2-eSA-16-LL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-LL | 13.2648 | 2.8964 | 2133.9934 | 0 | 3.074 | 2133.9934 | 2206.9518
DEER-SFAM-CZ11-V2-eSA-16-LM-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-LM | 13.2866 | 2.7983 | 2125.4648 | 0 | 3.074 | 2125.4648 | 2191.6084
DEER-SFAM-CZ11-V2-eSA-16-NM-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-NM | 14.7361 | 2.6387 | 1934.6894 | 0 | 3.074 | 1934.6894 | 1999.605
DEER-SFAM-CZ11-V2-eSA-16-TH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-TH | 13.1253 | 3.1357 | 2420.24 | 0 | 3.074 | 2420.24 | 2461.8075
DEER-SFAM-CZ11-V2-eSA-16-TL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSA-16 | CZ11-V2-eSA-16-TL | 14.0751 | 3.2455 | 2219.3683 | 0 | 3.4592 | 2219.3683 | 2264.3101
DEER-SFAM-CZ11-V2-eSA-17-CH-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-CH | 14.4957 | 2.7747 | 2176.2233 | 0 | 3.074 | 2176.2233 | 2258.5065
DEER-SFAM-CZ11-V2-eSA-17-CL-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-CL | 14.3693 | 2.8039 | 2166.5304 | 0 | 3.074 | 2166.5304 | 2248.7953
DEER-SFAM-CZ11-V2-eSA-17-CM-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-CM | 14.5012 | 2.7957 | 2192.7795 | 0 | 3.074 | 2192.7795 | 2257.5328
DEER-SFAM-CZ11-V2-eSA-17-LH-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-LH | 14.1531 | 2.6479 | 1966.8832 | 0 | 3.074 | 1966.8832 | 2053.9246
DEER-SFAM-CZ11-V2-eSA-17-LL-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-LL | 13.8818 | 2.7865 | 2058.5268 | 0 | 3.074 | 2058.5268 | 2105.9799
DEER-SFAM-CZ11-V2-eSA-17-LM-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-LM | 13.7711 | 2.7629 | 2054.0305 | 0 | 3.074 | 2054.0305 | 2094.9862
DEER-SFAM-CZ11-V2-eSA-17-TH-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-TH | 14.8447 | 2.7011 | 2064.5553 | 0 | 3.074 | 2064.5553 | 2131.0135
DEER-SFAM-CZ11-V2-eSA-17-TL-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-TL | 15.3515 | 3.0094 | 1930.1727 | 0 | 3.4592 | 1930.1727 | 2034.8245
DEER-SFAM-CZ11-V2-eSA-17-TM-s2 | 17 | CZ11 | V2 | CZ11-V2-eSA-17 | CZ11-V2-eSA-17-TM | 15.2842 | 3.0694 | 2278.1453 | 0 | 3.4592 | 2278.1453 | 2312.9491
DEER-SFAM-CZ11-V2-eSA-18-LH-s2 | 18 | CZ11 | V2 | CZ11-V2-eSA-18 | CZ11-V2-eSA-18-LH | 14.7573 | 2.5778 | 1917.5262 | 0 | 3.074 | 1917.5262 | 1974.5675
DEER-SFAM-CZ11-V2-eSA-18-LL-s2 | 18 | CZ11 | V2 | CZ11-V2-eSA-18 | CZ11-V2-eSA-18-LL | 14.9005 | 2.5927 | 1880.9503 | 0 | 3.074 | 1880.9503 | 1955.4082
DEER-SFAM-CZ11-V2-eSA-18-TH-s2 | 18 | CZ11 | V2 | CZ11-V2-eSA-18 | CZ11-V2-eSA-18-TH | 15.525 | 2.7669 | 2023.0652 | 0 | 3.4592 | 2023.0652 | 2068.304
DEER-SFAM-CZ11-V2-eSA-18-TL-s2 | 18 | CZ11 | V2 | CZ11-V2-eSA-18 | CZ11-V2-eSA-18-TL | 15.023 | 2.8409 | 2150.9165 | 0 | 3.074 | 2150.9165 | 2200.5899
DEER-SFAM-CZ11-V2-eSA-18-TM-s2 | 18 | CZ11 | V2 | CZ11-V2-eSA-18 | CZ11-V2-eSA-18-TM | 14.9009 | 2.6579 | 2041.7074 | 0 | 3.074 | 2041.7074 | 2087.8687
DEER-SFAM-CZ11-V2-eSH-10-HH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-HH | 9.4887 | 3.8937 | 2929.5479 | 3629.5029 | 3.4592 | 6559.0508 | 3304.5389
DEER-SFAM-CZ11-V2-eSH-10-HL-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-HL | 9.1692 | 4.0921 | 3031.3724 | 3668.4428 | 3.4592 | 6699.8153 | 3398.3823
DEER-SFAM-CZ11-V2-eSH-10-HM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-HM | 9.6542 | 3.7113 | 2967.4871 | 3579.6246 | 3.074 | 6547.1117 | 3320.615
DEER-SFAM-CZ11-V2-eSH-10-LH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-LH | 9.8559 | 3.4027 | 2867.9098 | 3841.2924 | 3.074 | 6709.2022 | 3253.5679
DEER-SFAM-CZ11-V2-eSH-10-LL-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-LL | 9.6603 | 3.6351 | 2926.0131 | 3818.1585 | 3.074 | 6744.1716 | 3329.2364
DEER-SFAM-CZ11-V2-eSH-10-LM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-LM | 9.9554 | 3.4891 | 2853.2197 | 3719.6662 | 3.074 | 6572.8859 | 3222.1368
DEER-SFAM-CZ11-V2-eSH-10-MH-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-MH | 9.8345 | 3.5453 | 2906.8743 | 3826.6145 | 3.074 | 6733.4888 | 3316.6021
DEER-SFAM-CZ11-V2-eSH-10-ML-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-ML | 9.5277 | 3.832 | 2999.5938 | 3594.6024 | 3.074 | 6594.1963 | 3373.741
DEER-SFAM-CZ11-V2-eSH-10-MM-s1 | 10 | CZ11 | V2 | CZ11-V2-eSH-10 | CZ11-V2-eSH-10-MM | 9.5896 | 3.6389 | 2981.389 | 3716.5995 | 3.074 | 6697.9885 | 3327.7699
DEER-SFAM-CZ11-V2-eSH-13-HH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-HH | 11.0533 | 3.3731 | 2459.0364 | 3528.6579 | 3.4592 | 5987.6943 | 2801.3511
DEER-SFAM-CZ11-V2-eSH-13-HL-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-HL | 12.2845 | 3.4127 | 2338.6729 | 3077.7201 | 3.4592 | 5416.393 | 2679.2576
DEER-SFAM-CZ11-V2-eSH-13-HM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-HM | 11.3516 | 3.306 | 2401.9131 | 3149.7449 | 3.4592 | 5551.658 | 2710.558
DEER-SFAM-CZ11-V2-eSH-13-LH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-LH | 12.1112 | 2.803 | 2285.2309 | 3975.706 | 3.074 | 6260.9369 | 2797.6056
DEER-SFAM-CZ11-V2-eSH-13-LL-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-LL | 12.8891 | 2.896 | 2213.7662 | 3341.439 | 3.074 | 5555.2051 | 2526.8124
DEER-SFAM-CZ11-V2-eSH-13-LM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-LM | 11.4177 | 2.9526 | 2383.339 | 2813.9852 | 3.074 | 5197.3242 | 2736.0342
DEER-SFAM-CZ11-V2-eSH-13-MH-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-MH | 12.3686 | 3.1079 | 2268.4844 | 3575.8854 | 3.4592 | 5844.3698 | 2610.8226
DEER-SFAM-CZ11-V2-eSH-13-ML-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-ML | 11.2563 | 3.1677 | 2443.6243 | 3408.3951 | 3.074 | 5852.0195 | 2794.0603
DEER-SFAM-CZ11-V2-eSH-13-MM-s1 | 13 | CZ11 | V2 | CZ11-V2-eSH-13 | CZ11-V2-eSH-13-MM | 12.0788 | 3.0995 | 2355.9203 | 3356.2517 | 3.074 | 5712.172 | 2627.3141
DEER-SFAM-CZ11-V2-eSH-14-HH-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-HH | 11.709 | 3.2308 | 2323.8536 | 3236.9615 | 3.4592 | 5560.815 | 2584.3575
DEER-SFAM-CZ11-V2-eSH-14-HL-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-HL | 12.0944 | 3.1745 | 2247.4928 | 3234.7353 | 3.4592 | 5482.2281 | 2560.9725
DEER-SFAM-CZ11-V2-eSH-14-HM-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-HM | 12.0829 | 3.0638 | 2239.4695 | 3201.2607 | 3.4592 | 5440.7302 | 2462.9718
DEER-SFAM-CZ11-V2-eSH-14-MH-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-MH | 12.9226 | 2.6366 | 2130.7726 | 3617.5219 | 3.074 | 5748.2944 | 2470.4735
DEER-SFAM-CZ11-V2-eSH-14-ML-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-ML | 12.7872 | 3.0615 | 2182.9101 | 3661.1565 | 3.4592 | 5844.0666 | 2613.2141
DEER-SFAM-CZ11-V2-eSH-14-MM-s1 | 14 | CZ11 | V2 | CZ11-V2-eSH-14 | CZ11-V2-eSH-14-MM | 12.617 | 2.7957 | 2161.011 | 3250.4375 | 3.074 | 5411.4485 | 2454.2271
DEER-SFAM-CZ11-V2-eSH-15-HH-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-HH | 13.0715 | 2.8315 | 2067.0327 | 3874.4938 | 3.4592 | 5941.5265 | 2311.3666
DEER-SFAM-CZ11-V2-eSH-15-HL-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-HL | 13.2843 | 2.9472 | 2084.2993 | 2755.5708 | 3.4592 | 4839.8701 | 2323.2276
DEER-SFAM-CZ11-V2-eSH-15-HM-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-HM | 13.7125 | 2.8797 | 2024.4872 | 2864.2219 | 3.4592 | 4888.709 | 2263.1835
DEER-SFAM-CZ11-V2-eSH-15-MH-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-MH | 13.3773 | 2.7551 | 2098.764 | 3497.4863 | 3.074 | 5596.2504 | 2330.2689
DEER-SFAM-CZ11-V2-eSH-15-ML-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-ML | 13.6395 | 2.9107 | 2042.2418 | 3182.7367 | 3.4592 | 5224.9785 | 2284.305
DEER-SFAM-CZ11-V2-eSH-15-MM-s1 | 15 | CZ11 | V2 | CZ11-V2-eSH-15 | CZ11-V2-eSH-15-MM | 13.9191 | 2.8626 | 2011.251 | 3371.4008 | 3.4592 | 5382.6518 | 2267.0719
DEER-SFAM-CZ11-V2-eSH-16-CH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-CH | 13.8945 | 3.0338 | 2288.1799 | 3744.0795 | 3.4592 | 6032.2594 | 2533.7208
DEER-SFAM-CZ11-V2-eSH-16-CL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-CL | 14.059 | 3.2012 | 2361.711 | 3470.7995 | 3.4592 | 5832.5105 | 2613.2837
DEER-SFAM-CZ11-V2-eSH-16-LH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-LH | 13.5865 | 2.7023 | 2039.7435 | 3943.347 | 3.074 | 5983.0905 | 2299.8049
DEER-SFAM-CZ11-V2-eSH-16-LL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-LL | 13.1844 | 2.8703 | 2136.4438 | 3671.0299 | 3.074 | 5807.4737 | 2347.5358
DEER-SFAM-CZ11-V2-eSH-16-LM-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-LM | 13.1218 | 2.8129 | 2123.6363 | 3997.3232 | 3.074 | 6120.9594 | 2415.373
DEER-SFAM-CZ11-V2-eSH-16-TH-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-TH | 14.1618 | 3.1777 | 2200.7683 | 4737.4063 | 3.4592 | 6938.1747 | 2479.8026
DEER-SFAM-CZ11-V2-eSH-16-TL-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-TL | 13.2066 | 3.1576 | 2427.783 | 4671.5772 | 3.074 | 7099.3602 | 2690.8429
DEER-SFAM-CZ11-V2-eSH-16-TM-s2 | 16 | CZ11 | V2 | CZ11-V2-eSH-16 | CZ11-V2-eSH-16-TM | 13.4074 | 3.0957 | 2393.7511 | 4718.8832 | 3.074 | 7112.6343 | 2663.229
DEER-SFAM-CZ11-V2-eSH-17-CM-s2 | 17 | CZ11 | V2 | CZ11-V2-eSH-17 | CZ11-V2-eSH-17-CM | 14.8265 | 3.0456 | 2235.6986 | 3716.2538 | 3.4592 | 5951.9524 | 2504.6592
DEER-SFAM-CZ11-V2-eSH-17-LM-s2 | 17 | CZ11 | V2 | CZ11-V2-eSH-17 | CZ11-V2-eSH-17-LM | 13.9795 | 2.7346 | 2079.6645 | 3541.8712 | 3.074 | 5621.5358 | 2197.8606
DEER-SFAM-CZ11-V2-eSH-17-TH-s2 | 17 | CZ11 | V2 | CZ11-V2-eSH-17 | CZ11-V2-eSH-17-TH | 14.8205 | 2.9855 | 2093.2072 | 4736.6097 | 3.4592 | 6829.8169 | 2392.126
DEER-SFAM-CZ11-V2-eSH-17-TL-s2 | 17 | CZ11 | V2 | CZ11-V2-eSH-17 | CZ11-V2-eSH-17-TL | 14.748 | 3.0457 | 2113.2471 | 4718.1421 | 3.4592 | 6831.3892 | 2408.8643
DEER-SFAM-CZ11-V2-eSH-18-LH-s2 | 18 | CZ11 | V2 | CZ11-V2-eSH-18 | CZ11-V2-eSH-18-LH | 14.5071 | 2.6326 | 1947.5287 | 4196.5882 | 3.074 | 6144.1168 | 2158.7187
DEER-SFAM-CZ11-V2-eSH-18-LL-s2 | 18 | CZ11 | V2 | CZ11-V2-eSH-18 | CZ11-V2-eSH-18-LL | 13.8722 | 2.7247 | 2018.7788 | 3733.0283 | 3.074 | 5751.8072 | 2203.0172
DEER-SFAM-CZ11-V2-eSH-18-LM-s2 | 18 | CZ11 | V2 | CZ11-V2-eSH-18 | CZ11-V2-eSH-18-LM | 14.6057 | 2.6636 | 1949.0735 | 4437.4953 | 3.074 | 6386.5688 | 2193.5884
DEER-SFAM-CZ11-V2-eSH-18-TM-s2 | 18 | CZ11 | V2 | CZ11-V2-eSH-18 | CZ11-V2-eSH-18-TM | 15.1958 | 2.7387 | 2041.0664 | 4751.8933 | 3.074 | 6792.9596 | 2474.7029
DEER-SFAM-CZ11-V3-eSA-10-HH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-HH | 8.938 | 4.1072 | 2818.6046 | 0 | 3.8 | 2818.6046 | 2931.5973
DEER-SFAM-CZ11-V3-eSA-10-HL-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-HL | 8.5136 | 4.4588 | 2937.0645 | 0 | 3.8 | 2937.0645 | 3050.1141
DEER-SFAM-CZ11-V3-eSA-10-HM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-HM | 8.5608 | 4.2651 | 2862.0886 | 0 | 3.8 | 2862.0886 | 2975.128
DEER-SFAM-CZ11-V3-eSA-10-LH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-LH | 9.3261 | 4.0386 | 2787.9275 | 0 | 3.8 | 2787.9275 | 2901.0343
DEER-SFAM-CZ11-V3-eSA-10-LL-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-LL | 8.9457 | 4.1422 | 2816.2592 | 0 | 3.8 | 2816.2592 | 2929.322
DEER-SFAM-CZ11-V3-eSA-10-LM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-LM | 9.2394 | 4.0539 | 2779.9924 | 0 | 3.8 | 2779.9924 | 2893.1016
DEER-SFAM-CZ11-V3-eSA-10-MH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-MH | 9.14 | 3.9454 | 2807.9654 | 0 | 3.8 | 2807.9654 | 2921.0526
DEER-SFAM-CZ11-V3-eSA-10-ML-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-ML | 8.6712 | 4.2333 | 2898.6044 | 0 | 3.8 | 2898.6044 | 3011.655
DEER-SFAM-CZ11-V3-eSA-10-MM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSA-10 | CZ11-V3-eSA-10-MM | 9.0212 | 3.8294 | 2790.7873 | 0 | 3.5 | 2790.7873 | 2903.7875
DEER-SFAM-CZ11-V3-eSA-13-HH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-HH | 11.6237 | 3.4508 | 2224.7439 | 0 | 3.8 | 2224.7439 | 2326.6477
DEER-SFAM-CZ11-V3-eSA-13-HL-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-HL | 11.0595 | 3.654 | 2260.7329 | 0 | 3.8 | 2260.7329 | 2349.9253
DEER-SFAM-CZ11-V3-eSA-13-HM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-HM | 11.4079 | 3.4042 | 2195.1024 | 0 | 3.8 | 2195.1024 | 2296.9839
DEER-SFAM-CZ11-V3-eSA-13-LH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-LH | 11.7804 | 3.1515 | 2133.434 | 0 | 3.8 | 2133.434 | 2246.5005
DEER-SFAM-CZ11-V3-eSA-13-LL-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-LL | 11.3773 | 3.4091 | 2229.8071 | 0 | 3.8 | 2229.8071 | 2342.7381
DEER-SFAM-CZ11-V3-eSA-13-LM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-LM | 11.261 | 3.1641 | 2225.873 | 0 | 3.5 | 2225.873 | 2338.8212
DEER-SFAM-CZ11-V3-eSA-13-MH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-MH | 11.8725 | 3.3253 | 2166.7363 | 0 | 3.8 | 2166.7363 | 2279.7761
DEER-SFAM-CZ11-V3-eSA-13-ML-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-ML | 10.9511 | 3.406 | 2204.0451 | 0 | 3.8 | 2204.0451 | 2316.7509
DEER-SFAM-CZ11-V3-eSA-13-MM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSA-13 | CZ11-V3-eSA-13-MM | 11.9461 | 3.28 | 2106.2492 | 0 | 3.8 | 2106.2492 | 2219.279
DEER-SFAM-CZ11-V3-eSA-14-HH-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-HH | 11.171 | 3.2819 | 2154.7753 | 0 | 3.8 | 2154.7753 | 2249.5254
DEER-SFAM-CZ11-V3-eSA-14-HL-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-HL | 12.3377 | 3.265 | 2057.8151 | 0 | 3.8 | 2057.8151 | 2127.4883
DEER-SFAM-CZ11-V3-eSA-14-HM-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-HM | 11.7419 | 3.4 | 2174.5556 | 0 | 3.8 | 2174.5556 | 2281.425
DEER-SFAM-CZ11-V3-eSA-14-MH-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-MH | 12.1224 | 2.956 | 2113.0351 | 0 | 3.5 | 2113.0351 | 2187.2872
DEER-SFAM-CZ11-V3-eSA-14-ML-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-ML | 11.7575 | 3.3099 | 2107.0376 | 0 | 3.8 | 2107.0376 | 2225.6549
DEER-SFAM-CZ11-V3-eSA-14-MM-s1 | 14 | CZ11 | V3 | CZ11-V3-eSA-14 | CZ11-V3-eSA-14-MM | 12.026 | 2.975 | 2077.391 | 0 | 3.5 | 2077.391 | 2158.7851
DEER-SFAM-CZ11-V3-eSA-15-HH-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-HH | 12.9498 | 2.9818 | 1932.6644 | 0 | 3.8 | 1932.6644 | 2011.6426
DEER-SFAM-CZ11-V3-eSA-15-HL-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-HL | 13.2695 | 3.0602 | 1897.0415 | 0 | 3.8 | 1897.0415 | 1995.495
DEER-SFAM-CZ11-V3-eSA-15-HM-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-HM | 13.1478 | 2.8907 | 1899.6386 | 0 | 3.8 | 1899.6386 | 1978.9149
DEER-SFAM-CZ11-V3-eSA-15-MH-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-MH | 12.2034 | 3.1945 | 2027.917 | 0 | 3.8 | 2027.917 | 2086.7658
DEER-SFAM-CZ11-V3-eSA-15-ML-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-ML | 13.0504 | 3.0519 | 1955.9735 | 0 | 3.8 | 1955.9735 | 2035.1666
DEER-SFAM-CZ11-V3-eSA-15-MM-s1 | 15 | CZ11 | V3 | CZ11-V3-eSA-15 | CZ11-V3-eSA-15-MM | 12.7692 | 3.0974 | 1961.3476 | 0 | 3.8 | 1961.3476 | 2033.5105
DEER-SFAM-CZ11-V3-eSA-16-CH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-CH | 13.7776 | 3.2275 | 2109.1813 | 0 | 3.8 | 2109.1813 | 2154.8411
DEER-SFAM-CZ11-V3-eSA-16-CL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-CL | 14.128 | 3.0247 | 1968.1556 | 0 | 3.8 | 1968.1556 | 2025.8831
DEER-SFAM-CZ11-V3-eSA-16-CM-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-CM | 13.7846 | 3.075 | 2043.7891 | 0 | 3.8 | 2043.7891 | 2104.6699
DEER-SFAM-CZ11-V3-eSA-16-LH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-LH | 13.6316 | 2.9242 | 1855.2196 | 0 | 3.8 | 1855.2196 | 1933.5496
DEER-SFAM-CZ11-V3-eSA-16-LL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-LL | 13.2094 | 3.1226 | 1939.7872 | 0 | 3.8 | 1939.7872 | 1991.1551
DEER-SFAM-CZ11-V3-eSA-16-LM-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-LM | 13.1547 | 3.0441 | 1944.0046 | 0 | 3.8 | 1944.0046 | 1990.5705
DEER-SFAM-CZ11-V3-eSA-16-NM-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-NM | 14.9819 | 2.7762 | 1727.497 | 0 | 3.8 | 1727.497 | 1773.2536
DEER-SFAM-CZ11-V3-eSA-16-TH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-TH | 13.001 | 3.3853 | 2207.9619 | 0 | 3.8 | 2207.9619 | 2237.3064
DEER-SFAM-CZ11-V3-eSA-16-TL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSA-16 | CZ11-V3-eSA-16-TL | 14.2316 | 3.2017 | 1942.3846 | 0 | 3.8 | 1942.3846 | 1974.0136
DEER-SFAM-CZ11-V3-eSA-17-CH-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-CH | 14.5761 | 3.0677 | 1953.9101 | 0 | 3.8 | 1953.9101 | 2011.629
DEER-SFAM-CZ11-V3-eSA-17-CL-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-CL | 14.5664 | 3.011 | 1933.4239 | 0 | 3.8 | 1933.4239 | 1991.1279
DEER-SFAM-CZ11-V3-eSA-17-CM-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-CM | 14.6739 | 3.0465 | 1957.8031 | 0 | 3.8 | 1957.8031 | 2003.3253
DEER-SFAM-CZ11-V3-eSA-17-LH-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-LH | 14.0592 | 2.7787 | 1795.7592 | 0 | 3.5 | 1795.7592 | 1857.0832
DEER-SFAM-CZ11-V3-eSA-17-LL-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-LL | 13.8476 | 3.0103 | 1863.4696 | 0 | 3.8 | 1863.4696 | 1896.8056
DEER-SFAM-CZ11-V3-eSA-17-LM-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-LM | 13.7148 | 2.9723 | 1868.1918 | 0 | 3.8 | 1868.1918 | 1897.0062
DEER-SFAM-CZ11-V3-eSA-17-TH-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-TH | 14.4863 | 2.9814 | 1917.6158 | 0 | 3.8 | 1917.6158 | 1964.5216
DEER-SFAM-CZ11-V3-eSA-17-TL-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-TL | 15.6326 | 2.9376 | 1706.871 | 0 | 3.8 | 1706.871 | 1780.1593
DEER-SFAM-CZ11-V3-eSA-17-TM-s2 | 17 | CZ11 | V3 | CZ11-V3-eSA-17 | CZ11-V3-eSA-17-TM | 15.3725 | 3.1133 | 1965.649 | 0 | 3.8 | 1965.649 | 1990.0982
DEER-SFAM-CZ11-V3-eSA-18-LH-s2 | 18 | CZ11 | V3 | CZ11-V3-eSA-18 | CZ11-V3-eSA-18-LH | 14.6253 | 2.7811 | 1750.4233 | 0 | 3.8 | 1750.4233 | 1790.5792
DEER-SFAM-CZ11-V3-eSA-18-LL-s2 | 18 | CZ11 | V3 | CZ11-V3-eSA-18 | CZ11-V3-eSA-18-LL | 14.8824 | 2.802 | 1710.4941 | 0 | 3.8 | 1710.4941 | 1762.9402
DEER-SFAM-CZ11-V3-eSA-18-TH-s2 | 18 | CZ11 | V3 | CZ11-V3-eSA-18 | CZ11-V3-eSA-18-TH | 15.2783 | 2.7962 | 1827.6468 | 0 | 3.8 | 1827.6468 | 1859.4849
DEER-SFAM-CZ11-V3-eSA-18-TL-s2 | 18 | CZ11 | V3 | CZ11-V3-eSA-18 | CZ11-V3-eSA-18-TL | 14.8688 | 3.1833 | 1956.9819 | 0 | 3.8 | 1956.9819 | 1992.0017
DEER-SFAM-CZ11-V3-eSA-18-TM-s2 | 18 | CZ11 | V3 | CZ11-V3-eSA-18 | CZ11-V3-eSA-18-TM | 14.5902 | 2.9011 | 1888.5733 | 0 | 3.8 | 1888.5733 | 1921.137
DEER-SFAM-CZ11-V3-eSH-10-HH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-HH | 9.1486 | 4.0458 | 2754.6925 | 2515.1471 | 3.8 | 5269.8396 | 3006.6396
DEER-SFAM-CZ11-V3-eSH-10-HL-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-HL | 8.8877 | 4.2471 | 2835.7739 | 2530.6111 | 3.8 | 5366.385 | 3082.685
DEER-SFAM-CZ11-V3-eSH-10-HM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-HM | 9.1968 | 4.2091 | 2817.2538 | 2499.4625 | 3.8 | 5316.7163 | 3054.3163
DEER-SFAM-CZ11-V3-eSH-10-LH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-LH | 9.2765 | 3.9187 | 2770.7089 | 2621.1427 | 3.8 | 5391.8516 | 3030.2516
DEER-SFAM-CZ11-V3-eSH-10-LL-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-LL | 9.2583 | 4.1025 | 2760.4783 | 2569.6462 | 3.8 | 5330.1245 | 3031.3245
DEER-SFAM-CZ11-V3-eSH-10-LM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-LM | 9.4656 | 3.9413 | 2712.1177 | 2553.1689 | 3.8 | 5265.2866 | 2960.9866
DEER-SFAM-CZ11-V3-eSH-10-MH-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-MH | 9.3064 | 4.0645 | 2785.5396 | 2596.8393 | 3.8 | 5382.3789 | 3060.7789
DEER-SFAM-CZ11-V3-eSH-10-ML-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-ML | 9.1659 | 4.3142 | 2814.4894 | 2437.3533 | 3.8 | 5251.8427 | 3066.6427
DEER-SFAM-CZ11-V3-eSH-10-MM-s1 | 10 | CZ11 | V3 | CZ11-V3-eSH-10 | CZ11-V3-eSH-10-MM | 9.1695 | 4.1477 | 2830.5865 | 2541.0908 | 3.8 | 5371.6773 | 3064.6773
DEER-SFAM-CZ11-V3-eSH-13-HH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-HH | 10.8119 | 3.4689 | 2305.3806 | 2421.5995 | 3.8 | 4726.9801 | 2535.5801
DEER-SFAM-CZ11-V3-eSH-13-HL-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-HL | 11.918 | 3.5848 | 2181.7826 | 2100.7075 | 3.8 | 4282.4901 | 2410.7901
DEER-SFAM-CZ11-V3-eSH-13-HM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-HM | 11.1347 | 3.3921 | 2243.8608 | 2176.4679 | 3.8 | 4420.3287 | 2451.9287
DEER-SFAM-CZ11-V3-eSH-13-LH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-LH | 11.5036 | 3.2322 | 2194.0339 | 2460.9957 | 3.8 | 4655.0296 | 2537.2296
DEER-SFAM-CZ11-V3-eSH-13-LL-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-LL | 12.3682 | 3.272 | 2084.5019 | 2197.0363 | 3.8 | 4281.5382 | 2295.3382
DEER-SFAM-CZ11-V3-eSH-13-LM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-LM | 11.0301 | 3.2381 | 2256.2491 | 1904.7804 | 3.5 | 4161.0295 | 2494.2295
DEER-SFAM-CZ11-V3-eSH-13-MH-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-MH | 11.8647 | 3.2283 | 2141.9519 | 2445.1544 | 3.8 | 4587.1063 | 2371.5063
DEER-SFAM-CZ11-V3-eSH-13-ML-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-ML | 10.8431 | 3.6464 | 2325.5223 | 2222.6313 | 3.8 | 4548.1536 | 2560.8536
DEER-SFAM-CZ11-V3-eSH-13-MM-s1 | 13 | CZ11 | V3 | CZ11-V3-eSH-13 | CZ11-V3-eSH-13-MM | 11.5851 | 3.4973 | 2228.112 | 2282.0415 | 3.8 | 4510.1535 | 2411.9535
DEER-SFAM-CZ11-V3-eSH-14-HH-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-HH | 11.4925 | 3.3068 | 2171.9061 | 2221.9691 | 3.8 | 4393.8752 | 2347.2752
DEER-SFAM-CZ11-V3-eSH-14-HL-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-HL | 11.9584 | 3.234 | 2085.6046 | 2173.494 | 3.8 | 4259.0986 | 2295.5986
DEER-SFAM-CZ11-V3-eSH-14-HM-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-HM | 11.8994 | 3.123 | 2088.0064 | 2172.7826 | 3.8 | 4260.789 | 2238.289
DEER-SFAM-CZ11-V3-eSH-14-MH-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-MH | 12.3048 | 3.0281 | 2042.7735 | 2263.3055 | 3.8 | 4306.079 | 2271.479
DEER-SFAM-CZ11-V3-eSH-14-ML-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-ML | 12.4789 | 3.1619 | 2029.1624 | 2310.2796 | 3.8 | 4339.442 | 2313.342
DEER-SFAM-CZ11-V3-eSH-14-MM-s1 | 14 | CZ11 | V3 | CZ11-V3-eSH-14 | CZ11-V3-eSH-14-MM | 12.1807 | 3.1671 | 2045.5577 | 2103.9379 | 3.8 | 4149.4956 | 2242.5956
DEER-SFAM-CZ11-V3-eSH-15-HH-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-HH | 12.8431 | 2.8857 | 1933.5023 | 2443.5468 | 3.8 | 4377.0491 | 2096.2491
DEER-SFAM-CZ11-V3-eSH-15-HL-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-HL | 13.1107 | 3.0463 | 1939.1606 | 1893.8596 | 3.8 | 3833.0202 | 2100.1202
DEER-SFAM-CZ11-V3-eSH-15-HM-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-HM | 13.3034 | 2.9547 | 1895.0504 | 1980.5433 | 3.8 | 3875.5937 | 2054.7937
DEER-SFAM-CZ11-V3-eSH-15-MH-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-MH | 12.7806 | 3.0871 | 1993.0793 | 2163.1721 | 3.8 | 4156.2514 | 2147.1514
DEER-SFAM-CZ11-V3-eSH-15-ML-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-ML | 13.3474 | 2.9962 | 1895.8642 | 2059.7695 | 3.8 | 3955.6337 | 2056.4337
DEER-SFAM-CZ11-V3-eSH-15-MM-s1 | 15 | CZ11 | V3 | CZ11-V3-eSH-15 | CZ11-V3-eSH-15-MM | 13.5009 | 2.9483 | 1881.9575 | 2223.2347 | 3.8 | 4105.1922 | 2053.5922
DEER-SFAM-CZ11-V3-eSH-16-CH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-CH | 13.9399 | 3.0185 | 2031.4287 | 2239.1659 | 3.8 | 4270.5946 | 2174.5946
DEER-SFAM-CZ11-V3-eSH-16-CL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-CL | 14.1263 | 3.2684 | 2074.5884 | 2092.9411 | 3.8 | 4167.5295 | 2223.1295
DEER-SFAM-CZ11-V3-eSH-16-LH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-LH | 13.1849 | 2.9479 | 1911.4921 | 2312.573 | 3.8 | 4224.0651 | 2072.8651
DEER-SFAM-CZ11-V3-eSH-16-LL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-LL | 13.1263 | 3.1301 | 1945.338 | 2118.4658 | 3.8 | 4063.8038 | 2075.1038
DEER-SFAM-CZ11-V3-eSH-16-LM-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-LM | 12.9383 | 2.9683 | 1952.6731 | 2334.246 | 3.5 | 4286.9191 | 2133.7191
DEER-SFAM-CZ11-V3-eSH-16-TH-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-TH | 14.1029 | 3.1738 | 1964.0598 | 2791.6646 | 3.8 | 4755.7244 | 2105.7244
DEER-SFAM-CZ11-V3-eSH-16-TL-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-TL | 13.3335 | 3.4695 | 2175.1527 | 2737.4441 | 3.8 | 4912.5968 | 2304.4968
DEER-SFAM-CZ11-V3-eSH-16-TM-s2 | 16 | CZ11 | V3 | CZ11-V3-eSH-16 | CZ11-V3-eSH-16-TM | 13.4964 | 3.401 | 2149.4939 | 2778.0549 | 3.8 | 4927.5488 | 2282.8488
DEER-SFAM-CZ11-V3-eSH-17-CM-s2 | 17 | CZ11 | V3 | CZ11-V3-eSH-17 | CZ11-V3-eSH-17-CM | 14.8898 | 3.1074 | 1965.763 | 2179.1559 | 3.8 | 4144.9189 | 2120.5189
DEER-SFAM-CZ11-V3-eSH-17-LM-s2 | 17 | CZ11 | V3 | CZ11-V3-eSH-17 | CZ11-V3-eSH-17-LM | 13.7329 | 3.0574 | 1910.4947 | 2059.4074 | 3.8 | 3969.9021 | 1983.4021
DEER-SFAM-CZ11-V3-eSH-17-TH-s2 | 17 | CZ11 | V3 | CZ11-V3-eSH-17 | CZ11-V3-eSH-17-TH | 14.7127 | 3.015 | 1874.3863 | 2786.7188 | 3.8 | 4661.1051 | 2028.6051
DEER-SFAM-CZ11-V3-eSH-17-TL-s2 | 17 | CZ11 | V3 | CZ11-V3-eSH-17 | CZ11-V3-eSH-17-TL | 14.7092 | 3.0738 | 1883.7533 | 2758.7679 | 3.8 | 4642.5212 | 2035.3212
DEER-SFAM-CZ11-V3-eSH-18-LH-s2 | 18 | CZ11 | V3 | CZ11-V3-eSH-18 | CZ11-V3-eSH-18-LH | 14.4058 | 2.783 | 1771.2229 | 2375.6804 | 3.5 | 4146.9033 | 1891.0033
DEER-SFAM-CZ11-V3-eSH-18-LL-s2 | 18 | CZ11 | V3 | CZ11-V3-eSH-18 | CZ11-V3-eSH-18-LL | 13.7979 | 2.8828 | 1837.2476 | 2140.9499 | 3.5 | 3978.1975 | 1949.4975
DEER-SFAM-CZ11-V3-eSH-18-LM-s2 | 18 | CZ11 | V3 | CZ11-V3-eSH-18 | CZ11-V3-eSH-18-LM | 14.5121 | 2.9031 | 1772.2137 | 2436.5443 | 3.8 | 4208.758 | 1905.358
DEER-SFAM-CZ11-V3-eSH-18-TM-s2 | 18 | CZ11 | V3 | CZ11-V3-eSH-18 | CZ11-V3-eSH-18-TM | 15.1402 | 2.9159 | 1864.8021 | 2781.9816 | 3.5 | 4646.7837 | 2108.7837
DEER-SFAM-CZ11-V4-eSA-10-HH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-HH | 8.9269 | 3.7116 | 2484.1905 | 0 | 3.5 | 2484.1905 | 2577.2206
DEER-SFAM-CZ11-V4-eSA-10-HL-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-HL | 8.5061 | 4.0132 | 2585.666 | 0 | 3.5 | 2585.666 | 2678.7417
DEER-SFAM-CZ11-V4-eSA-10-HM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-HM | 8.5479 | 3.8389 | 2520.1806 | 0 | 3.5 | 2520.1806 | 2613.248
DEER-SFAM-CZ11-V4-eSA-10-LH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-LH | 9.3191 | 3.6517 | 2455.2586 | 0 | 3.5 | 2455.2586 | 2548.3804
DEER-SFAM-CZ11-V4-eSA-10-LL-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-LL | 8.9388 | 3.727 | 2478.6542 | 0 | 3.5 | 2478.6542 | 2571.7405
DEER-SFAM-CZ11-V4-eSA-10-LM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-LM | 9.2351 | 3.6663 | 2446.9399 | 0 | 3.5 | 2446.9399 | 2540.0637
DEER-SFAM-CZ11-V4-eSA-10-MH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-MH | 9.115 | 3.5719 | 2478.0458 | 0 | 3.5 | 2478.0458 | 2571.1516
DEER-SFAM-CZ11-V4-eSA-10-ML-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-ML | 8.6676 | 3.8143 | 2551.4458 | 0 | 3.5 | 2551.4458 | 2644.523
DEER-SFAM-CZ11-V4-eSA-10-MM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSA-10 | CZ11-V4-eSA-10-MM | 8.958 | 3.6637 | 2475.1252 | 0 | 3.5 | 2475.1252 | 2568.2069
DEER-SFAM-CZ11-V4-eSA-13-HH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-HH | 11.5154 | 3.2035 | 1971.5227 | 0 | 3.8 | 1971.5227 | 2055.4604
DEER-SFAM-CZ11-V4-eSA-13-HL-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-HL | 11.0758 | 3.268 | 1985.7679 | 0 | 3.5 | 1985.7679 | 2059.2008
DEER-SFAM-CZ11-V4-eSA-13-HM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-HM | 11.3476 | 3.1212 | 1934.1408 | 0 | 3.8 | 1934.1408 | 2018.0622
DEER-SFAM-CZ11-V4-eSA-13-LH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-LH | 11.7581 | 2.8261 | 1880.4753 | 0 | 3.5 | 1880.4753 | 1973.5646
DEER-SFAM-CZ11-V4-eSA-13-LL-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-LL | 11.3872 | 3.0651 | 1960.9383 | 0 | 3.5 | 1960.9383 | 2053.9178
DEER-SFAM-CZ11-V4-eSA-13-LM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-LM | 11.1675 | 3.0016 | 1975.6106 | 0 | 3.5 | 1975.6106 | 2068.6545
DEER-SFAM-CZ11-V4-eSA-13-MH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-MH | 11.7747 | 3.0521 | 1921.7054 | 0 | 3.8 | 1921.7054 | 2014.818
DEER-SFAM-CZ11-V4-eSA-13-ML-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-ML | 10.959 | 3.0374 | 1936.7903 | 0 | 3.5 | 1936.7903 | 2029.5832
DEER-SFAM-CZ11-V4-eSA-13-MM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSA-13 | CZ11-V4-eSA-13-MM | 11.8758 | 2.9746 | 1858.1274 | 0 | 3.8 | 1858.1274 | 1951.2326
DEER-SFAM-CZ11-V4-eSA-14-HH-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-HH | 11.1607 | 2.9324 | 1895.7568 | 0 | 3.5 | 1895.7568 | 1973.7658
DEER-SFAM-CZ11-V4-eSA-14-HL-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-HL | 12.2987 | 2.9532 | 1813.7667 | 0 | 3.8 | 1813.7667 | 1871.1566
DEER-SFAM-CZ11-V4-eSA-14-HM-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-HM | 11.7598 | 3.0412 | 1910.9062 | 0 | 3.5 | 1910.9062 | 1998.8933
DEER-SFAM-CZ11-V4-eSA-14-MH-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-MH | 11.9982 | 2.8155 | 1879.3986 | 0 | 3.5 | 1879.3986 | 1940.5657
DEER-SFAM-CZ11-V4-eSA-14-ML-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-ML | 11.7648 | 2.9678 | 1852.4507 | 0 | 3.5 | 1852.4507 | 1950.1111
DEER-SFAM-CZ11-V4-eSA-14-MM-s1 | 14 | CZ11 | V4 | CZ11-V4-eSA-14 | CZ11-V4-eSA-14-MM | 11.9119 | 2.8297 | 1845.8213 | 0 | 3.5 | 1845.8213 | 1912.8691
DEER-SFAM-CZ11-V4-eSA-15-HH-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-HH | 12.8249 | 2.7396 | 1713.1998 | 0 | 3.8 | 1713.1998 | 1778.2535
DEER-SFAM-CZ11-V4-eSA-15-HL-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-HL | 13.2245 | 2.7683 | 1677.9585 | 0 | 3.8 | 1677.9585 | 1759.0579
DEER-SFAM-CZ11-V4-eSA-15-HM-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-HM | 13.0419 | 2.6432 | 1680.2501 | 0 | 3.8 | 1680.2501 | 1745.5507
DEER-SFAM-CZ11-V4-eSA-15-MH-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-MH | 12.1989 | 2.8667 | 1789.1969 | 0 | 3.5 | 1789.1969 | 1837.6472
DEER-SFAM-CZ11-V4-eSA-15-ML-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-ML | 13.0681 | 2.7316 | 1719.5783 | 0 | 3.5 | 1719.5783 | 1784.7795
DEER-SFAM-CZ11-V4-eSA-15-MM-s1 | 15 | CZ11 | V4 | CZ11-V4-eSA-15 | CZ11-V4-eSA-15-MM | 12.7795 | 2.7674 | 1724.0918 | 0 | 3.5 | 1724.0918 | 1783.5033
DEER-SFAM-CZ11-V4-eSA-16-CH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-CH | 13.8079 | 2.9013 | 1854.43 | 0 | 3.5 | 1854.43 | 1892.016
DEER-SFAM-CZ11-V4-eSA-16-CL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-CL | 14.172 | 2.7702 | 1735.8234 | 0 | 3.8 | 1735.8234 | 1783.3753
DEER-SFAM-CZ11-V4-eSA-16-CM-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-CM | 13.8149 | 2.8321 | 1805.3589 | 0 | 3.8 | 1805.3589 | 1855.5114
DEER-SFAM-CZ11-V4-eSA-16-LH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-LH | 13.578 | 2.5885 | 1638.497 | 0 | 3.5 | 1638.497 | 1702.9568
DEER-SFAM-CZ11-V4-eSA-16-LL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-LL | 13.1885 | 2.7632 | 1707.9043 | 0 | 3.5 | 1707.9043 | 1750.1937
DEER-SFAM-CZ11-V4-eSA-16-LM-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-LM | 13.1369 | 2.7018 | 1711.4999 | 0 | 3.5 | 1711.4999 | 1749.8409
DEER-SFAM-CZ11-V4-eSA-16-NM-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-NM | 14.9937 | 2.4418 | 1518.4383 | 0 | 3.5 | 1518.4383 | 1556.1052
DEER-SFAM-CZ11-V4-eSA-16-TH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-TH | 12.9843 | 3.023 | 1950.9269 | 0 | 3.5 | 1950.9269 | 1975.085
DEER-SFAM-CZ11-V4-eSA-16-TL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSA-16 | CZ11-V4-eSA-16-TL | 14.215 | 2.8767 | 1718.1973 | 0 | 3.8 | 1718.1973 | 1744.2713
DEER-SFAM-CZ11-V4-eSA-17-CH-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-CH | 14.6106 | 2.7508 | 1717.1699 | 0 | 3.5 | 1717.1699 | 1764.6788
DEER-SFAM-CZ11-V4-eSA-17-CL-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-CL | 14.6076 | 2.6977 | 1698.9319 | 0 | 3.5 | 1698.9319 | 1746.4281
DEER-SFAM-CZ11-V4-eSA-17-CM-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-CM | 14.747 | 2.7972 | 1721.4892 | 0 | 3.8 | 1721.4892 | 1758.9978
DEER-SFAM-CZ11-V4-eSA-17-LH-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-LH | 13.9714 | 2.5473 | 1597.5124 | 0 | 3.5 | 1597.5124 | 1648.0133
DEER-SFAM-CZ11-V4-eSA-17-LL-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-LL | 13.8371 | 2.6664 | 1639.2656 | 0 | 3.5 | 1639.2656 | 1666.7257
DEER-SFAM-CZ11-V4-eSA-17-LM-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-LM | 13.6966 | 2.6326 | 1644.2705 | 0 | 3.5 | 1644.2705 | 1667.9985
DEER-SFAM-CZ11-V4-eSA-17-TH-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-TH | 14.446 | 2.6703 | 1694.6151 | 0 | 3.5 | 1694.6151 | 1733.2291
DEER-SFAM-CZ11-V4-eSA-17-TL-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-TL | 15.7101 | 2.667 | 1506.3788 | 0 | 3.8 | 1506.3788 | 1566.7746
DEER-SFAM-CZ11-V4-eSA-17-TM-s2 | 17 | CZ11 | V4 | CZ11-V4-eSA-17 | CZ11-V4-eSA-17-TM | 15.3116 | 2.8822 | 1746.5237 | 0 | 3.8 | 1746.5237 | 1766.7075
DEER-SFAM-CZ11-V4-eSA-18-LH-s2 | 18 | CZ11 | V4 | CZ11-V4-eSA-18 | CZ11-V4-eSA-18-LH | 14.5974 | 2.4626 | 1541.828 | 0 | 3.5 | 1541.828 | 1574.8911
DEER-SFAM-CZ11-V4-eSA-18-LL-s2 | 18 | CZ11 | V4 | CZ11-V4-eSA-18 | CZ11-V4-eSA-18-LL | 14.8727 | 2.4811 | 1504.7777 | 0 | 3.5 | 1504.7777 | 1547.9534
DEER-SFAM-CZ11-V4-eSA-18-TH-s2 | 18 | CZ11 | V4 | CZ11-V4-eSA-18 | CZ11-V4-eSA-18-TH | 15.0846 | 2.5585 | 1635.9619 | 0 | 3.8 | 1635.9619 | 1662.1978
DEER-SFAM-CZ11-V4-eSA-18-TL-s2 | 18 | CZ11 | V4 | CZ11-V4-eSA-18 | CZ11-V4-eSA-18-TL | 14.8047 | 2.9596 | 1738.1463 | 0 | 3.8 | 1738.1463 | 1767.0023
DEER-SFAM-CZ11-V4-eSA-18-TM-s2 | 18 | CZ11 | V4 | CZ11-V4-eSA-18 | CZ11-V4-eSA-18-TM | 14.5547 | 2.5974 | 1668.0006 | 0 | 3.5 | 1668.0006 | 1694.8092
DEER-SFAM-CZ11-V4-eSH-10-HH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-HH | 9.0528 | 3.725 | 2453.4512 | 2102.1489 | 3.8 | 4555.6001 | 2661.9001
DEER-SFAM-CZ11-V4-eSH-10-HL-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-HL | 8.8255 | 3.9098 | 2511.0924 | 2108.7076 | 3.8 | 4619.8 | 2715.3
DEER-SFAM-CZ11-V4-eSH-10-HM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-HM | 9.1915 | 3.7846 | 2481.4974 | 2075.4176 | 3.5 | 4556.915 | 2677.515
DEER-SFAM-CZ11-V4-eSH-10-LH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-LH | 9.2517 | 3.5432 | 2445.283 | 2178.3557 | 3.5 | 4623.6387 | 2659.9387
DEER-SFAM-CZ11-V4-eSH-10-LL-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-LL | 9.2527 | 3.6815 | 2430.848 | 2132.9416 | 3.5 | 4563.7896 | 2654.8896
DEER-SFAM-CZ11-V4-eSH-10-LM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-LM | 9.4472 | 3.5363 | 2391.8091 | 2121.1662 | 3.5 | 4512.9753 | 2597.6753
DEER-SFAM-CZ11-V4-eSH-10-MH-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-MH | 9.2929 | 3.67 | 2455.1296 | 2156.7337 | 3.5 | 4611.8633 | 2682.7633
DEER-SFAM-CZ11-V4-eSH-10-ML-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-ML | 9.1722 | 3.8664 | 2475.8665 | 2022.8407 | 3.5 | 4498.7072 | 2684.5072
DEER-SFAM-CZ11-V4-eSH-10-MM-s1 | 10 | CZ11 | V4 | CZ11-V4-eSH-10 | CZ11-V4-eSH-10-MM | 9.1687 | 3.7455 | 2491.9511 | 2107.8993 | 3.5 | 4599.8504 | 2685.5504
DEER-SFAM-CZ11-V4-eSH-13-HH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-HH | 10.7028 | 3.2026 | 2047.3364 | 2025.585 | 3.8 | 4072.9214 | 2237.8214
DEER-SFAM-CZ11-V4-eSH-13-HL-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-HL | 11.8791 | 3.286 | 1923.3251 | 1745.9857 | 3.8 | 3669.3108 | 2112.8108
DEER-SFAM-CZ11-V4-eSH-13-HM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-HM | 11.0442 | 3.1305 | 1983.4934 | 1816.071 | 3.8 | 3799.5644 | 2155.6644
DEER-SFAM-CZ11-V4-eSH-13-LH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-LH | 11.4833 | 2.9157 | 1933.7828 | 2047.663 | 3.5 | 3981.4458 | 2217.6458
DEER-SFAM-CZ11-V4-eSH-13-LL-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-LL | 12.368 | 2.9324 | 1835.4278 | 1824.2144 | 3.5 | 3659.6422 | 2009.8422
DEER-SFAM-CZ11-V4-eSH-13-LM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-LM | 10.9473 | 3.0691 | 2000.7816 | 1586.963 | 3.5 | 3587.7446 | 2197.6446
DEER-SFAM-CZ11-V4-eSH-13-MH-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-MH | 11.7277 | 2.9603 | 1900.8694 | 2050.0114 | 3.8 | 3950.8808 | 2090.7808
DEER-SFAM-CZ11-V4-eSH-13-ML-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-ML | 10.8618 | 3.2947 | 2042.9885 | 1842.4947 | 3.5 | 3885.4832 | 2237.5832
DEER-SFAM-CZ11-V4-eSH-13-MM-s1 | 13 | CZ11 | V4 | CZ11-V4-eSH-13 | CZ11-V4-eSH-13-MM | 11.5904 | 3.1274 | 1960.45 | 1893.7181 | 3.5 | 3854.1681 | 2112.4681
DEER-SFAM-CZ11-V4-eSH-14-HH-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-HH | 11.397 | 3.0512 | 1919.7086 | 1854.7128 | 3.8 | 3774.4214 | 2064.8214
DEER-SFAM-CZ11-V4-eSH-14-HL-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-HL | 11.9144 | 2.9661 | 1834.6589 | 1806.5425 | 3.8 | 3641.2014 | 2008.4014
DEER-SFAM-CZ11-V4-eSH-14-HM-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-HM | 11.8044 | 2.8762 | 1844.5738 | 1812.7655 | 3.8 | 3657.3393 | 1968.9393
DEER-SFAM-CZ11-V4-eSH-14-MH-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-MH | 12.2815 | 2.7225 | 1800.634 | 1882.5162 | 3.5 | 3683.1502 | 1989.8502
DEER-SFAM-CZ11-V4-eSH-14-ML-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-ML | 12.4406 | 2.8586 | 1788.2529 | 1917.8454 | 3.8 | 3706.0983 | 2023.3983
DEER-SFAM-CZ11-V4-eSH-14-MM-s1 | 14 | CZ11 | V4 | CZ11-V4-eSH-14 | CZ11-V4-eSH-14-MM | 12.1856 | 2.8356 | 1798.5764 | 1746.6546 | 3.5 | 3545.231 | 1961.531
DEER-SFAM-CZ11-V4-eSH-15-HH-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-HH | 12.7167 | 2.6507 | 1713.364 | 2036.6856 | 3.8 | 3750.0496 | 1848.0496
DEER-SFAM-CZ11-V4-eSH-15-HL-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-HL | 13.043 | 2.7867 | 1708.5922 | 1575.7625 | 3.8 | 3284.3547 | 1841.7547
DEER-SFAM-CZ11-V4-eSH-15-HM-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-HM | 13.2327 | 2.6839 | 1670.7701 | 1650.844 | 3.8 | 3321.6141 | 1802.9141
DEER-SFAM-CZ11-V4-eSH-15-MH-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-MH | 12.7861 | 2.7584 | 1751.8174 | 1795.406 | 3.5 | 3547.2234 | 1879.2234
DEER-SFAM-CZ11-V4-eSH-15-ML-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-ML | 13.3119 | 2.7006 | 1670.1088 | 1710.5558 | 3.8 | 3380.6646 | 1802.9646
DEER-SFAM-CZ11-V4-eSH-15-MM-s1 | 15 | CZ11 | V4 | CZ11-V4-eSH-15 | CZ11-V4-eSH-15-MM | 13.4398 | 2.6858 | 1661.1099 | 1850.8515 | 3.8 | 3511.9614 | 1803.1614
DEER-SFAM-CZ11-V4-eSH-16-CH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-CH | 13.9462 | 2.784 | 1795.5523 | 1849.7371 | 3.8 | 3645.2894 | 1910.8894
DEER-SFAM-CZ11-V4-eSH-16-CL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-CL | 14.1746 | 3.0505 | 1824.9265 | 1725.8216 | 3.8 | 3550.7481 | 1945.1481
DEER-SFAM-CZ11-V4-eSH-16-LH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-LH | 13.1093 | 2.6185 | 1689.4157 | 1930.9713 | 3.5 | 3620.387 | 1823.087
DEER-SFAM-CZ11-V4-eSH-16-LL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-LL | 13.1157 | 2.7787 | 1711.2403 | 1762.676 | 3.5 | 3473.9163 | 1818.7163
DEER-SFAM-CZ11-V4-eSH-16-LM-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-LM | 12.7974 | 2.7387 | 1740.1008 | 1924.0732 | 3.5 | 3664.174 | 1889.474
DEER-SFAM-CZ11-V4-eSH-16-TH-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-TH | 13.9631 | 2.8704 | 1751.7269 | 2308.4092 | 3.8 | 4060.1361 | 1861.5361
DEER-SFAM-CZ11-V4-eSH-16-TL-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-TL | 13.379 | 3.1002 | 1913.7352 | 2271.8237 | 3.5 | 4185.5589 | 2019.5589
DEER-SFAM-CZ11-V4-eSH-16-TM-s2 | 16 | CZ11 | V4 | CZ11-V4-eSH-16 | CZ11-V4-eSH-16-TM | 13.5366 | 3.0439 | 1891.937 | 2307.851 | 3.5 | 4199.788 | 2000.888
DEER-SFAM-CZ11-V4-eSH-17-CM-s2 | 17 | CZ11 | V4 | CZ11-V4-eSH-17 | CZ11-V4-eSH-17-CM | 14.9388 | 2.9006 | 1729.5398 | 1792.2377 | 3.8 | 3521.7775 | 1854.9775
DEER-SFAM-CZ11-V4-eSH-17-LM-s2 | 17 | CZ11 | V4 | CZ11-V4-eSH-17 | CZ11-V4-eSH-17-LM | 13.7017 | 2.7476 | 1684.4004 | 1714.0744 | 3.5 | 3398.4748 | 1744.7748
DEER-SFAM-CZ11-V4-eSH-17-TH-s2 | 17 | CZ11 | V4 | CZ11-V4-eSH-17 | CZ11-V4-eSH-17-TH | 14.6127 | 2.7534 | 1666.9255 | 2305.5557 | 3.8 | 3972.4812 | 1785.5812
DEER-SFAM-CZ11-V4-eSH-17-TL-s2 | 17 | CZ11 | V4 | CZ11-V4-eSH-17 | CZ11-V4-eSH-17-TL | 14.6394 | 2.7925 | 1671.8031 | 2278.4086 | 3.8 | 3950.2117 | 1788.7117
DEER-SFAM-CZ11-V4-eSH-18-LH-s2 | 18 | CZ11 | V4 | CZ11-V4-eSH-18 | CZ11-V4-eSH-18-LH | 14.3496 | 2.5709 | 1566.6584 | 1938.2797 | 3.5 | 3504.9381 | 1663.8381
DEER-SFAM-CZ11-V4-eSH-18-LL-s2 | 18 | CZ11 | V4 | CZ11-V4-eSH-18 | CZ11-V4-eSH-18-LL | 13.7526 | 2.6622 | 1623.5686 | 1753.3185 | 3.5 | 3376.8871 | 1716.0871
DEER-SFAM-CZ11-V4-eSH-18-LM-s2 | 18 | CZ11 | V4 | CZ11-V4-eSH-18 | CZ11-V4-eSH-18-LM | 14.494 | 2.576 | 1559.5097 | 2031.0187 | 3.5 | 3590.5284 | 1670.3284
DEER-SFAM-CZ11-V4-eSH-18-TM-s2 | 18 | CZ11 | V4 | CZ11-V4-eSH-18 | CZ11-V4-eSH-18-TM | 15.1419 | 2.7202 | 1660.213 | 2296.6991 | 3.5 | 3956.9121 | 1849.9121
DEER-SFAM-CZ12-V1-eSA-10-HH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-HH | 9.6569 | 4.0834 | 2229.347 | 0 | 3.5124 | 2229.347 | 2444.1631
DEER-SFAM-CZ12-V1-eSA-10-HL-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-HL | 8.9549 | 4.5442 | 2342.2219 | 0 | 3.5124 | 2342.2219 | 2557.1873
DEER-SFAM-CZ12-V1-eSA-10-HM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-HM | 8.9836 | 4.221 | 2275.1898 | 0 | 3.5124 | 2275.1898 | 2490.1294
DEER-SFAM-CZ12-V1-eSA-10-LH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-LH | 10.4617 | 3.9166 | 2130.5474 | 0 | 3.5124 | 2130.5474 | 2345.6626
DEER-SFAM-CZ12-V1-eSA-10-LL-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-LL | 9.3011 | 4.2074 | 2258.8945 | 0 | 3.5124 | 2258.8945 | 2473.8941
DEER-SFAM-CZ12-V1-eSA-10-LM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-LM | 10.284 | 3.9675 | 2145.9062 | 0 | 3.5124 | 2145.9062 | 2361.0275
DEER-SFAM-CZ12-V1-eSA-10-MH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-MH | 10.2756 | 3.8154 | 2143.4285 | 0 | 3.5124 | 2143.4285 | 2358.4914
DEER-SFAM-CZ12-V1-eSA-10-ML-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-ML | 9.1529 | 4.2839 | 2325.2908 | 0 | 3.5124 | 2325.2908 | 2540.2599
DEER-SFAM-CZ12-V1-eSA-10-MM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSA-10 | CZ12-V1-eSA-10-MM | 9.954 | 4.0115 | 2137.4259 | 0 | 3.5124 | 2137.4259 | 2352.4107
DEER-SFAM-CZ12-V1-eSA-13-HH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-HH | 11.9092 | 3.3984 | 1739.4426 | 0 | 3.5124 | 1739.4426 | 1933.2129
DEER-SFAM-CZ12-V1-eSA-13-HL-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-HL | 12.205 | 3.5559 | 1727.23 | 0 | 3.5124 | 1727.23 | 1896.8201
DEER-SFAM-CZ12-V1-eSA-13-HM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-HM | 11.9625 | 3.4787 | 1738.6286 | 0 | 3.5124 | 1738.6286 | 1932.3425
DEER-SFAM-CZ12-V1-eSA-13-LH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-LH | 13.0692 | 3.0663 | 1639.5642 | 0 | 3.5124 | 1639.5642 | 1854.5749
DEER-SFAM-CZ12-V1-eSA-13-LL-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-LL | 12.5276 | 3.3194 | 1724.1827 | 0 | 3.5124 | 1724.1827 | 1938.8374
DEER-SFAM-CZ12-V1-eSA-13-LM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-LM | 12.5823 | 3.1914 | 1705.161 | 0 | 3.5124 | 1705.161 | 1920.023
DEER-SFAM-CZ12-V1-eSA-13-MH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-MH | 13.0159 | 3.2168 | 1681.55 | 0 | 3.5124 | 1681.55 | 1896.4906
DEER-SFAM-CZ12-V1-eSA-13-ML-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-ML | 11.8968 | 3.4168 | 1703.7782 | 0 | 3.5124 | 1703.7782 | 1918.0653
DEER-SFAM-CZ12-V1-eSA-13-MM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSA-13 | CZ12-V1-eSA-13-MM | 12.9209 | 3.3126 | 1669.646 | 0 | 3.5124 | 1669.646 | 1884.5603
DEER-SFAM-CZ12-V1-eSA-14-HH-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-HH | 12.1278 | 3.2606 | 1662.5257 | 0 | 3.5124 | 1662.5257 | 1842.672
DEER-SFAM-CZ12-V1-eSA-14-HL-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-HL | 13.4255 | 3.2666 | 1606.2978 | 0 | 3.5124 | 1606.2978 | 1738.7638
DEER-SFAM-CZ12-V1-eSA-14-HM-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-HM | 13.165 | 3.3054 | 1644.1701 | 0 | 3.5124 | 1644.1701 | 1847.3929
DEER-SFAM-CZ12-V1-eSA-14-MH-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-MH | 13.5436 | 2.9671 | 1621.0042 | 0 | 3.5124 | 1621.0042 | 1762.2396
DEER-SFAM-CZ12-V1-eSA-14-ML-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-ML | 12.9743 | 3.1926 | 1604.2929 | 0 | 3.5124 | 1604.2929 | 1829.8418
DEER-SFAM-CZ12-V1-eSA-14-MM-s1 | 14 | CZ12 | V1 | CZ12-V1-eSA-14 | CZ12-V1-eSA-14-MM | 13.4475 | 2.9941 | 1588.784 | 0 | 3.5124 | 1588.784 | 1743.6188
DEER-SFAM-CZ12-V1-eSA-15-HH-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-HH | 13.6135 | 3.0237 | 1516.7625 | 0 | 3.5124 | 1516.7625 | 1666.9322
DEER-SFAM-CZ12-V1-eSA-15-HL-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-HL | 14.3796 | 3.0442 | 1479.7758 | 0 | 3.5124 | 1479.7758 | 1666.9545
DEER-SFAM-CZ12-V1-eSA-15-HM-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-HM | 13.5546 | 2.933 | 1504.7804 | 0 | 3.5124 | 1504.7804 | 1655.5102
DEER-SFAM-CZ12-V1-eSA-15-MH-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-MH | 13.7573 | 3.0535 | 1529.7234 | 0 | 3.5124 | 1529.7234 | 1641.6183
DEER-SFAM-CZ12-V1-eSA-15-ML-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-ML | 14.385 | 2.9871 | 1510.4481 | 0 | 3.5124 | 1510.4481 | 1660.96
DEER-SFAM-CZ12-V1-eSA-15-MM-s1 | 15 | CZ12 | V1 | CZ12-V1-eSA-15 | CZ12-V1-eSA-15-MM | 14.2132 | 3.0139 | 1498.5996 | 0 | 3.5124 | 1498.5996 | 1635.808
DEER-SFAM-CZ12-V1-eSA-16-CH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-CH | 14.0189 | 3.2164 | 1844.7116 | 0 | 3.5124 | 1844.7116 | 1930.349
DEER-SFAM-CZ12-V1-eSA-16-CL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-CL | 14.1802 | 3.2655 | 1736.9332 | 0 | 3.5124 | 1736.9332 | 1845.953
DEER-SFAM-CZ12-V1-eSA-16-CM-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-CM | 13.938 | 3.2818 | 1791.683 | 0 | 3.5124 | 1791.683 | 1906.85
DEER-SFAM-CZ12-V1-eSA-16-LH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-LH | 13.9853 | 3.027 | 1570.8967 | 0 | 3.5124 | 1570.8967 | 1718.3991
DEER-SFAM-CZ12-V1-eSA-16-LL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-LL | 13.476 | 3.2735 | 1670.3725 | 0 | 3.5124 | 1670.3725 | 1767.0825
DEER-SFAM-CZ12-V1-eSA-16-LM-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-LM | 13.634 | 3.1536 | 1650.2929 | 0 | 3.5124 | 1650.2929 | 1737.9069
DEER-SFAM-CZ12-V1-eSA-16-NM-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-NM | 15.0661 | 2.9637 | 1514.3261 | 0 | 3.5124 | 1514.3261 | 1600.2777
DEER-SFAM-CZ12-V1-eSA-16-TH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-TH | 13.5193 | 3.4784 | 1941.9003 | 0 | 3.5124 | 1941.9003 | 1996.2883
DEER-SFAM-CZ12-V1-eSA-16-TL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSA-16 | CZ12-V1-eSA-16-TL | 14.1985 | 3.3061 | 1773.1952 | 0 | 3.5124 | 1773.1952 | 1831.8919
DEER-SFAM-CZ12-V1-eSA-17-CH-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-CH | 14.8355 | 3.0965 | 1705.0386 | 0 | 3.5124 | 1705.0386 | 1813.9796
DEER-SFAM-CZ12-V1-eSA-17-CL-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-CL | 14.7283 | 3.1536 | 1705.127 | 0 | 3.5124 | 1705.127 | 1814.0459
DEER-SFAM-CZ12-V1-eSA-17-CM-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-CM | 14.8355 | 3.14 | 1730.3237 | 0 | 3.5124 | 1730.3237 | 1815.7038
DEER-SFAM-CZ12-V1-eSA-17-LH-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-LH | 14.464 | 2.9631 | 1521.4493 | 0 | 3.5124 | 1521.4493 | 1637.0335
DEER-SFAM-CZ12-V1-eSA-17-LL-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-LL | 14.1951 | 3.1449 | 1605.0315 | 0 | 3.5124 | 1605.0315 | 1667.8442
DEER-SFAM-CZ12-V1-eSA-17-LM-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-LM | 14.0815 | 3.0808 | 1593.7968 | 0 | 3.5124 | 1593.7968 | 1648.0431
DEER-SFAM-CZ12-V1-eSA-17-TH-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-TH | 15.4036 | 2.9773 | 1609.0738 | 0 | 3.5124 | 1609.0738 | 1696.3267
DEER-SFAM-CZ12-V1-eSA-17-TL-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-TL | 15.522 | 3.0195 | 1516.6378 | 0 | 3.5124 | 1516.6378 | 1654.462
DEER-SFAM-CZ12-V1-eSA-17-TM-s2 | 17 | CZ12 | V1 | CZ12-V1-eSA-17 | CZ12-V1-eSA-17-TM | 15.4511 | 3.1704 | 1835.5066 | 0 | 3.5124 | 1835.5066 | 1880.7327
DEER-SFAM-CZ12-V1-eSA-18-LH-s2 | 18 | CZ12 | V1 | CZ12-V1-eSA-18 | CZ12-V1-eSA-18-LH | 15.0421 | 2.9059 | 1500.7712 | 0 | 3.5124 | 1500.7712 | 1576.3277
DEER-SFAM-CZ12-V1-eSA-18-LL-s2 | 18 | CZ12 | V1 | CZ12-V1-eSA-18 | CZ12-V1-eSA-18-LL | 15.2976 | 2.8852 | 1450.5818 | 0 | 3.5124 | 1450.5818 | 1549.2182
DEER-SFAM-CZ12-V1-eSA-18-TH-s2 | 18 | CZ12 | V1 | CZ12-V1-eSA-18 | CZ12-V1-eSA-18-TH | 16.0332 | 2.8321 | 1556.1975 | 0 | 3.5124 | 1556.1975 | 1615.4877
DEER-SFAM-CZ12-V1-eSA-18-TL-s2 | 18 | CZ12 | V1 | CZ12-V1-eSA-18 | CZ12-V1-eSA-18-TL | 15.3608 | 3.154 | 1710.4819 | 0 | 3.5124 | 1710.4819 | 1775.6948
DEER-SFAM-CZ12-V1-eSA-18-TM-s2 | 18 | CZ12 | V1 | CZ12-V1-eSA-18 | CZ12-V1-eSA-18-TM | 15.4888 | 2.9153 | 1589.7357 | 0 | 3.5124 | 1589.7357 | 1650.3475
DEER-SFAM-CZ12-V1-eSH-10-HH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-HH | 9.955 | 4.0602 | 2157.9161 | 4858.1361 | 3.5124 | 7016.0521 | 2657.2718
DEER-SFAM-CZ12-V1-eSH-10-HL-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-HL | 9.6035 | 4.2025 | 2241.7367 | 4886.9597 | 3.5124 | 7128.6964 | 2732.6566
DEER-SFAM-CZ12-V1-eSH-10-HM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-HM | 10.0453 | 4.1789 | 2198.549 | 4706.1368 | 3.5124 | 6904.6858 | 2670.9224
DEER-SFAM-CZ12-V1-eSH-10-LH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-LH | 10.3922 | 3.7855 | 2111.9871 | 5145.318 | 3.5124 | 7257.3051 | 2625.7406
DEER-SFAM-CZ12-V1-eSH-10-LL-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-LL | 10.0027 | 4.0313 | 2178.9804 | 5063.3045 | 3.5124 | 7242.2849 | 2715.6079
DEER-SFAM-CZ12-V1-eSH-10-LM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-LM | 10.2369 | 3.9125 | 2135.9032 | 4916.1122 | 3.5124 | 7052.0154 | 2626.2026
DEER-SFAM-CZ12-V1-eSH-10-MH-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-MH | 10.396 | 3.9584 | 2134.1377 | 5115.4222 | 3.5124 | 7249.5598 | 2680.5402
DEER-SFAM-CZ12-V1-eSH-10-ML-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-ML | 9.9198 | 4.2463 | 2217.3735 | 4724.5136 | 3.5124 | 6941.8871 | 2713.147
DEER-SFAM-CZ12-V1-eSH-10-MM-s1 | 10 | CZ12 | V1 | CZ12-V1-eSH-10 | CZ12-V1-eSH-10-MM | 10.0432 | 4.0994 | 2207.0669 | 4927.7703 | 3.5124 | 7134.8372 | 2668.4548
DEER-SFAM-CZ12-V1-eSH-13-HH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-HH | 11.5098 | 3.4824 | 1805.2678 | 4816.7276 | 3.5124 | 6621.9954 | 2258.49
DEER-SFAM-CZ12-V1-eSH-13-HL-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-HL | 12.5838 | 3.5086 | 1715.6639 | 4177.124 | 3.5124 | 5892.7879 | 2168.5299
DEER-SFAM-CZ12-V1-eSH-13-HM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-HM | 11.7682 | 3.4427 | 1775.2955 | 4258.2807 | 3.5124 | 6033.5762 | 2184.7702
DEER-SFAM-CZ12-V1-eSH-13-LH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-LH | 12.9708 | 3.0926 | 1662.4288 | 5367.8888 | 3.5124 | 7030.3175 | 2343.4914
DEER-SFAM-CZ12-V1-eSH-13-LL-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-LL | 13.3437 | 3.2373 | 1645.9885 | 4475.9926 | 3.5124 | 6121.9811 | 2061.5177
DEER-SFAM-CZ12-V1-eSH-13-LM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-LM | 12.3486 | 3.2564 | 1724.7955 | 3764.2731 | 3.5124 | 5489.0686 | 2195.6057
DEER-SFAM-CZ12-V1-eSH-13-MH-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-MH | 13.0954 | 3.2225 | 1647.5888 | 4912.1115 | 3.5124 | 6559.7002 | 2102.8183
DEER-SFAM-CZ12-V1-eSH-13-ML-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-ML | 12.167 | 3.4684 | 1752.2108 | 4598.8313 | 3.5124 | 6351.0421 | 2220.4013
DEER-SFAM-CZ12-V1-eSH-13-MM-s1 | 13 | CZ12 | V1 | CZ12-V1-eSH-13 | CZ12-V1-eSH-13-MM | 12.7204 | 3.4534 | 1722.085 | 4448.1362 | 3.5124 | 6170.2212 | 2084.0044
DEER-SFAM-CZ12-V1-eSH-14-HH-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-HH | 12.154 | 3.3301 | 1708.0264 | 4415.3066 | 3.5124 | 6123.3329 | 2053.2923
DEER-SFAM-CZ12-V1-eSH-14-HL-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-HL | 12.4542 | 3.2843 | 1662.6409 | 4472.3829 | 3.5124 | 6135.0238 | 2078.9525
DEER-SFAM-CZ12-V1-eSH-14-HM-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-HM | 12.4158 | 3.1676 | 1657.3079 | 4390.2042 | 3.5124 | 6047.5122 | 1953.0411
DEER-SFAM-CZ12-V1-eSH-14-MH-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-MH | 13.785 | 2.9082 | 1554.0518 | 4855.8418 | 3.5124 | 6409.8936 | 2003.5831
DEER-SFAM-CZ12-V1-eSH-14-ML-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-ML | 13.7209 | 3.1889 | 1572.1933 | 5228.0955 | 3.5124 | 6800.2888 | 2142.0062
DEER-SFAM-CZ12-V1-eSH-14-MM-s1 | 14 | CZ12 | V1 | CZ12-V1-eSH-14 | CZ12-V1-eSH-14-MM | 13.5041 | 3.073 | 1570.7054 | 4363.7786 | 3.5124 | 5934.4841 | 1961.362
DEER-SFAM-CZ12-V1-eSH-15-HH-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-HH | 13.3084 | 2.9248 | 1527.6977 | 5437.488 | 3.5124 | 6965.1856 | 1847.5951
DEER-SFAM-CZ12-V1-eSH-15-HL-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-HL | 13.6199 | 3.0877 | 1540.2773 | 3742.6624 | 3.5124 | 5282.9397 | 1858.2993
DEER-SFAM-CZ12-V1-eSH-15-HM-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-HM | 14.4786 | 2.9714 | 1472.3793 | 3933.8987 | 3.5124 | 5406.278 | 1790.5017
DEER-SFAM-CZ12-V1-eSH-15-MH-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-MH | 14.3612 | 3.0256 | 1505.8404 | 4781.5711 | 3.5124 | 6287.4115 | 1815.1165
DEER-SFAM-CZ12-V1-eSH-15-ML-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-ML | 14.6079 | 3.0194 | 1472.594 | 4517.2151 | 3.5124 | 5989.8092 | 1794.3801
DEER-SFAM-CZ12-V1-eSH-15-MM-s1 | 15 | CZ12 | V1 | CZ12-V1-eSH-15 | CZ12-V1-eSH-15-MM | 14.6591 | 2.954 | 1468.907 | 4683.5586 | 3.5124 | 6152.4655 | 1806.0484
DEER-SFAM-CZ12-V1-eSH-16-CH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-CH | 14.1902 | 3.1834 | 1779.633 | 5077.9112 | 3.5124 | 6857.5442 | 2101.3014
DEER-SFAM-CZ12-V1-eSH-16-CL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-CL | 14.3644 | 3.2507 | 1823.4901 | 4737.5059 | 3.5124 | 6560.996 | 2155.7257
DEER-SFAM-CZ12-V1-eSH-16-LH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-LH | 13.7805 | 3.0186 | 1583.2147 | 5324.1278 | 3.5124 | 6907.3424 | 1929.2615
DEER-SFAM-CZ12-V1-eSH-16-LL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-LL | 13.5421 | 3.2305 | 1643.8566 | 4975.0448 | 3.5124 | 6618.9014 | 1926.7838
DEER-SFAM-CZ12-V1-eSH-16-LM-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-LM | 13.3964 | 3.1384 | 1640.8232 | 5394.9405 | 3.5124 | 7035.7637 | 2029.6658
DEER-SFAM-CZ12-V1-eSH-16-TH-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-TH | 14.4154 | 3.2943 | 1705.6697 | 6269.9136 | 3.5124 | 7975.5832 | 2063.4813
DEER-SFAM-CZ12-V1-eSH-16-TL-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-TL | 13.6579 | 3.5467 | 1940.0151 | 6252.3169 | 3.5124 | 8192.332 | 2270.5434
DEER-SFAM-CZ12-V1-eSH-16-TM-s2 | 16 | CZ12 | V1 | CZ12-V1-eSH-16 | CZ12-V1-eSH-16-TM | 13.8436 | 3.4804 | 1914.6831 | 6308.8982 | 3.5124 | 8223.5814 | 2253.0705
DEER-SFAM-CZ12-V1-eSH-17-CM-s2 | 17 | CZ12 | V1 | CZ12-V1-eSH-17 | CZ12-V1-eSH-17-CM | 15.1633 | 3.0945 | 1724.7352 | 5189.7237 | 3.5124 | 6914.4589 | 2096.0326
DEER-SFAM-CZ12-V1-eSH-17-LM-s2 | 17 | CZ12 | V1 | CZ12-V1-eSH-17 | CZ12-V1-eSH-17-LM | 14.2591 | 3.0709 | 1643.4377 | 4808.6908 | 3.5124 | 6452.1285 | 1802.0727
DEER-SFAM-CZ12-V1-eSH-17-TH-s2 | 17 | CZ12 | V1 | CZ12-V1-eSH-17 | CZ12-V1-eSH-17-TH | 15.277 | 3.0771 | 1602.8412 | 6251.6531 | 3.5124 | 7854.4943 | 1982.5867
DEER-SFAM-CZ12-V1-eSH-17-TL-s2 | 17 | CZ12 | V1 | CZ12-V1-eSH-17 | CZ12-V1-eSH-17-TL | 15.1617 | 3.148 | 1621.5526 | 6248.8554 | 3.5124 | 7870.408 | 1997.9419
DEER-SFAM-CZ12-V1-eSH-18-LH-s2 | 18 | CZ12 | V1 | CZ12-V1-eSH-18 | CZ12-V1-eSH-18-LH | 15.0984 | 2.9368 | 1479.5476 | 5641.1621 | 3.5124 | 7120.7097 | 1755.8662
DEER-SFAM-CZ12-V1-eSH-18-LL-s2 | 18 | CZ12 | V1 | CZ12-V1-eSH-18 | CZ12-V1-eSH-18-LL | 14.4743 | 3.0175 | 1529.1352 | 5053.9724 | 3.5124 | 6583.1076 | 1775.0733
DEER-SFAM-CZ12-V1-eSH-18-LM-s2 | 18 | CZ12 | V1 | CZ12-V1-eSH-18 | CZ12-V1-eSH-18-LM | 15.0205 | 2.9846 | 1503.5054 | 5948.1215 | 3.5124 | 7451.627 | 1821.6613
DEER-SFAM-CZ12-V1-eSH-18-TM-s2 | 18 | CZ12 | V1 | CZ12-V1-eSH-18 | CZ12-V1-eSH-18-TM | 16.0985 | 3.0356 | 1551.381 | 6286.2577 | 3.5124 | 7837.6387 | 2095.0509
DEER-SFAM-CZ12-V2-eSA-10-HH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-HH | 9.7488 | 3.5814 | 2210.0627 | 0 | 3.074 | 2210.0627 | 2354.3212
DEER-SFAM-CZ12-V2-eSA-10-HL-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-HL | 9.0524 | 3.977 | 2325.539 | 0 | 3.074 | 2325.539 | 2469.9009
DEER-SFAM-CZ12-V2-eSA-10-HM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-HM | 9.0831 | 3.672 | 2258.6831 | 0 | 3.074 | 2258.6831 | 2403.0264
DEER-SFAM-CZ12-V2-eSA-10-LH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-LH | 10.4646 | 3.4358 | 2115.4724 | 0 | 3.074 | 2115.4724 | 2259.9368
DEER-SFAM-CZ12-V2-eSA-10-LL-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-LL | 9.3551 | 3.6908 | 2254.2739 | 0 | 3.074 | 2254.2739 | 2398.6599
DEER-SFAM-CZ12-V2-eSA-10-LM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-LM | 10.2995 | 3.4766 | 2131.2924 | 0 | 3.074 | 2131.2924 | 2275.761
DEER-SFAM-CZ12-V2-eSA-10-MH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-MH | 10.3155 | 3.3477 | 2124.9866 | 0 | 3.074 | 2124.9866 | 2269.416
DEER-SFAM-CZ12-V2-eSA-10-ML-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-ML | 9.2096 | 3.7562 | 2315.9393 | 0 | 3.074 | 2315.9393 | 2460.3034
DEER-SFAM-CZ12-V2-eSA-10-MM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSA-10 | CZ12-V2-eSA-10-MM | 10.0311 | 3.5148 | 2120.8835 | 0 | 3.074 | 2120.8835 | 2265.2591
DEER-SFAM-CZ12-V2-eSA-13-HH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-HH | 11.9529 | 3.2114 | 1748.6717 | 0 | 3.4592 | 1748.6717 | 1878.9049
DEER-SFAM-CZ12-V2-eSA-13-HL-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-HL | 12.3175 | 3.151 | 1715.061 | 0 | 3.074 | 1715.061 | 1828.9515
DEER-SFAM-CZ12-V2-eSA-13-HM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-HM | 11.9508 | 3.2683 | 1746.8716 | 0 | 3.4592 | 1746.8716 | 1877.0697
DEER-SFAM-CZ12-V2-eSA-13-LH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-LH | 13.1448 | 2.7051 | 1627.3867 | 0 | 3.074 | 1627.3867 | 1771.7796
DEER-SFAM-CZ12-V2-eSA-13-LL-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-LL | 12.5928 | 2.9325 | 1716.4506 | 0 | 3.074 | 1716.4506 | 1860.5973
DEER-SFAM-CZ12-V2-eSA-13-LM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-LM | 12.6478 | 2.8179 | 1696.5179 | 0 | 3.074 | 1696.5179 | 1840.8081
DEER-SFAM-CZ12-V2-eSA-13-MH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-MH | 12.9851 | 3.0363 | 1686.0214 | 0 | 3.4592 | 1686.0214 | 1830.484
DEER-SFAM-CZ12-V2-eSA-13-ML-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-ML | 12.0108 | 3.0195 | 1695.3676 | 0 | 3.074 | 1695.3676 | 1839.2716
DEER-SFAM-CZ12-V2-eSA-13-MM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSA-13 | CZ12-V2-eSA-13-MM | 12.9302 | 3.1027 | 1669.0052 | 0 | 3.4592 | 1669.0052 | 1813.4517
DEER-SFAM-CZ12-V2-eSA-14-HH-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-HH | 12.2627 | 2.8799 | 1651.7784 | 0 | 3.074 | 1651.7784 | 1772.7565
DEER-SFAM-CZ12-V2-eSA-14-HL-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-HL | 13.4605 | 3.0484 | 1605.0885 | 0 | 3.4592 | 1605.0885 | 1694.1225
DEER-SFAM-CZ12-V2-eSA-14-HM-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-HM | 13.2349 | 2.9176 | 1629.7075 | 0 | 3.074 | 1629.7075 | 1766.1846
DEER-SFAM-CZ12-V2-eSA-14-MH-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-MH | 13.5943 | 2.6176 | 1612.2632 | 0 | 3.074 | 1612.2632 | 1707.1103
DEER-SFAM-CZ12-V2-eSA-14-ML-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-ML | 13.0666 | 2.8277 | 1595.1064 | 0 | 3.074 | 1595.1064 | 1746.5749
DEER-SFAM-CZ12-V2-eSA-14-MM-s1 | 14 | CZ12 | V2 | CZ12-V2-eSA-14 | CZ12-V2-eSA-14-MM | 13.5114 | 2.6453 | 1580.2338 | 0 | 3.074 | 1580.2338 | 1684.214
DEER-SFAM-CZ12-V2-eSA-15-HH-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-HH | 13.6065 | 2.8453 | 1523.7891 | 0 | 3.4592 | 1523.7891 | 1624.7197
DEER-SFAM-CZ12-V2-eSA-15-HL-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-HL | 14.407 | 2.8479 | 1481.5085 | 0 | 3.4592 | 1481.5085 | 1607.3177
DEER-SFAM-CZ12-V2-eSA-15-HM-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-HM | 13.6141 | 2.7534 | 1508.7299 | 0 | 3.4592 | 1508.7299 | 1610.0385
DEER-SFAM-CZ12-V2-eSA-15-MH-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-MH | 13.8705 | 2.6995 | 1513.9684 | 0 | 3.074 | 1513.9684 | 1589.1145
DEER-SFAM-CZ12-V2-eSA-15-ML-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-ML | 14.48 | 2.6404 | 1502.3072 | 0 | 3.074 | 1502.3072 | 1603.3809
DEER-SFAM-CZ12-V2-eSA-15-MM-s1 | 15 | CZ12 | V2 | CZ12-V2-eSA-15 | CZ12-V2-eSA-15-MM | 14.2913 | 2.6665 | 1486.4865 | 0 | 3.074 | 1486.4865 | 1578.6317
DEER-SFAM-CZ12-V2-eSA-16-CH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-CH | 14.1 | 2.816 | 1775.573 | 0 | 3.074 | 1775.573 | 1833.9995
DEER-SFAM-CZ12-V2-eSA-16-CL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-CL | 14.3487 | 3.0219 | 1692.1099 | 0 | 3.4592 | 1692.1099 | 1766.2749
DEER-SFAM-CZ12-V2-eSA-16-CM-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-CM | 14.0548 | 3.0843 | 1753.0484 | 0 | 3.4592 | 1753.0484 | 1831.3743
DEER-SFAM-CZ12-V2-eSA-16-LH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-LH | 14.1942 | 2.6326 | 1527.2007 | 0 | 3.074 | 1527.2007 | 1627.15
DEER-SFAM-CZ12-V2-eSA-16-LL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-LL | 13.6554 | 2.8492 | 1624.7526 | 0 | 3.074 | 1624.7526 | 1690.2944
DEER-SFAM-CZ12-V2-eSA-16-LM-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-LM | 13.7735 | 2.7452 | 1607.4464 | 0 | 3.074 | 1607.4464 | 1666.8559
DEER-SFAM-CZ12-V2-eSA-16-NM-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-NM | 15.1772 | 2.5644 | 1480.7612 | 0 | 3.074 | 1480.7612 | 1539.0978
DEER-SFAM-CZ12-V2-eSA-16-TH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-TH | 13.7466 | 3.0333 | 1839.1465 | 0 | 3.074 | 1839.1465 | 1876.5417
DEER-SFAM-CZ12-V2-eSA-16-TL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSA-16 | CZ12-V2-eSA-16-TL | 14.4613 | 3.0577 | 1714.7367 | 0 | 3.4592 | 1714.7367 | 1755.0956
DEER-SFAM-CZ12-V2-eSA-17-CH-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-CH | 14.9396 | 2.954 | 1665.4913 | 0 | 3.4592 | 1665.4913 | 1739.6272
DEER-SFAM-CZ12-V2-eSA-17-CL-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-CL | 14.873 | 2.9802 | 1661.6995 | 0 | 3.4592 | 1661.6995 | 1735.8178
DEER-SFAM-CZ12-V2-eSA-17-CM-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-CM | 14.9692 | 2.98 | 1689.6255 | 0 | 3.4592 | 1689.6255 | 1747.9805
DEER-SFAM-CZ12-V2-eSA-17-LH-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-LH | 14.6525 | 2.5726 | 1481.3016 | 0 | 3.074 | 1481.3016 | 1559.6052
DEER-SFAM-CZ12-V2-eSA-17-LL-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-LL | 14.3806 | 2.7375 | 1559.1576 | 0 | 3.074 | 1559.1576 | 1601.7511
DEER-SFAM-CZ12-V2-eSA-17-LM-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-LM | 14.2572 | 2.682 | 1555.9914 | 0 | 3.074 | 1555.9914 | 1592.7671
DEER-SFAM-CZ12-V2-eSA-17-TH-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-TH | 15.5993 | 2.5976 | 1543.2084 | 0 | 3.074 | 1543.2084 | 1602.9746
DEER-SFAM-CZ12-V2-eSA-17-TL-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-TL | 15.889 | 2.7843 | 1470.9489 | 0 | 3.4592 | 1470.9489 | 1565.076
DEER-SFAM-CZ12-V2-eSA-17-TM-s2 | 17 | CZ12 | V2 | CZ12-V2-eSA-17 | CZ12-V2-eSA-17-TM | 15.5964 | 3.0351 | 1764.9065 | 0 | 3.4592 | 1764.9065 | 1796.1334
DEER-SFAM-CZ12-V2-eSA-18-LH-s2 | 18 | CZ12 | V2 | CZ12-V2-eSA-18 | CZ12-V2-eSA-18-LH | 15.256 | 2.5305 | 1458.2821 | 0 | 3.074 | 1458.2821 | 1509.5163
DEER-SFAM-CZ12-V2-eSA-18-LL-s2 | 18 | CZ12 | V2 | CZ12-V2-eSA-18 | CZ12-V2-eSA-18-LL | 15.4651 | 2.5104 | 1412.8874 | 0 | 3.074 | 1412.8874 | 1479.7849
DEER-SFAM-CZ12-V2-eSA-18-TH-s2 | 18 | CZ12 | V2 | CZ12-V2-eSA-18 | CZ12-V2-eSA-18-TH | 16.1304 | 2.6505 | 1527.3014 | 0 | 3.4592 | 1527.3014 | 1567.9478
DEER-SFAM-CZ12-V2-eSA-18-TL-s2 | 18 | CZ12 | V2 | CZ12-V2-eSA-18 | CZ12-V2-eSA-18-TL | 15.5315 | 3.0243 | 1659.5165 | 0 | 3.4592 | 1659.5165 | 1704.2867
DEER-SFAM-CZ12-V2-eSA-18-TM-s2 | 18 | CZ12 | V2 | CZ12-V2-eSA-18 | CZ12-V2-eSA-18-TM | 15.6945 | 2.5371 | 1523.6255 | 0 | 3.074 | 1523.6255 | 1565.1289
DEER-SFAM-CZ12-V2-eSH-10-HH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-HH | 9.8817 | 3.819 | 2174.076 | 3188.8628 | 3.4592 | 5362.9389 | 2506.1168
DEER-SFAM-CZ12-V2-eSH-10-HL-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-HL | 9.5705 | 3.9548 | 2253.1041 | 3220.8617 | 3.4592 | 5473.9658 | 2578.9855
DEER-SFAM-CZ12-V2-eSH-10-HM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-HM | 10.1355 | 3.6699 | 2179.2968 | 3129.6679 | 3.074 | 5308.9648 | 2492.4436
DEER-SFAM-CZ12-V2-eSH-10-LH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-LH | 10.4449 | 3.3365 | 2097.4295 | 3359.5363 | 3.074 | 5456.9658 | 2439.1411
DEER-SFAM-CZ12-V2-eSH-10-LL-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-LL | 10.0826 | 3.5266 | 2164.5032 | 3313.2917 | 3.074 | 5477.7949 | 2521.3352
DEER-SFAM-CZ12-V2-eSH-10-LM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-LM | 10.3352 | 3.4429 | 2119.4942 | 3241.9596 | 3.074 | 5361.4538 | 2446.0246
DEER-SFAM-CZ12-V2-eSH-10-MH-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-MH | 10.4361 | 3.4828 | 2117.2595 | 3340.3139 | 3.074 | 5457.5734 | 2480.2922
DEER-SFAM-CZ12-V2-eSH-10-ML-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-ML | 10.0051 | 3.7258 | 2200.1647 | 3115.1556 | 3.074 | 5315.3203 | 2530.5625
DEER-SFAM-CZ12-V2-eSH-10-MM-s1 | 10 | CZ12 | V2 | CZ12-V2-eSH-10 | CZ12-V2-eSH-10-MM | 10.0988 | 3.5974 | 2189.1996 | 3247.3957 | 3.074 | 5436.5954 | 2496.2298
DEER-SFAM-CZ12-V2-eSH-13-HH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-HH | 11.5306 | 3.2861 | 1815.028 | 3085.805 | 3.4592 | 4900.833 | 2118.1133
DEER-SFAM-CZ12-V2-eSH-13-HL-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-HL | 12.6047 | 3.2968 | 1716.3047 | 2681.9717 | 3.4592 | 4398.2764 | 2017.7797
DEER-SFAM-CZ12-V2-eSH-13-HM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-HM | 11.8022 | 3.2434 | 1782.5814 | 2753.3232 | 3.4592 | 4535.9046 | 2055.6729
DEER-SFAM-CZ12-V2-eSH-13-LH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-LH | 13.023 | 2.7302 | 1651.0345 | 3388.0172 | 3.074 | 5039.0516 | 2104.9989
DEER-SFAM-CZ12-V2-eSH-13-LL-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-LL | 13.4942 | 2.86 | 1630.3332 | 2884.7871 | 3.074 | 4515.1204 | 1907.3457
DEER-SFAM-CZ12-V2-eSH-13-LM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-LM | 12.4088 | 2.8776 | 1716.8254 | 2457.8387 | 3.074 | 4174.6642 | 2029.6811
DEER-SFAM-CZ12-V2-eSH-13-MH-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-MH | 13.0325 | 3.0483 | 1656.3052 | 3128.0742 | 3.4592 | 4784.3793 | 1959.9556
DEER-SFAM-CZ12-V2-eSH-13-ML-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-ML | 12.2436 | 3.0716 | 1743.7881 | 2947.0742 | 3.074 | 4690.8623 | 2054.5876
DEER-SFAM-CZ12-V2-eSH-13-MM-s1 | 13 | CZ12 | V2 | CZ12-V2-eSH-13 | CZ12-V2-eSH-13-MM | 12.8327 | 3.0544 | 1707.9238 | 2917.3438 | 3.074 | 4625.2676 | 1948.8749
DEER-SFAM-CZ12-V2-eSH-14-HH-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-HH | 12.1968 | 3.1332 | 1714.7965 | 2824.8359 | 3.4592 | 4539.6324 | 1945.4208
DEER-SFAM-CZ12-V2-eSH-14-HL-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-HL | 12.5149 | 3.0782 | 1667.3166 | 2806.4634 | 3.4592 | 4473.78 | 1944.9259
DEER-SFAM-CZ12-V2-eSH-14-HM-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-HM | 12.4534 | 2.9667 | 1663.5281 | 2782.2342 | 3.4592 | 4445.7623 | 1861.209
DEER-SFAM-CZ12-V2-eSH-14-MH-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-MH | 13.8521 | 2.5689 | 1543.6169 | 3078.2341 | 3.074 | 4621.851 | 1844.0714
DEER-SFAM-CZ12-V2-eSH-14-ML-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-ML | 13.6418 | 2.9937 | 1567.2991 | 3148.9666 | 3.4592 | 4716.2656 | 1948.0442
DEER-SFAM-CZ12-V2-eSH-14-MM-s1 | 14 | CZ12 | V2 | CZ12-V2-eSH-14 | CZ12-V2-eSH-14-MM | 13.5389 | 2.7199 | 1564.5252 | 2792.03 | 3.074 | 4356.5552 | 1824.4263
DEER-SFAM-CZ12-V2-eSH-15-HH-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-HH | 13.362 | 2.7403 | 1531.6485 | 3325.3304 | 3.4592 | 4856.9789 | 1747.9273
DEER-SFAM-CZ12-V2-eSH-15-HL-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-HL | 13.646 | 2.9021 | 1546.6352 | 2398.5214 | 3.4592 | 3945.1566 | 1758.3237
DEER-SFAM-CZ12-V2-eSH-15-HM-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-HM | 14.4501 | 2.7816 | 1480.1907 | 2491.6014 | 3.4592 | 3971.792 | 1691.8057
DEER-SFAM-CZ12-V2-eSH-15-MH-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-MH | 14.4481 | 2.6665 | 1489.5134 | 2987.1769 | 3.074 | 4476.6903 | 1694.6762
DEER-SFAM-CZ12-V2-eSH-15-ML-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-ML | 14.5435 | 2.8318 | 1466.8899 | 2746.0871 | 3.4592 | 4212.977 | 1681.057
DEER-SFAM-CZ12-V2-eSH-15-MM-s1 | 15 | CZ12 | V2 | CZ12-V2-eSH-15 | CZ12-V2-eSH-15-MM | 14.655 | 2.7645 | 1472.564 | 2910.9154 | 3.4592 | 4383.4794 | 1698.8674
DEER-SFAM-CZ12-V2-eSH-16-CH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-CH | 14.2902 | 2.9734 | 1742.7581 | 3163.5106 | 3.4592 | 4906.2687 | 1949.5424
DEER-SFAM-CZ12-V2-eSH-16-CL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-CL | 14.4384 | 3.1328 | 1784.1138 | 2932.2546 | 3.4592 | 4716.3684 | 1997.1247
DEER-SFAM-CZ12-V2-eSH-16-LH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-LH | 14.0164 | 2.6279 | 1537.695 | 3329.0541 | 3.074 | 4866.7491 | 1763.7628
DEER-SFAM-CZ12-V2-eSH-16-LL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-LL | 13.6848 | 2.8086 | 1606.9229 | 3081.4418 | 3.074 | 4688.3647 | 1790.2897
DEER-SFAM-CZ12-V2-eSH-16-LM-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-LM | 13.5926 | 2.7305 | 1597.6569 | 3362.3315 | 3.074 | 4959.9884 | 1851.0864
DEER-SFAM-CZ12-V2-eSH-16-TH-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-TH | 14.5961 | 3.059 | 1667.298 | 3998.5665 | 3.4592 | 5665.8645 | 1891.5474
DEER-SFAM-CZ12-V2-eSH-16-TL-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-TL | 13.8284 | 3.101 | 1843.31 | 3958.0966 | 3.074 | 5801.4066 | 2057.4926
DEER-SFAM-CZ12-V2-eSH-16-TM-s2 | 16 | CZ12 | V2 | CZ12-V2-eSH-16 | CZ12-V2-eSH-16-TM | 14.0083 | 3.043 | 1820.2003 | 4003.5795 | 3.074 | 5823.7798 | 2039.8631
DEER-SFAM-CZ12-V2-eSH-17-CM-s2 | 17 | CZ12 | V2 | CZ12-V2-eSH-17 | CZ12-V2-eSH-17-CM | 15.2417 | 2.9823 | 1687.6647 | 3164.3461 | 3.4592 | 4852.0108 | 1917.6675
DEER-SFAM-CZ12-V2-eSH-17-LM-s2 | 17 | CZ12 | V2 | CZ12-V2-eSH-17 | CZ12-V2-eSH-17-LM | 14.4464 | 2.6878 | 1592.5904 | 2976.7309 | 3.074 | 4569.3213 | 1695.4019
DEER-SFAM-CZ12-V2-eSH-17-TH-s2 | 17 | CZ12 | V2 | CZ12-V2-eSH-17 | CZ12-V2-eSH-17-TH | 15.4341 | 2.8776 | 1572.7248 | 4000.8862 | 3.4592 | 5573.6109 | 1813.1306
DEER-SFAM-CZ12-V2-eSH-17-TL-s2 | 17 | CZ12 | V2 | CZ12-V2-eSH-17 | CZ12-V2-eSH-17-TL | 15.3466 | 2.9358 | 1585.8406 | 3979.4275 | 3.4592 | 5565.2681 | 1823.4537
DEER-SFAM-CZ12-V2-eSH-18-LH-s2 | 18 | CZ12 | V2 | CZ12-V2-eSH-18 | CZ12-V2-eSH-18-LH | 15.2719 | 2.5552 | 1439.7387 | 3509.5081 | 3.074 | 4949.2467 | 1617.8088
DEER-SFAM-CZ12-V2-eSH-18-LL-s2 | 18 | CZ12 | V2 | CZ12-V2-eSH-18 | CZ12-V2-eSH-18-LL | 14.6265 | 2.6271 | 1492.0929 | 3121.0879 | 3.074 | 4613.1808 | 1651.3942
DEER-SFAM-CZ12-V2-eSH-18-LM-s2 | 18 | CZ12 | V2 | CZ12-V2-eSH-18 | CZ12-V2-eSH-18-LM | 15.2275 | 2.5928 | 1460.5653 | 3709.0118 | 3.074 | 5169.5771 | 1665.9858
DEER-SFAM-CZ12-V2-eSH-18-TM-s2 | 18 | CZ12 | V2 | CZ12-V2-eSH-18 | CZ12-V2-eSH-18-TM | 16.2794 | 2.6557 | 1490.7938 | 3996.5762 | 3.074 | 5487.37 | 1849.1835
DEER-SFAM-CZ12-V3-eSA-10-HH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-HH | 9.4506 | 3.9516 | 2072.0646 | 0 | 3.8 | 2072.0646 | 2172.3338
DEER-SFAM-CZ12-V3-eSA-10-HL-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-HL | 8.887 | 4.3675 | 2172.2182 | 0 | 3.8 | 2172.2182 | 2272.5411
DEER-SFAM-CZ12-V3-eSA-10-HM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-HM | 8.9203 | 4.0197 | 2113.3738 | 0 | 3.8 | 2113.3738 | 2213.6867
DEER-SFAM-CZ12-V3-eSA-10-LH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-LH | 9.9143 | 3.8525 | 2014.3732 | 0 | 3.8 | 2014.3732 | 2114.7483
DEER-SFAM-CZ12-V3-eSA-10-LL-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-LL | 9.1807 | 4.0567 | 2105.8108 | 0 | 3.8 | 2105.8108 | 2206.1459
DEER-SFAM-CZ12-V3-eSA-10-LM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-LM | 9.8325 | 3.8769 | 2016.8669 | 0 | 3.8 | 2016.8669 | 2117.2447
DEER-SFAM-CZ12-V3-eSA-10-MH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-MH | 9.7223 | 3.771 | 2038.0293 | 0 | 3.8 | 2038.0293 | 2138.3865
DEER-SFAM-CZ12-V3-eSA-10-ML-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-ML | 9.0146 | 4.1765 | 2161.9234 | 0 | 3.8 | 2161.9234 | 2262.2473
DEER-SFAM-CZ12-V3-eSA-10-MM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSA-10 | CZ12-V3-eSA-10-MM | 9.6613 | 3.7174 | 2005.7442 | 0 | 3.5 | 2005.7442 | 2106.0203
DEER-SFAM-CZ12-V3-eSA-13-HH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-HH | 11.7144 | 3.3196 | 1638.7375 | 0 | 3.8 | 1638.7375 | 1729.1697
DEER-SFAM-CZ12-V3-eSA-13-HL-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-HL | 11.9278 | 3.4664 | 1617.0543 | 0 | 3.8 | 1617.0543 | 1696.207
DEER-SFAM-CZ12-V3-eSA-13-HM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-HM | 11.7951 | 3.3224 | 1628.0585 | 0 | 3.8 | 1628.0585 | 1718.4702
DEER-SFAM-CZ12-V3-eSA-13-LH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-LH | 12.521 | 3.0149 | 1551.6569 | 0 | 3.8 | 1551.6569 | 1651.9957
DEER-SFAM-CZ12-V3-eSA-13-LL-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-LL | 12.1537 | 3.2474 | 1616.8211 | 0 | 3.8 | 1616.8211 | 1717.0331
DEER-SFAM-CZ12-V3-eSA-13-LM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-LM | 12.055 | 3.1636 | 1616.4301 | 0 | 3.8 | 1616.4301 | 1716.7154
DEER-SFAM-CZ12-V3-eSA-13-MH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-MH | 12.5908 | 3.1537 | 1574.8469 | 0 | 3.8 | 1574.8469 | 1675.1603
DEER-SFAM-CZ12-V3-eSA-13-ML-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-ML | 11.7714 | 3.2947 | 1587.5906 | 0 | 3.8 | 1587.5906 | 1687.6065
DEER-SFAM-CZ12-V3-eSA-13-MM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSA-13 | CZ12-V3-eSA-13-MM | 12.6822 | 3.202 | 1544.0208 | 0 | 3.8 | 1544.0208 | 1644.3249
DEER-SFAM-CZ12-V3-eSA-14-HH-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-HH | 11.9424 | 3.1668 | 1557.3579 | 0 | 3.8 | 1557.3579 | 1641.4413
DEER-SFAM-CZ12-V3-eSA-14-HL-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-HL | 13.0387 | 3.1213 | 1500.1559 | 0 | 3.8 | 1500.1559 | 1561.9867
DEER-SFAM-CZ12-V3-eSA-14-HM-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-HM | 12.6596 | 3.2242 | 1544.5516 | 0 | 3.8 | 1544.5516 | 1639.3914
DEER-SFAM-CZ12-V3-eSA-14-MH-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-MH | 12.9889 | 2.8234 | 1526.1298 | 0 | 3.5 | 1526.1298 | 1592.0205
DEER-SFAM-CZ12-V3-eSA-14-ML-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-ML | 12.6317 | 3.1296 | 1509.9786 | 0 | 3.8 | 1509.9786 | 1615.2412
DEER-SFAM-CZ12-V3-eSA-14-MM-s1 | 14 | CZ12 | V3 | CZ12-V3-eSA-14 | CZ12-V3-eSA-14-MM | 12.9678 | 2.8414 | 1495.3758 | 0 | 3.5 | 1495.3758 | 1567.605
DEER-SFAM-CZ12-V3-eSA-15-HH-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-HH | 13.3836 | 2.8932 | 1426.7104 | 0 | 3.8 | 1426.7104 | 1496.7995
DEER-SFAM-CZ12-V3-eSA-15-HL-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-HL | 13.9859 | 2.9225 | 1387.1414 | 0 | 3.8 | 1387.1414 | 1474.5096
DEER-SFAM-CZ12-V3-eSA-15-HM-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-HM | 13.444 | 2.7955 | 1408.2922 | 0 | 3.8 | 1408.2922 | 1478.6451
DEER-SFAM-CZ12-V3-eSA-15-MH-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-MH | 13.2586 | 3.0151 | 1443.8634 | 0 | 3.8 | 1443.8634 | 1496.0897
DEER-SFAM-CZ12-V3-eSA-15-ML-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-ML | 13.974 | 2.9122 | 1412.7896 | 0 | 3.8 | 1412.7896 | 1483.0648
DEER-SFAM-CZ12-V3-eSA-15-MM-s1 | 15 | CZ12 | V3 | CZ12-V3-eSA-15 | CZ12-V3-eSA-15-MM | 13.7336 | 2.9386 | 1405.6973 | 0 | 3.8 | 1405.6973 | 1469.7378
DEER-SFAM-CZ12-V3-eSA-16-CH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-CH | 14.1057 | 3.1464 | 1593.6928 | 0 | 3.8 | 1593.6928 | 1634.2451
DEER-SFAM-CZ12-V3-eSA-16-CL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-CL | 14.4744 | 2.9725 | 1494.2849 | 0 | 3.8 | 1494.2849 | 1545.5504
DEER-SFAM-CZ12-V3-eSA-16-CM-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-CM | 14.1111 | 3.0772 | 1550.9619 | 0 | 3.8 | 1550.9619 | 1605.0225
DEER-SFAM-CZ12-V3-eSA-16-LH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-LH | 13.9896 | 2.8199 | 1407.6048 | 0 | 3.8 | 1407.6048 | 1477.1962
DEER-SFAM-CZ12-V3-eSA-16-LL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-LL | 13.6155 | 3.0195 | 1468.6152 | 0 | 3.8 | 1468.6152 | 1514.215
DEER-SFAM-CZ12-V3-eSA-16-LM-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-LM | 13.6366 | 2.9323 | 1464.3054 | 0 | 3.8 | 1464.3054 | 1505.6324
DEER-SFAM-CZ12-V3-eSA-16-NM-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-NM | 15.3344 | 2.6605 | 1326.0709 | 0 | 3.8 | 1326.0709 | 1366.7
DEER-SFAM-CZ12-V3-eSA-16-TH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-TH | 13.6069 | 3.2688 | 1656.4714 | 0 | 3.8 | 1656.4714 | 1682.5384
DEER-SFAM-CZ12-V3-eSA-16-TL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSA-16 | CZ12-V3-eSA-16-TL | 14.6628 | 3.0311 | 1485.5394 | 0 | 3.8 | 1485.5394 | 1513.602
DEER-SFAM-CZ12-V3-eSA-17-CH-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-CH | 14.9689 | 3.0023 | 1474.5073 | 0 | 3.8 | 1474.5073 | 1525.7641
DEER-SFAM-CZ12-V3-eSA-17-CL-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-CL | 14.9716 | 2.9925 | 1465.244 | 0 | 3.8 | 1465.244 | 1516.4878
DEER-SFAM-CZ12-V3-eSA-17-CM-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-CM | 15.058 | 3.0036 | 1482.96 | 0 | 3.8 | 1482.96 | 1523.3906
DEER-SFAM-CZ12-V3-eSA-17-LH-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-LH | 14.5845 | 2.6495 | 1345.1615 | 0 | 3.5 | 1345.1615 | 1399.6431
DEER-SFAM-CZ12-V3-eSA-17-LL-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-LL | 14.3587 | 2.9154 | 1403.9231 | 0 | 3.8 | 1403.9231 | 1433.4869
DEER-SFAM-CZ12-V3-eSA-17-LM-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-LM | 14.2114 | 2.8638 | 1408.6922 | 0 | 3.8 | 1408.6922 | 1434.2564
DEER-SFAM-CZ12-V3-eSA-17-TH-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-TH | 15.2515 | 2.8372 | 1422.0844 | 0 | 3.8 | 1422.0844 | 1463.75
DEER-SFAM-CZ12-V3-eSA-17-TL-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-TL | 16.1754 | 2.7787 | 1297.2896 | 0 | 3.8 | 1297.2896 | 1362.3727
DEER-SFAM-CZ12-V3-eSA-17-TM-s2 | 17 | CZ12 | V3 | CZ12-V3-eSA-17 | CZ12-V3-eSA-17-TM | 15.7 | 3.0849 | 1503.9469 | 0 | 3.8 | 1503.9469 | 1525.6128
DEER-SFAM-CZ12-V3-eSA-18-LH-s2 | 18 | CZ12 | V3 | CZ12-V3-eSA-18 | CZ12-V3-eSA-18-LH | 15.1391 | 2.6976 | 1322.3595 | 0 | 3.8 | 1322.3595 | 1357.9975
DEER-SFAM-CZ12-V3-eSA-18-LL-s2 | 18 | CZ12 | V3 | CZ12-V3-eSA-18 | CZ12-V3-eSA-18-LL | 15.4438 | 2.6843 | 1284.0173 | 0 | 3.8 | 1284.0173 | 1330.5797
DEER-SFAM-CZ12-V3-eSA-18-TH-s2 | 18 | CZ12 | V3 | CZ12-V3-eSA-18 | CZ12-V3-eSA-18-TH | 15.936 | 2.6637 | 1366.3444 | 0 | 3.8 | 1366.3444 | 1394.6098
DEER-SFAM-CZ12-V3-eSA-18-TL-s2 | 18 | CZ12 | V3 | CZ12-V3-eSA-18 | CZ12-V3-eSA-18-TL | 15.4931 | 3.0836 | 1458.3538 | 0 | 3.8 | 1458.3538 | 1489.4608
DEER-SFAM-CZ12-V3-eSA-18-TM-s2 | 18 | CZ12 | V3 | CZ12-V3-eSA-18 | CZ12-V3-eSA-18-TM | 15.3837 | 2.7516 | 1400.6985 | 0 | 3.8 | 1400.6985 | 1429.6207
DEER-SFAM-CZ12-V3-eSH-10-HH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-HH | 9.484 | 3.9169 | 2047.5563 | 2176.7886 | 3.8 | 4224.3449 | 2267.7449
DEER-SFAM-CZ12-V3-eSH-10-HL-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-HL | 9.2496 | 4.0416 | 2104.981 | 2188.0405 | 3.8 | 4293.0215 | 2321.3215
DEER-SFAM-CZ12-V3-eSH-10-HM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-HM | 9.6932 | 4.0898 | 2059.1167 | 2160.0607 | 3.8 | 4219.1774 | 2266.5774
DEER-SFAM-CZ12-V3-eSH-10-LH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-LH | 9.8559 | 3.7465 | 2012.9076 | 2276.7087 | 3.8 | 4289.6163 | 2239.8163
DEER-SFAM-CZ12-V3-eSH-10-LL-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-LL | 9.6406 | 3.9228 | 2044.3446 | 2210.8557 | 3.8 | 4255.2003 | 2280.9003
DEER-SFAM-CZ12-V3-eSH-10-LM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-LM | 9.8212 | 3.8271 | 2013.837 | 2202.0946 | 3.8 | 4215.9316 | 2231.2316
DEER-SFAM-CZ12-V3-eSH-10-MH-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-MH | 9.8956 | 3.891 | 2017.3991 | 2247.0547 | 3.8 | 4264.4538 | 2258.0538
DEER-SFAM-CZ12-V3-eSH-10-ML-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-ML | 9.6116 | 4.131 | 2066.8192 | 2089.1986 | 3.8 | 4156.0178 | 2286.6178
DEER-SFAM-CZ12-V3-eSH-10-MM-s1 | 10 | CZ12 | V3 | CZ12-V3-eSH-10 | CZ12-V3-eSH-10-MM | 9.7165 | 4.0145 | 2057.5616 | 2194.3911 | 3.8 | 4251.9527 | 2262.3527
DEER-SFAM-CZ12-V3-eSH-13-HH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-HH | 11.3314 | 3.3517 | 1693.8302 | 2094.9445 | 3.8 | 3788.7747 | 1894.9747
DEER-SFAM-CZ12-V3-eSH-13-HL-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-HL | 12.3258 | 3.4636 | 1600.0721 | 1806.6791 | 3.8 | 3406.7512 | 1800.1512
DEER-SFAM-CZ12-V3-eSH-13-HM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-HM | 11.6273 | 3.2981 | 1657.3834 | 1877.7113 | 3.8 | 3535.0947 | 1839.0947
DEER-SFAM-CZ12-V3-eSH-13-LH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-LH | 12.3369 | 3.0682 | 1580.9844 | 2127.6442 | 3.8 | 3708.6286 | 1880.9286
DEER-SFAM-CZ12-V3-eSH-13-LL-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-LL | 12.9704 | 3.1863 | 1531.661 | 1895.0045 | 3.8 | 3426.6655 | 1715.7655
DEER-SFAM-CZ12-V3-eSH-13-LM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-LM | 11.9231 | 3.089 | 1622.9975 | 1647.3072 | 3.5 | 3270.3047 | 1831.3047
DEER-SFAM-CZ12-V3-eSH-13-MH-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-MH | 12.4794 | 3.1613 | 1567.2894 | 2116.7501 | 3.8 | 3684.0395 | 1768.2395
DEER-SFAM-CZ12-V3-eSH-13-ML-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-ML | 11.7709 | 3.4329 | 1653.4747 | 1915.116 | 3.8 | 3568.5907 | 1859.3907
DEER-SFAM-CZ12-V3-eSH-13-MM-s1 | 13 | CZ12 | V3 | CZ12-V3-eSH-13 | CZ12-V3-eSH-13-MM | 12.3405 | 3.3714 | 1608.7348 | 1968.142 | 3.8 | 3576.8768 | 1769.7768
DEER-SFAM-CZ12-V3-eSH-14-HH-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-HH | 12.0261 | 3.1907 | 1593.9032 | 1917.0311 | 3.8 | 3510.9343 | 1747.1343
DEER-SFAM-CZ12-V3-eSH-14-HL-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-HL | 12.4157 | 3.1155 | 1541.2935 | 1868.7337 | 3.8 | 3410.0272 | 1724.8272
DEER-SFAM-CZ12-V3-eSH-14-HM-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-HM | 12.3087 | 3.0192 | 1547.0935 | 1868.6955 | 3.8 | 3415.789 | 1678.289
DEER-SFAM-CZ12-V3-eSH-14-MH-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-MH | 13.1559 | 2.8797 | 1476.0191 | 1949.4956 | 3.8 | 3425.5147 | 1675.6147
DEER-SFAM-CZ12-V3-eSH-14-ML-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-ML | 13.2424 | 3.0913 | 1466.394 | 1984.5134 | 3.8 | 3450.9074 | 1714.5074
DEER-SFAM-CZ12-V3-eSH-14-MM-s1 | 14 | CZ12 | V3 | CZ12-V3-eSH-14 | CZ12-V3-eSH-14-MM | 13.016 | 3.0158 | 1479.5491 | 1809.429 | 3.8 | 3288.9781 | 1651.8781
DEER-SFAM-CZ12-V3-eSH-15-HH-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-HH | 13.2021 | 2.7854 | 1429.6221 | 2113.2252 | 3.8 | 3542.8473 | 1571.7473
DEER-SFAM-CZ12-V3-eSH-15-HL-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-HL | 13.4815 | 2.9755 | 1437.0792 | 1627.7405 | 3.8 | 3064.8197 | 1577.8197
DEER-SFAM-CZ12-V3-eSH-15-HM-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-HM | 13.9339 | 2.8403 | 1391.8128 | 1704.9588 | 3.8 | 3096.7716 | 1531.5716
DEER-SFAM-CZ12-V3-eSH-15-MH-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-MH | 13.7599 | 2.9346 | 1417.2383 | 1865.3233 | 3.8 | 3282.5616 | 1551.9616
DEER-SFAM-CZ12-V3-eSH-15-ML-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-ML | 14.1555 | 2.924 | 1370.8446 | 1765.409 | 3.8 | 3136.2536 | 1511.0536
DEER-SFAM-CZ12-V3-eSH-15-MM-s1 | 15 | CZ12 | V3 | CZ12-V3-eSH-15 | CZ12-V3-eSH-15-MM | 14.1742 | 2.837 | 1381.4442 | 1909.1206 | 3.8 | 3290.5648 | 1531.2648
DEER-SFAM-CZ12-V3-eSH-16-CH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-CH | 14.3136 | 2.9612 | 1541.2819 | 1891.8581 | 3.8 | 3433.14 | 1664.04
DEER-SFAM-CZ12-V3-eSH-16-CL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-CL | 14.4529 | 3.2041 | 1568.2784 | 1766.2562 | 3.8 | 3334.5346 | 1696.1346
DEER-SFAM-CZ12-V3-eSH-16-LH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-LH | 13.6438 | 2.837 | 1436.3373 | 2000.7881 | 3.8 | 3437.1254 | 1577.2254
DEER-SFAM-CZ12-V3-eSH-16-LL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-LL | 13.6204 | 2.9974 | 1459.6575 | 1816.4748 | 3.8 | 3276.1323 | 1572.9323
DEER-SFAM-CZ12-V3-eSH-16-LM-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-LM | 13.4381 | 2.8183 | 1461.082 | 2003.3594 | 3.5 | 3464.4414 | 1619.2414
DEER-SFAM-CZ12-V3-eSH-16-TH-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-TH | 14.5929 | 3.0325 | 1477.3046 | 2359.5002 | 3.8 | 3836.8048 | 1597.3048
DEER-SFAM-CZ12-V3-eSH-16-TL-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-TL | 13.9304 | 3.392 | 1631.1275 | 2302.2301 | 3.8 | 3933.3576 | 1738.7576
DEER-SFAM-CZ12-V3-eSH-16-TM-s2 | 16 | CZ12 | V3 | CZ12-V3-eSH-16 | CZ12-V3-eSH-16-TM | 14.0826 | 3.3347 | 1613.6244 | 2341.7517 | 3.8 | 3955.3761 | 1724.2761
DEER-SFAM-CZ12-V3-eSH-17-CM-s2 | 17 | CZ12 | V3 | CZ12-V3-eSH-17 | CZ12-V3-eSH-17-CM | 15.2487 | 3.0496 | 1484.5886 | 1850.7836 | 3.8 | 3335.3722 | 1618.9722
DEER-SFAM-CZ12-V3-eSH-17-LM-s2 | 17 | CZ12 | V3 | CZ12-V3-eSH-17 | CZ12-V3-eSH-17-LM | 14.203 | 3.0069 | 1448.8638 | 1766.5667 | 3.8 | 3215.4305 | 1512.5305
DEER-SFAM-CZ12-V3-eSH-17-TH-s2 | 17 | CZ12 | V3 | CZ12-V3-eSH-17 | CZ12-V3-eSH-17-TH | 15.3722 | 2.8767 | 1398.8711 | 2353.4532 | 3.8 | 3752.3243 | 1528.3243
DEER-SFAM-CZ12-V3-eSH-17-TL-s2 | 17 | CZ12 | V3 | CZ12-V3-eSH-17 | CZ12-V3-eSH-17-TL | 15.3479 | 2.9283 | 1405.0996 | 2325.4831 | 3.8 | 3730.5827 | 1532.6827
DEER-SFAM-CZ12-V3-eSH-18-LH-s2 | 18 | CZ12 | V3 | CZ12-V3-eSH-18 | CZ12-V3-eSH-18-LH | 15.1776 | 2.638 | 1305.0144 | 2009.4147 | 3.5 | 3314.4291 | 1409.2291
DEER-SFAM-CZ12-V3-eSH-18-LL-s2 | 18 | CZ12 | V3 | CZ12-V3-eSH-18 | CZ12-V3-eSH-18-LL | 14.553 | 2.7182 | 1353.4384 | 1822.6513 | 3.5 | 3176.0897 | 1451.4897
DEER-SFAM-CZ12-V3-eSH-18-LM-s2 | 18 | CZ12 | V3 | CZ12-V3-eSH-18 | CZ12-V3-eSH-18-LM | 15.1424 | 2.7521 | 1322.9544 | 2073.9861 | 3.8 | 3396.9405 | 1439.0405
DEER-SFAM-CZ12-V3-eSH-18-TM-s2 | 18 | CZ12 | V3 | CZ12-V3-eSH-18 | CZ12-V3-eSH-18-TM | 16.1895 | 2.764 | 1344.4356 | 2329.9919 | 3.5 | 3674.4275 | 1544.1275
DEER-SFAM-CZ12-V4-eSA-10-HH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-HH | 9.4287 | 3.5711 | 1804.8081 | 0 | 3.5 | 1804.8081 | 1887.4764
DEER-SFAM-CZ12-V4-eSA-10-HL-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-HL | 8.88 | 3.9255 | 1887.0925 | 0 | 3.5 | 1887.0925 | 1969.8043
DEER-SFAM-CZ12-V4-eSA-10-HM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-HM | 8.909 | 3.6252 | 1837.7622 | 0 | 3.5 | 1837.7622 | 1920.4666
DEER-SFAM-CZ12-V4-eSA-10-LH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-LH | 9.91 | 3.4807 | 1751.1654 | 0 | 3.5 | 1751.1654 | 1833.9212
DEER-SFAM-CZ12-V4-eSA-10-LL-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-LL | 9.1727 | 3.6465 | 1830.3093 | 0 | 3.5 | 1830.3093 | 1913.0317
DEER-SFAM-CZ12-V4-eSA-10-LM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-LM | 9.8303 | 3.5022 | 1752.8145 | 0 | 3.5 | 1752.8145 | 1835.5723
DEER-SFAM-CZ12-V4-eSA-10-MH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-MH | 9.694 | 3.4098 | 1776.247 | 0 | 3.5 | 1776.247 | 1858.9878
DEER-SFAM-CZ12-V4-eSA-10-ML-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-ML | 9.0136 | 3.7538 | 1878.7276 | 0 | 3.5 | 1878.7276 | 1961.4404
DEER-SFAM-CZ12-V4-eSA-10-MM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSA-10 | CZ12-V4-eSA-10-MM | 9.6042 | 3.5151 | 1753.8343 | 0 | 3.5 | 1753.8343 | 1836.5516
DEER-SFAM-CZ12-V4-eSA-13-HH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-HH | 11.589 | 3.0761 | 1430.8633 | 0 | 3.8 | 1430.8633 | 1505.4588
DEER-SFAM-CZ12-V4-eSA-13-HL-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-HL | 11.9087 | 3.1775 | 1402.6282 | 0 | 3.8 | 1402.6282 | 1467.9197
DEER-SFAM-CZ12-V4-eSA-13-HM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-HM | 11.7369 | 3.0641 | 1415.9685 | 0 | 3.8 | 1415.9685 | 1490.5484
DEER-SFAM-CZ12-V4-eSA-13-LH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-LH | 12.4141 | 2.7905 | 1355.5118 | 0 | 3.8 | 1355.5118 | 1438.2774
DEER-SFAM-CZ12-V4-eSA-13-LL-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-LL | 12.1592 | 2.9303 | 1402.0835 | 0 | 3.5 | 1402.0835 | 1484.7043
DEER-SFAM-CZ12-V4-eSA-13-LM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-LM | 12.0445 | 2.857 | 1404.7814 | 0 | 3.5 | 1404.7814 | 1487.4632
DEER-SFAM-CZ12-V4-eSA-13-MH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-MH | 12.4927 | 2.9244 | 1374.7093 | 0 | 3.8 | 1374.7093 | 1457.4565
DEER-SFAM-CZ12-V4-eSA-13-ML-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-ML | 11.7776 | 2.9562 | 1378.4697 | 0 | 3.5 | 1378.4697 | 1460.9286
DEER-SFAM-CZ12-V4-eSA-13-MM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSA-13 | CZ12-V4-eSA-13-MM | 12.6091 | 2.9236 | 1344.9251 | 0 | 3.8 | 1344.9251 | 1427.6651
DEER-SFAM-CZ12-V4-eSA-14-HH-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-HH | 11.93 | 2.8485 | 1353.646 | 0 | 3.5 | 1353.646 | 1422.9696
DEER-SFAM-CZ12-V4-eSA-14-HL-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-HL | 13.0016 | 2.8607 | 1302.4212 | 0 | 3.8 | 1302.4212 | 1353.4249
DEER-SFAM-CZ12-V4-eSA-14-HM-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-HM | 12.6822 | 2.8999 | 1339.7401 | 0 | 3.5 | 1339.7401 | 1417.9316
DEER-SFAM-CZ12-V4-eSA-14-MH-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-MH | 12.8654 | 2.6741 | 1338.9077 | 0 | 3.5 | 1338.9077 | 1393.2643
DEER-SFAM-CZ12-V4-eSA-14-ML-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-ML | 12.6407 | 2.8127 | 1310.942 | 0 | 3.5 | 1310.942 | 1397.7268
DEER-SFAM-CZ12-V4-eSA-14-MM-s1 | 14 | CZ12 | V4 | CZ12-V4-eSA-14 | CZ12-V4-eSA-14-MM | 12.8603 | 2.6874 | 1310.115 | 0 | 3.5 | 1310.115 | 1369.699
DEER-SFAM-CZ12-V4-eSA-15-HH-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-HH | 13.2533 | 2.6769 | 1246.3091 | 0 | 3.8 | 1246.3091 | 1304.1235
DEER-SFAM-CZ12-V4-eSA-15-HL-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-HL | 13.936 | 2.6828 | 1205.1397 | 0 | 3.8 | 1205.1397 | 1277.2108
DEER-SFAM-CZ12-V4-eSA-15-HM-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-HM | 13.3358 | 2.5803 | 1227.5335 | 0 | 3.8 | 1227.5335 | 1285.5665
DEER-SFAM-CZ12-V4-eSA-15-MH-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-MH | 13.2527 | 2.7114 | 1251.5991 | 0 | 3.5 | 1251.5991 | 1294.6572
DEER-SFAM-CZ12-V4-eSA-15-ML-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-ML | 13.9882 | 2.6156 | 1221.0163 | 0 | 3.5 | 1221.0163 | 1278.9554
DEER-SFAM-CZ12-V4-eSA-15-MM-s1 | 15 | CZ12 | V4 | CZ12-V4-eSA-15 | CZ12-V4-eSA-15-MM | 13.7402 | 2.6333 | 1217.6505 | 0 | 3.5 | 1217.6505 | 1270.4493
DEER-SFAM-CZ12-V4-eSA-16-CH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-CH | 14.1369 | 2.9469 | 1386.2828 | 0 | 3.8 | 1386.2828 | 1419.7674
DEER-SFAM-CZ12-V4-eSA-16-CL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-CL | 14.4899 | 2.7416 | 1301.1579 | 0 | 3.8 | 1301.1579 | 1343.4785
DEER-SFAM-CZ12-V4-eSA-16-CM-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-CM | 14.1213 | 2.8542 | 1351.2835 | 0 | 3.8 | 1351.2835 | 1395.915
DEER-SFAM-CZ12-V4-eSA-16-LH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-LH | 13.9106 | 2.5275 | 1225.4773 | 0 | 3.5 | 1225.4773 | 1282.8634
DEER-SFAM-CZ12-V4-eSA-16-LL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-LL | 13.5734 | 2.6986 | 1275.6304 | 0 | 3.5 | 1275.6304 | 1313.2337
DEER-SFAM-CZ12-V4-eSA-16-LM-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-LM | 13.5953 | 2.6265 | 1271.2998 | 0 | 3.5 | 1271.2998 | 1305.3801
DEER-SFAM-CZ12-V4-eSA-16-NM-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-NM | 15.3226 | 2.3764 | 1149.1029 | 0 | 3.5 | 1149.1029 | 1182.6087
DEER-SFAM-CZ12-V4-eSA-16-TH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-TH | 13.5572 | 2.9327 | 1444.1166 | 0 | 3.5 | 1444.1166 | 1465.6207
DEER-SFAM-CZ12-V4-eSA-16-TL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSA-16 | CZ12-V4-eSA-16-TL | 14.6157 | 2.778 | 1301.969 | 0 | 3.8 | 1301.969 | 1325.1382
DEER-SFAM-CZ12-V4-eSA-17-CH-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-CH | 15.0024 | 2.8024 | 1281.3172 | 0 | 3.8 | 1281.3172 | 1323.6368
DEER-SFAM-CZ12-V4-eSA-17-CL-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-CL | 15.0253 | 2.7763 | 1272.1129 | 0 | 3.8 | 1272.1129 | 1314.4208
DEER-SFAM-CZ12-V4-eSA-17-CM-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-CM | 15.1038 | 2.7934 | 1288.9726 | 0 | 3.8 | 1288.9726 | 1322.356
DEER-SFAM-CZ12-V4-eSA-17-LH-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-LH | 14.4465 | 2.4569 | 1178.8173 | 0 | 3.5 | 1178.8173 | 1223.7761
DEER-SFAM-CZ12-V4-eSA-17-LL-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-LL | 14.3287 | 2.6068 | 1218.4414 | 0 | 3.5 | 1218.4414 | 1242.8206
DEER-SFAM-CZ12-V4-eSA-17-LM-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-LM | 14.1749 | 2.5624 | 1222.9017 | 0 | 3.5 | 1222.9017 | 1243.9831
DEER-SFAM-CZ12-V4-eSA-17-TH-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-TH | 15.177 | 2.5534 | 1239.9259 | 0 | 3.5 | 1239.9259 | 1274.2939
DEER-SFAM-CZ12-V4-eSA-17-TL-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-TL | 16.2124 | 2.5535 | 1133.3915 | 0 | 3.8 | 1133.3915 | 1187.1413
DEER-SFAM-CZ12-V4-eSA-17-TM-s2 | 17 | CZ12 | V4 | CZ12-V4-eSA-17 | CZ12-V4-eSA-17-TM | 15.6071 | 2.8869 | 1321.234 | 0 | 3.8 | 1321.234 | 1339.126
DEER-SFAM-CZ12-V4-eSA-18-LH-s2 | 18 | CZ12 | V4 | CZ12-V4-eSA-18 | CZ12-V4-eSA-18-LH | 15.0862 | 2.4134 | 1149.2794 | 0 | 3.5 | 1149.2794 | 1178.6681
DEER-SFAM-CZ12-V4-eSA-18-LL-s2 | 18 | CZ12 | V4 | CZ12-V4-eSA-18 | CZ12-V4-eSA-18-LL | 15.4065 | 2.4026 | 1114.1408 | 0 | 3.5 | 1114.1408 | 1152.5387
DEER-SFAM-CZ12-V4-eSA-18-TH-s2 | 18 | CZ12 | V4 | CZ12-V4-eSA-18 | CZ12-V4-eSA-18-TH | 15.6946 | 2.4691 | 1210.9468 | 0 | 3.8 | 1210.9468 | 1234.2803
DEER-SFAM-CZ12-V4-eSA-18-TL-s2 | 18 | CZ12 | V4 | CZ12-V4-eSA-18 | CZ12-V4-eSA-18-TL | 15.3809 | 2.8831 | 1280.9787 | 0 | 3.8 | 1280.9787 | 1306.664
DEER-SFAM-CZ12-V4-eSA-18-TM-s2 | 18 | CZ12 | V4 | CZ12-V4-eSA-18 | CZ12-V4-eSA-18-TM | 15.3136 | 2.4743 | 1220.9069 | 0 | 3.5 | 1220.9069 | 1244.7636
DEER-SFAM-CZ12-V4-eSH-10-HH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-HH | 9.3972 | 3.6206 | 1790.2628 | 1816.8582 | 3.8 | 3607.121 | 1972.421
DEER-SFAM-CZ12-V4-eSH-10-HL-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-HL | 9.1961 | 3.7518 | 1834.1376 | 1820.6077 | 3.8 | 3654.7453 | 2013.0453
DEER-SFAM-CZ12-V4-eSH-10-HM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-HM | 9.6774 | 3.6857 | 1791.4485 | 1790.9172 | 3.5 | 3582.3657 | 1962.9657
DEER-SFAM-CZ12-V4-eSH-10-LH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-LH | 9.8257 | 3.3875 | 1753.2917 | 1890.0303 | 3.5 | 3643.322 | 1940.922
DEER-SFAM-CZ12-V4-eSH-10-LL-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-LL | 9.6309 | 3.5261 | 1777.3123 | 1832.6423 | 3.5 | 3609.9546 | 1972.9546
DEER-SFAM-CZ12-V4-eSH-10-LM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-LM | 9.7329 | 3.5543 | 1761.0157 | 1837.9662 | 3.8 | 3598.9819 | 1940.8819
DEER-SFAM-CZ12-V4-eSH-10-MH-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-MH | 9.8787 | 3.5158 | 1755.3348 | 1864.0968 | 3.5 | 3619.4316 | 1954.3316
DEER-SFAM-CZ12-V4-eSH-10-ML-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-ML | 9.5781 | 3.8117 | 1796.4981 | 1736.5984 | 3.8 | 3533.0965 | 1978.3965
DEER-SFAM-CZ12-V4-eSH-10-MM-s1 | 10 | CZ12 | V4 | CZ12-V4-eSH-10 | CZ12-V4-eSH-10-MM | 9.7084 | 3.6191 | 1789.3782 | 1819.1257 | 3.5 | 3608.5039 | 1958.7039
DEER-SFAM-CZ12-V4-eSH-13-HH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-HH | 11.2152 | 3.1162 | 1479.5513 | 1749.6275 | 3.8 | 3229.1788 | 1645.9788
DEER-SFAM-CZ12-V4-eSH-13-HL-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-HL | 12.2648 | 3.1965 | 1390.5023 | 1500.2336 | 3.8 | 2890.7359 | 1556.0359
DEER-SFAM-CZ12-V4-eSH-13-HM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-HM | 11.5361 | 3.0591 | 1444.2399 | 1564.7421 | 3.8 | 3008.982 | 1594.582
DEER-SFAM-CZ12-V4-eSH-13-LH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-LH | 12.3174 | 2.7712 | 1375.4177 | 1767.8738 | 3.5 | 3143.2915 | 1623.4915
DEER-SFAM-CZ12-V4-eSH-13-LL-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-LL | 12.8927 | 2.9478 | 1334.8605 | 1576.6413 | 3.8 | 2911.5018 | 1487.2018
DEER-SFAM-CZ12-V4-eSH-13-LM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-LM | 11.8438 | 2.9172 | 1419.6404 | 1370.6961 | 3.5 | 2790.3365 | 1591.9365
DEER-SFAM-CZ12-V4-eSH-13-MH-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-MH | 12.3414 | 2.9339 | 1371.8396 | 1772.2376 | 3.8 | 3144.0772 | 1538.0772
DEER-SFAM-CZ12-V4-eSH-13-ML-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-ML | 11.7849 | 3.0981 | 1434.4489 | 1586.0469 | 3.5 | 3020.4958 | 1604.6958
DEER-SFAM-CZ12-V4-eSH-13-MM-s1 | 13 | CZ12 | V4 | CZ12-V4-eSH-13 | CZ12-V4-eSH-13-MM | 12.3345 | 3.0328 | 1393.5051 | 1631.2289 | 3.5 | 3024.734 | 1526.634
DEER-SFAM-CZ12-V4-eSH-14-HH-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-HH | 11.9294 | 2.9571 | 1390.2377 | 1598.3801 | 3.8 | 2988.6178 | 1517.0178
DEER-SFAM-CZ12-V4-eSH-14-HL-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-HL | 12.3717 | 2.8731 | 1337.9075 | 1551.5451 | 3.8 | 2889.4526 | 1489.7526
DEER-SFAM-CZ12-V4-eSH-14-HM-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-HM | 12.2203 | 2.794 | 1347.7998 | 1557.1605 | 3.8 | 2904.9603 | 1456.3603
DEER-SFAM-CZ12-V4-eSH-14-MH-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-MH | 13.1307 | 2.595 | 1284.2349 | 1620.408 | 3.5 | 2904.6429 | 1449.3429
DEER-SFAM-CZ12-V4-eSH-14-ML-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-ML | 13.2113 | 2.8437 | 1273.3041 | 1647.3323 | 3.8 | 2920.6364 | 1478.6364
DEER-SFAM-CZ12-V4-eSH-14-MM-s1 | 14 | CZ12 | V4 | CZ12-V4-eSH-14 | CZ12-V4-eSH-14-MM | 13.0217 | 2.7076 | 1284.6641 | 1500.1966 | 3.5 | 2784.8607 | 1427.1607
DEER-SFAM-CZ12-V4-eSH-15-HH-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-HH | 13.0774 | 2.5775 | 1248.0745 | 1760.0288 | 3.8 | 3008.1033 | 1365.7033
DEER-SFAM-CZ12-V4-eSH-15-HL-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-HL | 13.4114 | 2.743 | 1249.7724 | 1352.6226 | 3.8 | 2602.395 | 1366.195
DEER-SFAM-CZ12-V4-eSH-15-HM-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-HM | 13.874 | 2.6068 | 1210.0476 | 1419.11 | 3.8 | 2629.1576 | 1325.6576
DEER-SFAM-CZ12-V4-eSH-15-MH-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-MH | 13.77 | 2.6512 | 1227.184 | 1546.6043 | 3.5 | 2773.7883 | 1338.5883
DEER-SFAM-CZ12-V4-eSH-15-ML-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-ML | 14.1275 | 2.677 | 1189.588 | 1464.8185 | 3.8 | 2654.4065 | 1305.6065
DEER-SFAM-CZ12-V4-eSH-15-MM-s1 | 15 | CZ12 | V4 | CZ12-V4-eSH-15 | CZ12-V4-eSH-15-MM | 14.1125 | 2.6109 | 1201.0331 | 1587.5897 | 3.8 | 2788.6228 | 1325.0228
DEER-SFAM-CZ12-V4-eSH-16-CH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-CH | 14.2953 | 2.7454 | 1346.6707 | 1563.6091 | 3.8 | 2910.2798 | 1446.2798
DEER-SFAM-CZ12-V4-eSH-16-CL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-CL | 14.4735 | 3.0165 | 1363.4922 | 1457.1653 | 3.8 | 2820.6575 | 1467.5575
DEER-SFAM-CZ12-V4-eSH-16-LH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-LH | 13.5494 | 2.5459 | 1251.9932 | 1668.4033 | 3.5 | 2920.3965 | 1368.6965
DEER-SFAM-CZ12-V4-eSH-16-LL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-LL | 13.5918 | 2.6842 | 1266.5253 | 1509.3956 | 3.5 | 2775.9209 | 1360.3209
DEER-SFAM-CZ12-V4-eSH-16-LM-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-LM | 13.2573 | 2.6235 | 1285.1614 | 1660.503 | 3.5 | 2945.6644 | 1415.5644
DEER-SFAM-CZ12-V4-eSH-16-TH-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-TH | 14.4005 | 2.7881 | 1306.3048 | 1956.7543 | 3.8 | 3263.0591 | 1400.7591
DEER-SFAM-CZ12-V4-eSH-16-TL-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-TL | 13.9572 | 3.0504 | 1414.145 | 1909.8833 | 3.5 | 3324.0283 | 1502.5283
DEER-SFAM-CZ12-V4-eSH-16-TM-s2 | 16 | CZ12 | V4 | CZ12-V4-eSH-16 | CZ12-V4-eSH-16-TM | 14.0987 | 2.9988 | 1400.0554 | 1943.9578 | 3.5 | 3344.0132 | 1490.8132
DEER-SFAM-CZ12-V4-eSH-17-CM-s2 | 17 | CZ12 | V4 | CZ12-V4-eSH-17 | CZ12-V4-eSH-17-CM | 15.2695 | 2.8705 | 1290.8764 | 1523.853 | 3.8 | 2814.7294 | 1400.4294
DEER-SFAM-CZ12-V4-eSH-17-LM-s2 | 17 | CZ12 | V4 | CZ12-V4-eSH-17 | CZ12-V4-eSH-17-LM | 14.1557 | 2.7045 | 1259.2583 | 1468.8088 | 3.5 | 2728.0671 | 1311.9671
DEER-SFAM-CZ12-V4-eSH-17-TH-s2 | 17 | CZ12 | V4 | CZ12-V4-eSH-17 | CZ12-V4-eSH-17-TH | 15.2372 | 2.6589 | 1232.3456 | 1951.176 | 3.8 | 3183.5216 | 1333.7216
DEER-SFAM-CZ12-V4-eSH-17-TL-s2 | 17 | CZ12 | V4 | CZ12-V4-eSH-17 | CZ12-V4-eSH-17-TL | 15.2295 | 2.6997 | 1235.9254 | 1923.7828 | 3.8 | 3159.7082 | 1336.0082
DEER-SFAM-CZ12-V4-eSH-18-LH-s2 | 18 | CZ12 | V4 | CZ12-V4-eSH-18 | CZ12-V4-eSH-18-LH | 15.0878 | 2.4543 | 1140.9699 | 1649.0021 | 3.5 | 2789.972 | 1225.772
DEER-SFAM-CZ12-V4-eSH-18-LL-s2 | 18 | CZ12 | V4 | CZ12-V4-eSH-18 | CZ12-V4-eSH-18-LL | 14.477 | 2.5301 | 1181.5714 | 1500.0412 | 3.5 | 2681.6126 | 1262.3126
DEER-SFAM-CZ12-V4-eSH-18-LM-s2 | 18 | CZ12 | V4 | CZ12-V4-eSH-18 | CZ12-V4-eSH-18-LM | 15.1012 | 2.4665 | 1148.685 | 1723.5225 | 3.5 | 2872.2075 | 1245.4075
DEER-SFAM-CZ12-V4-eSH-18-TM-s2 | 18 | CZ12 | V4 | CZ12-V4-eSH-18 | CZ12-V4-eSH-18-TM | 16.1172 | 2.5746 | 1181.8013 | 1927.2075 | 3.5 | 3109.0088 | 1339.3088
DEER-SFAM-CZ13-V1-eSA-10-HH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-HH | 9.5454 | 4.4359 | 4345.8121 | 0 | 3.5124 | 4345.8121 | 4512.0509
DEER-SFAM-CZ13-V1-eSA-10-HL-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-HL | 8.7129 | 4.9516 | 4619.9632 | 0 | 3.5124 | 4619.9632 | 4786.3145
DEER-SFAM-CZ13-V1-eSA-10-HM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-HM | 8.7688 | 4.6215 | 4458.7109 | 0 | 3.5124 | 4458.7109 | 4625.0424
DEER-SFAM-CZ13-V1-eSA-10-LH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-LH | 10.4442 | 4.1875 | 4178.9342 | 0 | 3.5124 | 4178.9342 | 4345.3991
DEER-SFAM-CZ13-V1-eSA-10-LL-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-LL | 9.1659 | 4.5175 | 4406.1378 | 0 | 3.5124 | 4406.1378 | 4572.5152
DEER-SFAM-CZ13-V1-eSA-10-LM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-LM | 10.2334 | 4.2442 | 4207.772 | 0 | 3.5124 | 4207.772 | 4374.2422
DEER-SFAM-CZ13-V1-eSA-10-MH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-MH | 10.2985 | 4.0744 | 4163.8221 | 0 | 3.5124 | 4163.8221 | 4330.2477
DEER-SFAM-CZ13-V1-eSA-10-ML-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-ML | 8.9988 | 4.5876 | 4535.2546 | 0 | 3.5124 | 4535.2546 | 4701.6091
DEER-SFAM-CZ13-V1-eSA-10-MM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSA-10 | CZ13-V1-eSA-10-MM | 9.7719 | 4.3066 | 4208.7007 | 0 | 3.5124 | 4208.7007 | 4375.0675
DEER-SFAM-CZ13-V1-eSA-13-HH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-HH | 11.7828 | 3.7011 | 3419.4945 | 0 | 3.5124 | 3419.4945 | 3569.4433
DEER-SFAM-CZ13-V1-eSA-13-HL-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-HL | 11.8176 | 3.9904 | 3452.6165 | 0 | 3.5124 | 3452.6165 | 3583.8517
DEER-SFAM-CZ13-V1-eSA-13-HM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-HM | 11.6407 | 3.8321 | 3428.9974 | 0 | 3.5124 | 3428.9974 | 3578.9017
DEER-SFAM-CZ13-V1-eSA-13-LH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-LH | 12.9858 | 3.3609 | 3207.5498 | 0 | 3.5124 | 3207.5498 | 3373.9348
DEER-SFAM-CZ13-V1-eSA-13-LL-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-LL | 12.2898 | 3.6736 | 3394.2199 | 0 | 3.5124 | 3394.2199 | 3560.3357
DEER-SFAM-CZ13-V1-eSA-13-LM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-LM | 12.3897 | 3.4883 | 3342.2604 | 0 | 3.5124 | 3342.2604 | 3508.5345
DEER-SFAM-CZ13-V1-eSA-13-MH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-MH | 12.598 | 3.5497 | 3329.1576 | 0 | 3.5124 | 3329.1576 | 3495.4894
DEER-SFAM-CZ13-V1-eSA-13-ML-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-ML | 11.4868 | 3.7695 | 3395.7632 | 0 | 3.5124 | 3395.7632 | 3561.5913
DEER-SFAM-CZ13-V1-eSA-13-MM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSA-13 | CZ13-V1-eSA-13-MM | 12.6306 | 3.6817 | 3299.3187 | 0 | 3.5124 | 3299.3187 | 3465.63
DEER-SFAM-CZ13-V1-eSA-14-HH-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-HH | 11.7958 | 3.6006 | 3298.8608 | 0 | 3.5124 | 3298.8608 | 3438.2657
DEER-SFAM-CZ13-V1-eSA-14-HL-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-HL | 12.9659 | 3.6212 | 3201.7376 | 0 | 3.5124 | 3201.7376 | 3304.2421
DEER-SFAM-CZ13-V1-eSA-14-HM-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-HM | 12.8909 | 3.6452 | 3285.8898 | 0 | 3.5124 | 3285.8898 | 3443.1528
DEER-SFAM-CZ13-V1-eSA-14-MH-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-MH | 13.4365 | 3.2357 | 3159.3729 | 0 | 3.5124 | 3159.3729 | 3268.6664
DEER-SFAM-CZ13-V1-eSA-14-ML-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-ML | 12.676 | 3.5497 | 3183.224 | 0 | 3.5124 | 3183.224 | 3357.7669
DEER-SFAM-CZ13-V1-eSA-14-MM-s1 | 14 | CZ13 | V1 | CZ13-V1-eSA-14 | CZ13-V1-eSA-14-MM | 13.2606 | 3.276 | 3116.3629 | 0 | 3.5124 | 3116.3629 | 3236.1783
DEER-SFAM-CZ13-V1-eSA-15-HH-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-HH | 13.2698 | 3.3424 | 2993.2167 | 0 | 3.5124 | 2993.2167 | 3109.4228
DEER-SFAM-CZ13-V1-eSA-15-HL-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-HL | 13.8307 | 3.3971 | 2950.2192 | 0 | 3.5124 | 2950.2192 | 3095.0679
DEER-SFAM-CZ13-V1-eSA-15-HM-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-HM | 13.2826 | 3.242 | 2958.325 | 0 | 3.5124 | 2958.325 | 3074.9643
DEER-SFAM-CZ13-V1-eSA-15-MH-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-MH | 13.4934 | 3.3995 | 3043.4697 | 0 | 3.5124 | 3043.4697 | 3130.0557
DEER-SFAM-CZ13-V1-eSA-15-ML-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-ML | 14.0245 | 3.3325 | 2990.1093 | 0 | 3.5124 | 2990.1093 | 3106.5834
DEER-SFAM-CZ13-V1-eSA-15-MM-s1 | 15 | CZ13 | V1 | CZ13-V1-eSA-15 | CZ13-V1-eSA-15-MM | 13.9386 | 3.3613 | 2982.7469 | 0 | 3.5124 | 2982.7469 | 3088.9231
DEER-SFAM-CZ13-V1-eSA-16-CH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-CH | 13.6228 | 3.4268 | 3589.507 | 0 | 3.5124 | 3589.507 | 3655.4784
DEER-SFAM-CZ13-V1-eSA-16-CL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-CL | 13.5788 | 3.5605 | 3414.1286 | 0 | 3.5124 | 3414.1286 | 3498.1039
DEER-SFAM-CZ13-V1-eSA-16-CM-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-CM | 13.4227 | 3.5395 | 3505.9479 | 0 | 3.5124 | 3505.9479 | 3594.6557
DEER-SFAM-CZ13-V1-eSA-16-LH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-LH | 13.6017 | 3.3165 | 3082.2003 | 0 | 3.5124 | 3082.2003 | 3195.8964
DEER-SFAM-CZ13-V1-eSA-16-LL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-LL | 13.0568 | 3.6033 | 3296.727 | 0 | 3.5124 | 3296.727 | 3371.5058
DEER-SFAM-CZ13-V1-eSA-16-LM-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-LM | 13.2463 | 3.4618 | 3248.0638 | 0 | 3.5124 | 3248.0638 | 3315.8327
DEER-SFAM-CZ13-V1-eSA-16-NM-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-NM | 14.5203 | 3.2935 | 2971.5751 | 0 | 3.5124 | 2971.5751 | 3038.0072
DEER-SFAM-CZ13-V1-eSA-16-TH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-TH | 12.9736 | 3.7428 | 3745.5674 | 0 | 3.5124 | 3745.5674 | 3787.5073
DEER-SFAM-CZ13-V1-eSA-16-TL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSA-16 | CZ13-V1-eSA-16-TL | 13.523 | 3.6336 | 3443.8671 | 0 | 3.5124 | 3443.8671 | 3489.2783
DEER-SFAM-CZ13-V1-eSA-17-CH-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-CH | 14.3255 | 3.3232 | 3345.9983 | 0 | 3.5124 | 3345.9983 | 3429.9185
DEER-SFAM-CZ13-V1-eSA-17-CL-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-CL | 14.1388 | 3.393 | 3350.5839 | 0 | 3.5124 | 3350.5839 | 3434.4866
DEER-SFAM-CZ13-V1-eSA-17-CM-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-CM | 14.2676 | 3.3738 | 3384.0443 | 0 | 3.5124 | 3384.0443 | 3449.8174
DEER-SFAM-CZ13-V1-eSA-17-LH-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-LH | 14.0133 | 3.2449 | 3004.961 | 0 | 3.5124 | 3004.961 | 3094.1094
DEER-SFAM-CZ13-V1-eSA-17-LL-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-LL | 13.7211 | 3.4557 | 3180.0008 | 0 | 3.5124 | 3180.0008 | 3228.6394
DEER-SFAM-CZ13-V1-eSA-17-LM-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-LM | 13.6079 | 3.4109 | 3139.5795 | 0 | 3.5124 | 3139.5795 | 3181.5566
DEER-SFAM-CZ13-V1-eSA-17-TH-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-TH | 14.7705 | 3.2411 | 3125.6167 | 0 | 3.5124 | 3125.6167 | 3192.9623
DEER-SFAM-CZ13-V1-eSA-17-TL-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-TL | 14.5659 | 3.3325 | 2995.7333 | 0 | 3.5124 | 2995.7333 | 3101.9081
DEER-SFAM-CZ13-V1-eSA-17-TM-s2 | 17 | CZ13 | V1 | CZ13-V1-eSA-17 | CZ13-V1-eSA-17-TM | 15.0302 | 3.4089 | 3530.5789 | 0 | 3.5124 | 3530.5789 | 3565.58
DEER-SFAM-CZ13-V1-eSA-18-LH-s2 | 18 | CZ13 | V1 | CZ13-V1-eSA-18 | CZ13-V1-eSA-18-LH | 14.582 | 3.2053 | 2962.4971 | 0 | 3.5124 | 2962.4971 | 3020.939
DEER-SFAM-CZ13-V1-eSA-18-LL-s2 | 18 | CZ13 | V1 | CZ13-V1-eSA-18 | CZ13-V1-eSA-18-LL | 14.7042 | 3.1714 | 2873.7754 | 0 | 3.5124 | 2873.7754 | 2950.0306
DEER-SFAM-CZ13-V1-eSA-18-TH-s2 | 18 | CZ13 | V1 | CZ13-V1-eSA-18 | CZ13-V1-eSA-18-TH | 15.4838 | 3.0886 | 3002.198 | 0 | 3.5124 | 3002.198 | 3048.0189
DEER-SFAM-CZ13-V1-eSA-18-TL-s2 | 18 | CZ13 | V1 | CZ13-V1-eSA-18 | CZ13-V1-eSA-18-TL | 14.7515 | 3.4128 | 3342.1356 | 0 | 3.5124 | 3342.1356 | 3392.374
DEER-SFAM-CZ13-V1-eSA-18-TM-s2 | 18 | CZ13 | V1 | CZ13-V1-eSA-18 | CZ13-V1-eSA-18-TM | 14.8996 | 3.1819 | 3082.1847 | 0 | 3.5124 | 3082.1847 | 3128.9828
DEER-SFAM-CZ13-V1-eSH-10-HH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-HH | 9.8518 | 4.4313 | 4209.6881 | 3859.6078 | 3.5124 | 8069.2958 | 4601.6751
DEER-SFAM-CZ13-V1-eSH-10-HL-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-HL | 9.4293 | 4.5875 | 4391.2446 | 3885.5211 | 3.5124 | 8276.7657 | 4776.0924
DEER-SFAM-CZ13-V1-eSH-10-HM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-HM | 9.8994 | 4.5829 | 4315.7355 | 3743.2936 | 3.5124 | 8059.0291 | 4686.2849
DEER-SFAM-CZ13-V1-eSH-10-LH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-LH | 10.3895 | 4.1223 | 4096.6672 | 4096.5207 | 3.5124 | 8193.1879 | 4500.3279
DEER-SFAM-CZ13-V1-eSH-10-LL-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-LL | 9.8085 | 4.3915 | 4275.9311 | 4034.7355 | 3.5124 | 8310.6666 | 4697.4055
DEER-SFAM-CZ13-V1-eSH-10-LM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-LM | 10.1674 | 4.2543 | 4151.7666 | 3913.3531 | 3.5124 | 8065.1197 | 4536.7474
DEER-SFAM-CZ13-V1-eSH-10-MH-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-MH | 10.3464 | 4.3084 | 4174.1685 | 4068.0575 | 3.5124 | 8242.226 | 4603.1963
DEER-SFAM-CZ13-V1-eSH-10-ML-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-ML | 9.7029 | 4.6262 | 4376.5756 | 3764.7347 | 3.5124 | 8141.3104 | 4766.1064
DEER-SFAM-CZ13-V1-eSH-10-MM-s1 | 10 | CZ13 | V1 | CZ13-V1-eSH-10 | CZ13-V1-eSH-10-MM | 9.94 | 4.456 | 4326.0805 | 3919.8013 | 3.5124 | 8245.8818 | 4688.0433
DEER-SFAM-CZ13-V1-eSH-13-HH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-HH | 11.1895 | 3.8234 | 3550.862 | 3861.3286 | 3.5124 | 7412.1906 | 3907.6874
DEER-SFAM-CZ13-V1-eSH-13-HL-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-HL | 12.4985 | 3.9155 | 3398.6619 | 3322.005 | 3.5124 | 6720.6669 | 3754.2722
DEER-SFAM-CZ13-V1-eSH-13-HM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-HM | 11.4271 | 3.758 | 3493.2399 | 3390.9225 | 3.5124 | 6884.1624 | 3814.9712
DEER-SFAM-CZ13-V1-eSH-13-LH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-LH | 12.8892 | 3.3717 | 3255.2976 | 4363.3889 | 3.5124 | 7618.6865 | 3793.5324
DEER-SFAM-CZ13-V1-eSH-13-LL-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-LL | 13.1246 | 3.5689 | 3241.0495 | 3578.8487 | 3.5124 | 6819.8982 | 3567.971
DEER-SFAM-CZ13-V1-eSH-13-LM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-LM | 12.1442 | 3.5583 | 3387.9697 | 2982.4035 | 3.5124 | 6370.3732 | 3757.204
DEER-SFAM-CZ13-V1-eSH-13-MH-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-MH | 12.8516 | 3.5523 | 3241.6382 | 3937.5512 | 3.5124 | 7179.1894 | 3599.6693
DEER-SFAM-CZ13-V1-eSH-13-ML-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-ML | 11.8515 | 3.846 | 3477.4725 | 3668.9931 | 3.5124 | 7146.4656 | 3845.171
DEER-SFAM-CZ13-V1-eSH-13-MM-s1 | 13 | CZ13 | V1 | CZ13-V1-eSH-13 | CZ13-V1-eSH-13-MM | 12.3484 | 3.8466 | 3422.2167 | 3542.5209 | 3.5124 | 6964.7377 | 3706.0817
DEER-SFAM-CZ13-V1-eSH-14-HH-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-HH | 11.7911 | 3.6653 | 3367.1168 | 3532.998 | 3.5124 | 6900.1148 | 3638.6844
DEER-SFAM-CZ13-V1-eSH-14-HL-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-HL | 12.0706 | 3.6141 | 3284.7125 | 3588.57 | 3.5124 | 6873.2824 | 3612.363
DEER-SFAM-CZ13-V1-eSH-14-HM-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-HM | 12.136 | 3.4902 | 3248.5745 | 3521.4942 | 3.5124 | 6770.0687 | 3481.427
DEER-SFAM-CZ13-V1-eSH-14-MH-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-MH | 13.6935 | 3.195 | 3040.9868 | 3939.9339 | 3.5124 | 6980.9207 | 3396.2327
DEER-SFAM-CZ13-V1-eSH-14-ML-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-ML | 13.4699 | 3.5168 | 3131.476 | 4245.061 | 3.5124 | 7376.5369 | 3581.6994
DEER-SFAM-CZ13-V1-eSH-14-MM-s1 | 14 | CZ13 | V1 | CZ13-V1-eSH-14 | CZ13-V1-eSH-14-MM | 13.3005 | 3.4092 | 3103.0862 | 3495.9064 | 3.5124 | 6598.9926 | 3410.3325
DEER-SFAM-CZ13-V1-eSH-15-HH-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-HH | 13.0687 | 3.2309 | 2995.285 | 4456.354 | 3.5124 | 7451.639 | 3248.5754
DEER-SFAM-CZ13-V1-eSH-15-HL-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-HL | 13.252 | 3.3717 | 3037.3958 | 2979.4156 | 3.5124 | 6016.8114 | 3287.0635
DEER-SFAM-CZ13-V1-eSH-15-HM-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-HM | 14.0569 | 3.2923 | 2918.5388 | 3149.0526 | 3.5124 | 6067.5914 | 3168.5997
DEER-SFAM-CZ13-V1-eSH-15-MH-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-MH | 14.0834 | 3.359 | 3006.717 | 3859.6471 | 3.5124 | 6866.364 | 3250.5388
DEER-SFAM-CZ13-V1-eSH-15-ML-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-ML | 14.311 | 3.3667 | 2938.3531 | 3638.962 | 3.5124 | 6577.315 | 3191.9637
DEER-SFAM-CZ13-V1-eSH-15-MM-s1 | 15 | CZ13 | V1 | CZ13-V1-eSH-15 | CZ13-V1-eSH-15-MM | 14.1874 | 3.2587 | 2911.747 | 3785.9856 | 3.5124 | 6697.7326 | 3177.8346
DEER-SFAM-CZ13-V1-eSH-16-CH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-CH | 13.6431 | 3.4403 | 3454.8222 | 4238.4147 | 3.5124 | 7693.2369 | 3714.9067
DEER-SFAM-CZ13-V1-eSH-16-CL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-CL | 13.9705 | 3.4699 | 3568.8538 | 3946.5638 | 3.5124 | 7515.4176 | 3836.2297
DEER-SFAM-CZ13-V1-eSH-16-LH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-LH | 13.4569 | 3.3171 | 3099.2465 | 4441.5497 | 3.5124 | 7540.7962 | 3372.9829
DEER-SFAM-CZ13-V1-eSH-16-LL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-LL | 13.0811 | 3.5423 | 3252.3115 | 4138.4783 | 3.5124 | 7390.7898 | 3473.9321
DEER-SFAM-CZ13-V1-eSH-16-LM-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-LM | 13.0505 | 3.4354 | 3216.7505 | 4506.1541 | 3.5124 | 7722.9046 | 3524.2812
DEER-SFAM-CZ13-V1-eSH-16-TH-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-TH | 13.8331 | 3.6131 | 3333.2152 | 5250.8546 | 3.5124 | 8584.0698 | 3629.8219
DEER-SFAM-CZ13-V1-eSH-16-TL-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-TL | 13.0094 | 3.8096 | 3775.8429 | 5191.8329 | 3.5124 | 8967.6758 | 4046.394
DEER-SFAM-CZ13-V1-eSH-16-TM-s2 | 16 | CZ13 | V1 | CZ13-V1-eSH-16 | CZ13-V1-eSH-16-TM | 13.2031 | 3.7362 | 3722.9508 | 5238.9996 | 3.5124 | 8961.9504 | 3999.7642
DEER-SFAM-CZ13-V1-eSH-17-CM-s2 | 17 | CZ13 | V1 | CZ13-V1-eSH-17 | CZ13-V1-eSH-17-CM | 14.7282 | 3.3084 | 3378.7641 | 4309.9037 | 3.5124 | 7688.6678 | 3674.0923
DEER-SFAM-CZ13-V1-eSH-17-LM-s2 | 17 | CZ13 | V1 | CZ13-V1-eSH-17 | CZ13-V1-eSH-17-LM | 13.9609 | 3.3433 | 3225.5227 | 3998.3334 | 3.5124 | 7223.8562 | 3349.5849
DEER-SFAM-CZ13-V1-eSH-17-TH-s2 | 17 | CZ13 | V1 | CZ13-V1-eSH-17 | CZ13-V1-eSH-17-TH | 14.6153 | 3.3608 | 3143.3853 | 5235.8947 | 3.5124 | 8379.28 | 3456.6479
DEER-SFAM-CZ13-V1-eSH-17-TL-s2 | 17 | CZ13 | V1 | CZ13-V1-eSH-17 | CZ13-V1-eSH-17-TL | 14.4737 | 3.4423 | 3184.5626 | 5230.9264 | 3.5124 | 8415.489 | 3495.6208
DEER-SFAM-CZ13-V1-eSH-18-LH-s2 | 18 | CZ13 | V1 | CZ13-V1-eSH-18 | CZ13-V1-eSH-18-LH | 14.5122 | 3.2259 | 2944.18 | 4731.2061 | 3.5124 | 7675.3862 | 3168.071
DEER-SFAM-CZ13-V1-eSH-18-LL-s2 | 18 | CZ13 | V1 | CZ13-V1-eSH-18 | CZ13-V1-eSH-18-LL | 13.9088 | 3.3075 | 3038.7596 | 4220.7953 | 3.5124 | 7259.5549 | 3232.8962
DEER-SFAM-CZ13-V1-eSH-18-LM-s2 | 18 | CZ13 | V1 | CZ13-V1-eSH-18 | CZ13-V1-eSH-18-LM | 14.4578 | 3.2827 | 2988.6212 | 4990.9261 | 3.5124 | 7979.5473 | 3248.0977
DEER-SFAM-CZ13-V1-eSH-18-TM-s2 | 18 | CZ13 | V1 | CZ13-V1-eSH-18 | CZ13-V1-eSH-18-TM | 15.2548 | 3.3138 | 3060.8653 | 5272.7944 | 3.5124 | 8333.6597 | 3504.7901
DEER-SFAM-CZ13-V2-eSA-10-HH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-HH | 9.6047 | 3.86 | 4140.4283 | 0 | 3.074 | 4140.4283 | 4250.8603
DEER-SFAM-CZ13-V2-eSA-10-HL-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-HL | 8.7659 | 4.3112 | 4413.155 | 0 | 3.074 | 4413.155 | 4523.6675
DEER-SFAM-CZ13-V2-eSA-10-HM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-HM | 8.8404 | 4.0142 | 4252.7857 | 0 | 3.074 | 4252.7857 | 4363.2842
DEER-SFAM-CZ13-V2-eSA-10-LH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-LH | 10.3939 | 3.6558 | 3985.5665 | 0 | 3.074 | 3985.5665 | 4096.1593
DEER-SFAM-CZ13-V2-eSA-10-LL-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-LL | 9.183 | 3.9354 | 4226.4857 | 0 | 3.074 | 4226.4857 | 4337.0175
DEER-SFAM-CZ13-V2-eSA-10-LM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-LM | 10.1996 | 3.6984 | 4014.8182 | 0 | 3.074 | 4014.8182 | 4125.4142
DEER-SFAM-CZ13-V2-eSA-10-MH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-MH | 10.2881 | 3.556 | 3969.567 | 0 | 3.074 | 3969.567 | 4080.132
DEER-SFAM-CZ13-V2-eSA-10-ML-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-ML | 9.01 | 4.0033 | 4346.296 | 0 | 3.074 | 4346.296 | 4456.8108
DEER-SFAM-CZ13-V2-eSA-10-MM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSA-10 | CZ13-V2-eSA-10-MM | 9.859 | 3.5934 | 3992.1755 | 0 | 2.9592 | 3992.1755 | 4102.6749
DEER-SFAM-CZ13-V2-eSA-13-HH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-HH | 11.9093 | 3.2313 | 3270.164 | 0 | 3.074 | 3270.164 | 3369.7808
DEER-SFAM-CZ13-V2-eSA-13-HL-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-HL | 11.8865 | 3.4992 | 3300.6548 | 0 | 3.074 | 3300.6548 | 3387.8395
DEER-SFAM-CZ13-V2-eSA-13-HM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-HM | 11.5601 | 3.664 | 3330.4928 | 0 | 3.4592 | 3330.4928 | 3430.1623
DEER-SFAM-CZ13-V2-eSA-13-LH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-LH | 13.0049 | 2.947 | 3063.2693 | 0 | 3.074 | 3063.2693 | 3173.8066
DEER-SFAM-CZ13-V2-eSA-13-LL-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-LL | 12.3041 | 3.2134 | 3251.1734 | 0 | 3.074 | 3251.1734 | 3361.5187
DEER-SFAM-CZ13-V2-eSA-13-LM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-LM | 12.4038 | 3.0525 | 3197.6878 | 0 | 3.074 | 3197.6878 | 3308.1443
DEER-SFAM-CZ13-V2-eSA-13-MH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-MH | 12.6822 | 3.0945 | 3165.128 | 0 | 3.074 | 3165.128 | 3275.6266
DEER-SFAM-CZ13-V2-eSA-13-ML-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-ML | 11.5727 | 3.306 | 3245.4708 | 0 | 3.074 | 3245.4708 | 3355.6317
DEER-SFAM-CZ13-V2-eSA-13-MM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSA-13 | CZ13-V2-eSA-13-MM | 12.5395 | 3.5305 | 3180.779 | 0 | 3.4592 | 3180.779 | 3291.3572
DEER-SFAM-CZ13-V2-eSA-14-HH-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-HH | 11.8783 | 3.1497 | 3150.0192 | 0 | 3.074 | 3150.0192 | 3242.6293
DEER-SFAM-CZ13-V2-eSA-14-HL-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-HL | 12.8561 | 3.444 | 3090.5116 | 0 | 3.4592 | 3090.5116 | 3158.6676
DEER-SFAM-CZ13-V2-eSA-14-HM-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-HM | 12.8759 | 3.1951 | 3135.3034 | 0 | 3.074 | 3135.3034 | 3239.7803
DEER-SFAM-CZ13-V2-eSA-14-MH-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-MH | 13.427 | 2.8323 | 3022.5274 | 0 | 3.074 | 3022.5274 | 3095.1321
DEER-SFAM-CZ13-V2-eSA-14-ML-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-ML | 12.7308 | 3.1162 | 3047.198 | 0 | 3.074 | 3047.198 | 3163.1514
DEER-SFAM-CZ13-V2-eSA-14-MM-s1 | 14 | CZ13 | V2 | CZ13-V2-eSA-14 | CZ13-V2-eSA-14-MM | 13.2679 | 2.8656 | 2981.2904 | 0 | 3.074 | 2981.2904 | 3060.8881
DEER-SFAM-CZ13-V2-eSA-15-HH-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-HH | 13.1751 | 3.2083 | 2908.0529 | 0 | 3.4592 | 2908.0529 | 2985.3166
DEER-SFAM-CZ13-V2-eSA-15-HL-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-HL | 13.7181 | 3.2472 | 2853.652 | 0 | 3.4592 | 2853.652 | 2949.9614
DEER-SFAM-CZ13-V2-eSA-15-HM-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-HM | 13.2487 | 3.104 | 2868.2985 | 0 | 3.4592 | 2868.2985 | 2945.8513
DEER-SFAM-CZ13-V2-eSA-15-MH-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-MH | 13.5325 | 2.9859 | 2900.6226 | 0 | 3.074 | 2900.6226 | 2958.1467
DEER-SFAM-CZ13-V2-eSA-15-ML-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-ML | 14.0586 | 2.9217 | 2860.761 | 0 | 3.074 | 2860.761 | 2938.1316
DEER-SFAM-CZ13-V2-eSA-15-MM-s1 | 15 | CZ13 | V2 | CZ13-V2-eSA-15 | CZ13-V2-eSA-15-MM | 13.9405 | 2.9469 | 2846.066 | 0 | 3.074 | 2846.066 | 2916.6037
DEER-SFAM-CZ13-V2-eSA-16-CH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-CH | 13.6538 | 2.9977 | 3337.8521 | 0 | 3.074 | 3337.8521 | 3382.4904
DEER-SFAM-CZ13-V2-eSA-16-CL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-CL | 13.7114 | 3.3854 | 3229.5882 | 0 | 3.4592 | 3229.5882 | 3286.2489
DEER-SFAM-CZ13-V2-eSA-16-CM-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-CM | 13.4839 | 3.4045 | 3331.8318 | 0 | 3.4592 | 3331.8318 | 3391.6717
DEER-SFAM-CZ13-V2-eSA-16-LH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-LH | 13.7504 | 2.8853 | 2889.3177 | 0 | 3.074 | 2889.3177 | 2965.6736
DEER-SFAM-CZ13-V2-eSA-16-LL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-LL | 13.1903 | 3.1401 | 3090.1264 | 0 | 3.074 | 3090.1264 | 3140.2697
DEER-SFAM-CZ13-V2-eSA-16-LM-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-LM | 13.3443 | 3.0164 | 3047.7367 | 0 | 3.074 | 3047.7367 | 3093.2016
DEER-SFAM-CZ13-V2-eSA-16-NM-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-NM | 14.6176 | 2.857 | 2792.5844 | 0 | 3.074 | 2792.5844 | 2837.1996
DEER-SFAM-CZ13-V2-eSA-16-TH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-TH | 13.105 | 3.2658 | 3445.611 | 0 | 3.074 | 3445.611 | 3474.1866
DEER-SFAM-CZ13-V2-eSA-16-TL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSA-16 | CZ13-V2-eSA-16-TL | 13.7559 | 3.4545 | 3241.3902 | 0 | 3.4592 | 3241.3902 | 3272.2823
DEER-SFAM-CZ13-V2-eSA-17-CH-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-CH | 14.3754 | 2.9056 | 3114.4698 | 0 | 3.074 | 3114.4698 | 3171.0127
DEER-SFAM-CZ13-V2-eSA-17-CL-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-CL | 14.1904 | 2.9666 | 3118.3806 | 0 | 3.074 | 3118.3806 | 3174.9111
DEER-SFAM-CZ13-V2-eSA-17-CM-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-CM | 14.3201 | 2.9507 | 3144.5011 | 0 | 3.074 | 3144.5011 | 3189.0057
DEER-SFAM-CZ13-V2-eSA-17-LH-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-LH | 14.1606 | 2.8221 | 2816.5764 | 0 | 3.074 | 2816.5764 | 2876.4047
DEER-SFAM-CZ13-V2-eSA-17-LL-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-LL | 13.8552 | 3.0117 | 2975.1316 | 0 | 3.074 | 2975.1316 | 3007.7617
DEER-SFAM-CZ13-V2-eSA-17-LM-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-LM | 13.7504 | 2.9701 | 2947.6986 | 0 | 3.074 | 2947.6986 | 2975.854
DEER-SFAM-CZ13-V2-eSA-17-TH-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-TH | 14.8708 | 2.8332 | 2907.0272 | 0 | 3.074 | 2907.0272 | 2952.7114
DEER-SFAM-CZ13-V2-eSA-17-TL-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-TL | 14.6889 | 2.8718 | 2788.4935 | 0 | 3.074 | 2788.4935 | 2860.2699
DEER-SFAM-CZ13-V2-eSA-17-TM-s2 | 17 | CZ13 | V2 | CZ13-V2-eSA-17 | CZ13-V2-eSA-17-TM | 15.0356 | 3.3169 | 3338.5976 | 0 | 3.4592 | 3338.5976 | 3362.5406
DEER-SFAM-CZ13-V2-eSA-18-LH-s2 | 18 | CZ13 | V2 | CZ13-V2-eSA-18 | CZ13-V2-eSA-18-LH | 14.7402 | 2.7958 | 2769.9409 | 0 | 3.074 | 2769.9409 | 2809.1489
DEER-SFAM-CZ13-V2-eSA-18-LL-s2 | 18 | CZ13 | V2 | CZ13-V2-eSA-18 | CZ13-V2-eSA-18-LL | 14.8243 | 2.7596 | 2698.6374 | 0 | 3.074 | 2698.6374 | 2749.8103
DEER-SFAM-CZ13-V2-eSA-18-TH-s2 | 18 | CZ13 | V2 | CZ13-V2-eSA-18 | CZ13-V2-eSA-18-TH | 15.6458 | 2.6945 | 2783.5607 | 0 | 3.074 | 2783.5607 | 2814.603
DEER-SFAM-CZ13-V2-eSA-18-TL-s2 | 18 | CZ13 | V2 | CZ13-V2-eSA-18 | CZ13-V2-eSA-18-TL | 14.9161 | 2.9948 | 3078.706 | 0 | 3.074 | 3078.706 | 3112.8513
DEER-SFAM-CZ13-V2-eSA-18-TM-s2 | 18 | CZ13 | V2 | CZ13-V2-eSA-18 | CZ13-V2-eSA-18-TM | 15.016 | 2.7821 | 2863.2648 | 0 | 3.074 | 2863.2648 | 2894.9938
DEER-SFAM-CZ13-V2-eSH-10-HH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-HH | 9.6557 | 4.2509 | 4100.3383 | 2517.4868 | 3.4592 | 6617.8251 | 4356.6402
DEER-SFAM-CZ13-V2-eSH-10-HL-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-HL | 9.2805 | 4.4109 | 4263.9739 | 2545.196 | 3.4592 | 6809.1698 | 4515.1634
DEER-SFAM-CZ13-V2-eSH-10-HM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-HM | 9.9199 | 3.9898 | 4113.4739 | 2469.9939 | 3.074 | 6583.4678 | 4355.0022
DEER-SFAM-CZ13-V2-eSH-10-LH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-LH | 10.4005 | 3.5999 | 3911.2781 | 2639.2991 | 3.074 | 6550.5772 | 4175.0375
DEER-SFAM-CZ13-V2-eSH-10-LL-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-LL | 9.8317 | 3.8204 | 4077.0531 | 2615.4286 | 3.074 | 6692.4817 | 4352.6412
DEER-SFAM-CZ13-V2-eSH-10-LM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-LM | 10.183 | 3.7017 | 3962.6857 | 2556.8842 | 3.074 | 6519.5699 | 4214.867
DEER-SFAM-CZ13-V2-eSH-10-MH-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-MH | 10.3385 | 3.7594 | 3982.1827 | 2627.2726 | 3.074 | 6609.4553 | 4262.3596
DEER-SFAM-CZ13-V2-eSH-10-ML-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-ML | 9.717 | 4.0283 | 4173.3344 | 2464.6444 | 3.074 | 6637.9787 | 4428.7813
DEER-SFAM-CZ13-V2-eSH-10-MM-s1 | 10 | CZ13 | V2 | CZ13-V2-eSH-10 | CZ13-V2-eSH-10-MM | 9.9414 | 3.8815 | 4126.4779 | 2560.4963 | 3.074 | 6686.9742 | 4363.4014
DEER-SFAM-CZ13-V2-eSH-13-HH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-HH | 11.3086 | 3.3377 | 3389.2223 | 2469.994 | 3.074 | 5859.2163 | 3622.7691
DEER-SFAM-CZ13-V2-eSH-13-HL-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-HL | 12.4226 | 3.7733 | 3280.9891 | 2122.6605 | 3.4592 | 5403.6497 | 3513.7438
DEER-SFAM-CZ13-V2-eSH-13-HM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-HM | 11.5354 | 3.2762 | 3338.0221 | 2194.0337 | 3.074 | 5532.0558 | 3548.7136
DEER-SFAM-CZ13-V2-eSH-13-LH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-LH | 12.8857 | 2.9537 | 3109.3724 | 2691.1056 | 3.074 | 5800.4779 | 3461.0036
DEER-SFAM-CZ13-V2-eSH-13-LL-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-LL | 13.1606 | 3.1286 | 3090.6879 | 2274.7287 | 3.074 | 5365.4167 | 3304.7328
DEER-SFAM-CZ13-V2-eSH-13-LM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-LM | 12.1493 | 3.1166 | 3243.0158 | 1933.8232 | 3.074 | 5176.839 | 3484.3037
DEER-SFAM-CZ13-V2-eSH-13-MH-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-MH | 12.6357 | 3.4158 | 3151.7419 | 2461.8426 | 3.4592 | 5613.5845 | 3385.9278
DEER-SFAM-CZ13-V2-eSH-13-ML-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-ML | 11.8732 | 3.3686 | 3332.0995 | 2323.5406 | 3.074 | 5655.6401 | 3571.8491
DEER-SFAM-CZ13-V2-eSH-13-MM-s1 | 13 | CZ13 | V2 | CZ13-V2-eSH-13 | CZ13-V2-eSH-13-MM | 12.4049 | 3.3657 | 3263.594 | 2302.591 | 3.074 | 5566.185 | 3449.3934
DEER-SFAM-CZ13-V2-eSH-14-HH-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-HH | 11.9112 | 3.1974 | 3215.8704 | 2265.1116 | 3.074 | 5480.982 | 3393.6551
DEER-SFAM-CZ13-V2-eSH-14-HL-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-HL | 12.0518 | 3.4546 | 3177.2016 | 2214.6512 | 3.4592 | 5391.8528 | 3391.4595
DEER-SFAM-CZ13-V2-eSH-14-HM-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-HM | 12.0924 | 3.3292 | 3151.2346 | 2196.0156 | 3.4592 | 5347.2501 | 3303.9205
DEER-SFAM-CZ13-V2-eSH-14-MH-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-MH | 13.6985 | 2.8018 | 2907.2785 | 2445.9607 | 3.074 | 5353.2392 | 3140.094
DEER-SFAM-CZ13-V2-eSH-14-ML-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-ML | 13.2729 | 3.3845 | 3017.8501 | 2476.515 | 3.4592 | 5494.3651 | 3311.8417
DEER-SFAM-CZ13-V2-eSH-14-MM-s1 | 14 | CZ13 | V2 | CZ13-V2-eSH-14 | CZ13-V2-eSH-14-MM | 13.2898 | 2.9909 | 2970.7255 | 2204.8377 | 3.074 | 5175.5632 | 3171.3516
DEER-SFAM-CZ13-V2-eSH-15-HH-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-HH | 13.0279 | 3.0915 | 2904.2609 | 2623.9115 | 3.4592 | 5528.1724 | 3071.4723
DEER-SFAM-CZ13-V2-eSH-15-HL-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-HL | 13.1979 | 3.2232 | 2947.9776 | 1901.3086 | 3.4592 | 4849.2861 | 3111.3373
DEER-SFAM-CZ13-V2-eSH-15-HM-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-HM | 13.8698 | 3.1491 | 2834.152 | 1969.2349 | 3.4592 | 4803.3869 | 2997.3766
DEER-SFAM-CZ13-V2-eSH-15-MH-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-MH | 14.091 | 2.946 | 2862.4164 | 2361.5229 | 3.074 | 5223.9393 | 3020.9012
DEER-SFAM-CZ13-V2-eSH-15-ML-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-ML | 14.1329 | 3.2366 | 2830.1855 | 2164.8441 | 3.4592 | 4995.0297 | 2995.527
DEER-SFAM-CZ13-V2-eSH-15-MM-s1 | 15 | CZ13 | V2 | CZ13-V2-eSH-15 | CZ13-V2-eSH-15-MM | 14.0431 | 3.1172 | 2821.7988 | 2295.216 | 3.4592 | 5117.0148 | 2996.6188
DEER-SFAM-CZ13-V2-eSH-16-CH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-CH | 13.6845 | 2.9867 | 3216.2694 | 2630.4178 | 3.074 | 5846.6872 | 3383.8276
DEER-SFAM-CZ13-V2-eSH-16-CL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-CL | 13.9991 | 3.0372 | 3315.2129 | 2442.5505 | 3.074 | 5757.7634 | 3487.2792
DEER-SFAM-CZ13-V2-eSH-16-LH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-LH | 13.6325 | 2.8925 | 2902.8015 | 2709.5577 | 3.074 | 5612.3592 | 3077.0175
DEER-SFAM-CZ13-V2-eSH-16-LL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-LL | 13.1827 | 3.0844 | 3057.3359 | 2504.5923 | 3.074 | 5561.9282 | 3197.4467
DEER-SFAM-CZ13-V2-eSH-16-LM-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-LM | 13.2008 | 2.9845 | 3016.3916 | 2739.8438 | 3.074 | 5756.2354 | 3211.6005
DEER-SFAM-CZ13-V2-eSH-16-TH-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-TH | 13.9752 | 3.4669 | 3163.6915 | 3303.9589 | 3.4592 | 6467.6504 | 3344.5852
DEER-SFAM-CZ13-V2-eSH-16-TL-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-TL | 13.0968 | 3.3323 | 3483.7806 | 3248.7886 | 3.074 | 6732.5692 | 3657.0219
DEER-SFAM-CZ13-V2-eSH-16-TM-s2 | 16 | CZ13 | V2 | CZ13-V2-eSH-16 | CZ13-V2-eSH-16-TM | 13.2915 | 3.2688 | 3434.9937 | 3283.0855 | 3.074 | 6718.0792 | 3612.8252
DEER-SFAM-CZ13-V2-eSH-17-CM-s2 | 17 | CZ13 | V2 | CZ13-V2-eSH-17 | CZ13-V2-eSH-17-CM | 14.7574 | 2.8968 | 3139.1767 | 2619.7108 | 3.074 | 5758.8875 | 3324.7145
DEER-SFAM-CZ13-V2-eSH-17-LM-s2 | 17 | CZ13 | V2 | CZ13-V2-eSH-17 | CZ13-V2-eSH-17-LM | 14.0682 | 2.9138 | 3016.9068 | 2417.5777 | 3.074 | 5434.4845 | 3095.4291
DEER-SFAM-CZ13-V2-eSH-17-TH-s2 | 17 | CZ13 | V2 | CZ13-V2-eSH-17 | CZ13-V2-eSH-17-TH | 14.7505 | 2.9297 | 2916.5625 | 3299.8166 | 3.074 | 6216.3791 | 3119.1251
DEER-SFAM-CZ13-V2-eSH-17-TL-s2 | 17 | CZ13 | V2 | CZ13-V2-eSH-17 | CZ13-V2-eSH-17-TL | 14.6135 | 3.0004 | 2954.7885 | 3287.8924 | 3.074 | 6242.6809 | 3155.1745
DEER-SFAM-CZ13-V2-eSH-18-LH-s2 | 18 | CZ13 | V2 | CZ13-V2-eSH-18 | CZ13-V2-eSH-18-LH | 14.632 | 2.8056 | 2759.9688 | 2889.2422 | 3.074 | 5649.211 | 2899.0223
DEER-SFAM-CZ13-V2-eSH-18-LL-s2 | 18 | CZ13 | V2 | CZ13-V2-eSH-18 | CZ13-V2-eSH-18-LL | 14.0206 | 2.8762 | 2856.0152 | 2546.7167 | 3.074 | 5402.7318 | 2978.3167
DEER-SFAM-CZ13-V2-eSH-18-LM-s2 | 18 | CZ13 | V2 | CZ13-V2-eSH-18 | CZ13-V2-eSH-18-LM | 14.6034 | 2.8464 | 2795.638 | 3060.595 | 3.074 | 5856.2331 | 2957.0389
DEER-SFAM-CZ13-V2-eSH-18-TM-s2 | 18 | CZ13 | V2 | CZ13-V2-eSH-18 | CZ13-V2-eSH-18-TM | 15.3368 | 2.8932 | 2845.2469 | 3316.439 | 3.074 | 6161.6859 | 3136.5521
DEER-SFAM-CZ13-V3-eSA-10-HH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-HH | 9.1977 | 4.4803 | 3945.9124 | 0 | 3.8 | 3945.9124 | 4018.3889
DEER-SFAM-CZ13-V3-eSA-10-HL-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-HL | 8.4868 | 4.9138 | 4186.7716 | 0 | 3.8 | 4186.7716 | 4259.2874
DEER-SFAM-CZ13-V3-eSA-10-HM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-HM | 8.587 | 4.5528 | 4042.4002 | 0 | 3.8 | 4042.4002 | 4114.9087
DEER-SFAM-CZ13-V3-eSA-10-LH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-LH | 9.7138 | 4.3279 | 3857.7415 | 0 | 3.8 | 3857.7415 | 3930.2957
DEER-SFAM-CZ13-V3-eSA-10-LL-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-LL | 8.903 | 4.5105 | 4005.665 | 0 | 3.8 | 4005.665 | 4078.1901
DEER-SFAM-CZ13-V3-eSA-10-LM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-LM | 9.6137 | 4.3617 | 3860.6086 | 0 | 3.8 | 3860.6086 | 3933.1647
DEER-SFAM-CZ13-V3-eSA-10-MH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-MH | 9.677 | 3.9433 | 3830.6382 | 0 | 3.5 | 3830.6382 | 3903.1418
DEER-SFAM-CZ13-V3-eSA-10-ML-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-ML | 8.6947 | 4.6721 | 4124.9842 | 0 | 3.8 | 4124.9842 | 4197.501
DEER-SFAM-CZ13-V3-eSA-10-MM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSA-10 | CZ13-V3-eSA-10-MM | 9.4109 | 4.054 | 3843.0608 | 0 | 3.5 | 3843.0608 | 3915.5421
DEER-SFAM-CZ13-V3-eSA-13-HH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-HH | 11.4443 | 3.7499 | 3140.3098 | 0 | 3.8 | 3140.3098 | 3205.6762
DEER-SFAM-CZ13-V3-eSA-13-HL-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-HL | 11.4228 | 4.0542 | 3148.5002 | 0 | 3.8 | 3148.5002 | 3205.7121
DEER-SFAM-CZ13-V3-eSA-13-HM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-HM | 11.3085 | 3.7632 | 3130.1896 | 0 | 3.8 | 3130.1896 | 3195.5406
DEER-SFAM-CZ13-V3-eSA-13-LH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-LH | 12.2405 | 3.4482 | 2963.4533 | 0 | 3.8 | 2963.4533 | 3035.9814
DEER-SFAM-CZ13-V3-eSA-13-LL-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-LL | 11.7186 | 3.7311 | 3111.4987 | 0 | 3.8 | 3111.4987 | 3183.9333
DEER-SFAM-CZ13-V3-eSA-13-LM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-LM | 11.7793 | 3.3774 | 3072.7139 | 0 | 3.5 | 3072.7139 | 3145.16
DEER-SFAM-CZ13-V3-eSA-13-MH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-MH | 11.9923 | 3.5623 | 3041.4665 | 0 | 3.8 | 3041.4665 | 3113.9756
DEER-SFAM-CZ13-V3-eSA-13-ML-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-ML | 11.2769 | 3.8309 | 3068.6282 | 0 | 3.8 | 3068.6282 | 3140.9216
DEER-SFAM-CZ13-V3-eSA-13-MM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSA-13 | CZ13-V3-eSA-13-MM | 12.1676 | 3.6812 | 2976.5003 | 0 | 3.8 | 2976.5003 | 3049.0022
DEER-SFAM-CZ13-V3-eSA-14-HH-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-HH | 11.4601 | 3.6499 | 3006.6728 | 0 | 3.8 | 3006.6728 | 3067.4486
DEER-SFAM-CZ13-V3-eSA-14-HL-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-HL | 12.3913 | 3.5838 | 2906.2799 | 0 | 3.8 | 2906.2799 | 2950.9702
DEER-SFAM-CZ13-V3-eSA-14-HM-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-HM | 12.147 | 3.7265 | 3010.3372 | 0 | 3.8 | 3010.3372 | 3078.8893
DEER-SFAM-CZ13-V3-eSA-14-MH-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-MH | 12.6506 | 3.149 | 2915.7045 | 0 | 3.5 | 2915.7045 | 2963.3288
DEER-SFAM-CZ13-V3-eSA-14-ML-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-ML | 12.1932 | 3.6358 | 2925.9975 | 0 | 3.8 | 2925.9975 | 3002.0843
DEER-SFAM-CZ13-V3-eSA-14-MM-s1 | 14 | CZ13 | V3 | CZ13-V3-eSA-14 | CZ13-V3-eSA-14-MM | 12.576 | 3.1773 | 2870.0688 | 0 | 3.5 | 2870.0688 | 2922.2753
DEER-SFAM-CZ13-V3-eSA-15-HH-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-HH | 12.8239 | 3.309 | 2749.2804 | 0 | 3.8 | 2749.2804 | 2799.9406
DEER-SFAM-CZ13-V3-eSA-15-HL-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-HL | 13.2364 | 3.3799 | 2692.1628 | 0 | 3.8 | 2692.1628 | 2755.3135
DEER-SFAM-CZ13-V3-eSA-15-HM-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-HM | 12.9852 | 3.1953 | 2697.837 | 0 | 3.8 | 2697.837 | 2748.6877
DEER-SFAM-CZ13-V3-eSA-15-MH-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-MH | 12.7325 | 3.4932 | 2808.951 | 0 | 3.8 | 2808.951 | 2846.6989
DEER-SFAM-CZ13-V3-eSA-15-ML-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-ML | 13.3881 | 3.3639 | 2732.9043 | 0 | 3.8 | 2732.9043 | 2783.698
DEER-SFAM-CZ13-V3-eSA-15-MM-s1 | 15 | CZ13 | V3 | CZ13-V3-eSA-15 | CZ13-V3-eSA-15-MM | 13.2195 | 3.4265 | 2727.2114 | 0 | 3.8 | 2727.2114 | 2773.4997
DEER-SFAM-CZ13-V3-eSA-16-CH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-CH | 13.5613 | 3.5224 | 3073.4166 | 0 | 3.8 | 3073.4166 | 3102.697
DEER-SFAM-CZ13-V3-eSA-16-CL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-CL | 13.8399 | 3.3593 | 2879.1905 | 0 | 3.8 | 2879.1905 | 2916.2082
DEER-SFAM-CZ13-V3-eSA-16-CM-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-CM | 13.5048 | 3.4494 | 2991.6862 | 0 | 3.8 | 2991.6862 | 3030.7263
DEER-SFAM-CZ13-V3-eSA-16-LH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-LH | 13.5014 | 3.257 | 2693.4139 | 0 | 3.8 | 2693.4139 | 2743.6422
DEER-SFAM-CZ13-V3-eSA-16-LL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-LL | 13.0534 | 3.5194 | 2828.7581 | 0 | 3.8 | 2828.7581 | 2861.6982
DEER-SFAM-CZ13-V3-eSA-16-LM-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-LM | 13.1212 | 3.3872 | 2807.9701 | 0 | 3.8 | 2807.9701 | 2837.8349
DEER-SFAM-CZ13-V3-eSA-16-NM-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-NM | 14.8248 | 3.0963 | 2513.855 | 0 | 3.8 | 2513.855 | 2543.1945
DEER-SFAM-CZ13-V3-eSA-16-TH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-TH | 12.974 | 3.6847 | 3190.5404 | 0 | 3.8 | 3190.5404 | 3209.3587
DEER-SFAM-CZ13-V3-eSA-16-TL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSA-16 | CZ13-V3-eSA-16-TL | 13.9128 | 3.4848 | 2864.4663 | 0 | 3.8 | 2864.4663 | 2884.7554
DEER-SFAM-CZ13-V3-eSA-17-CH-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-CH | 14.321 | 3.4057 | 2858.3854 | 0 | 3.8 | 2858.3854 | 2895.3977
DEER-SFAM-CZ13-V3-eSA-17-CL-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-CL | 14.2856 | 3.3971 | 2836.4386 | 0 | 3.8 | 2836.4386 | 2873.4413
DEER-SFAM-CZ13-V3-eSA-17-CM-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-CM | 14.3761 | 3.3952 | 2866.6319 | 0 | 3.8 | 2866.6319 | 2895.8244
DEER-SFAM-CZ13-V3-eSA-17-LH-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-LH | 14.0264 | 2.9958 | 2588.397 | 0 | 3.5 | 2588.397 | 2627.719
DEER-SFAM-CZ13-V3-eSA-17-LL-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-LL | 13.7142 | 3.3927 | 2714.9964 | 0 | 3.8 | 2714.9964 | 2736.4006
DEER-SFAM-CZ13-V3-eSA-17-LM-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-LM | 13.6127 | 3.3315 | 2708.0374 | 0 | 3.8 | 2708.0374 | 2726.522
DEER-SFAM-CZ13-V3-eSA-17-TH-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-TH | 14.492 | 3.258 | 2744.4783 | 0 | 3.8 | 2744.4783 | 2774.5586
DEER-SFAM-CZ13-V3-eSA-17-TL-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-TL | 15.1596 | 3.1693 | 2533.2396 | 0 | 3.8 | 2533.2396 | 2580.2411
DEER-SFAM-CZ13-V3-eSA-17-TM-s2 | 17 | CZ13 | V3 | CZ13-V3-eSA-17 | CZ13-V3-eSA-17-TM | 14.9867 | 3.4748 | 2925.5287 | 0 | 3.8 | 2925.5287 | 2941.2538
DEER-SFAM-CZ13-V3-eSA-18-LH-s2 | 18 | CZ13 | V3 | CZ13-V3-eSA-18 | CZ13-V3-eSA-18-LH | 14.5046 | 3.1431 | 2546.4048 | 0 | 3.8 | 2546.4048 | 2572.1578
DEER-SFAM-CZ13-V3-eSA-18-LL-s2 | 18 | CZ13 | V3 | CZ13-V3-eSA-18 | CZ13-V3-eSA-18-LL | 14.756 | 3.1192 | 2482.218 | 0 | 3.8 | 2482.218 | 2515.8481
DEER-SFAM-CZ13-V3-eSA-18-TH-s2 | 18 | CZ13 | V3 | CZ13-V3-eSA-18 | CZ13-V3-eSA-18-TH | 15.2283 | 3.0652 | 2622.9593 | 0 | 3.8 | 2622.9593 | 2643.3755
DEER-SFAM-CZ13-V3-eSA-18-TL-s2 | 18 | CZ13 | V3 | CZ13-V3-eSA-18 | CZ13-V3-eSA-18-TL | 14.6672 | 3.5292 | 2858.0808 | 0 | 3.8 | 2858.0808 | 2880.5387
DEER-SFAM-CZ13-V3-eSA-18-TM-s2 | 18 | CZ13 | V3 | CZ13-V3-eSA-18 | CZ13-V3-eSA-18-TM | 14.6693 | 3.1683 | 2694.7475 | 0 | 3.8 | 2694.7475 | 2715.6298
DEER-SFAM-CZ13-V3-eSH-10-HH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-HH | 9.202 | 4.3799 | 3898.9147 | 1641.0792 | 3.8 | 5539.9939 | 4060.2939
DEER-SFAM-CZ13-V3-eSH-10-HL-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-HL | 8.9242 | 4.561 | 4021.2076 | 1649.7352 | 3.8 | 5670.9428 | 4179.4428
DEER-SFAM-CZ13-V3-eSH-10-HM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-HM | 9.3332 | 4.6027 | 3952.0793 | 1629.2087 | 3.8 | 5581.288 | 4103.988
DEER-SFAM-CZ13-V3-eSH-10-LH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-LH | 9.6605 | 4.2329 | 3826.5338 | 1713.04 | 3.8 | 5539.5738 | 3992.7738
DEER-SFAM-CZ13-V3-eSH-10-LL-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-LL | 9.3181 | 4.3936 | 3896.4138 | 1673.4649 | 3.8 | 5569.8787 | 4069.8787
DEER-SFAM-CZ13-V3-eSH-10-LM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-LM | 9.5593 | 4.2249 | 3818.278 | 1665.4867 | 3.8 | 5483.7647 | 3977.6647
DEER-SFAM-CZ13-V3-eSH-10-MH-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-MH | 9.6553 | 4.4142 | 3862.9895 | 1694.6977 | 3.8 | 5557.6872 | 4039.2872
DEER-SFAM-CZ13-V3-eSH-10-ML-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-ML | 9.2357 | 4.6303 | 3969.7806 | 1585.4131 | 3.8 | 5555.1937 | 4131.1937
DEER-SFAM-CZ13-V3-eSH-10-MM-s1 | 10 | CZ13 | V3 | CZ13-V3-eSH-10 | CZ13-V3-eSH-10-MM | 9.4942 | 4.2732 | 3917.1199 | 1648.4994 | 3.5 | 5565.6193 | 4067.0193
DEER-SFAM-CZ13-V3-eSH-13-HH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-HH | 10.8196 | 3.793 | 3262.2926 | 1580.5364 | 3.8 | 4842.829 | 3409.729
DEER-SFAM-CZ13-V3-eSH-13-HL-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-HL | 12.0004 | 3.9763 | 3078.2809 | 1366.6712 | 3.8 | 4444.9521 | 3224.9521
DEER-SFAM-CZ13-V3-eSH-13-HM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-HM | 11.1078 | 3.7084 | 3189.0278 | 1418.8465 | 3.8 | 4607.8743 | 3322.2743
DEER-SFAM-CZ13-V3-eSH-13-LH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-LH | 12.03 | 3.4996 | 3030.8044 | 1603.4266 | 3.8 | 4634.231 | 3250.631
DEER-SFAM-CZ13-V3-eSH-13-LL-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-LL | 12.4279 | 3.6197 | 2952.2297 | 1431.6241 | 3.8 | 4383.8538 | 3087.2538
DEER-SFAM-CZ13-V3-eSH-13-LM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-LM | 11.5544 | 3.4551 | 3113.5689 | 1241.1608 | 3.5 | 4354.7297 | 3266.0297
DEER-SFAM-CZ13-V3-eSH-13-MH-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-MH | 11.9731 | 3.5406 | 3014.9438 | 1597.4836 | 3.8 | 4612.4274 | 3162.0274
DEER-SFAM-CZ13-V3-eSH-13-ML-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-ML | 11.2769 | 3.9697 | 3215.8416 | 1446.7801 | 3.8 | 4662.6217 | 3366.6217
DEER-SFAM-CZ13-V3-eSH-13-MM-s1 | 13 | CZ13 | V3 | CZ13-V3-eSH-13 | CZ13-V3-eSH-13-MM | 11.7573 | 3.8646 | 3123.505 | 1486.9967 | 3.8 | 4610.5017 | 3241.3017
DEER-SFAM-CZ13-V3-eSH-14-HH-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-HH | 11.4703 | 3.6149 | 3077.1822 | 1448.8179 | 3.8 | 4526.0001 | 3189.5001
DEER-SFAM-CZ13-V3-eSH-14-HL-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-HL | 11.8675 | 3.5406 | 2970.0373 | 1414.1124 | 3.8 | 4384.1497 | 3104.5497
DEER-SFAM-CZ13-V3-eSH-14-HM-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-HM | 11.8501 | 3.4175 | 2961.7739 | 1416.0325 | 3.8 | 4377.8064 | 3058.0064
DEER-SFAM-CZ13-V3-eSH-14-MH-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-MH | 12.8295 | 3.2987 | 2827.729 | 1474.6276 | 3.8 | 4302.3566 | 2974.1566
DEER-SFAM-CZ13-V3-eSH-14-ML-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-ML | 12.7607 | 3.5534 | 2835.9741 | 1501.0243 | 3.8 | 4336.9984 | 3017.9984
DEER-SFAM-CZ13-V3-eSH-14-MM-s1 | 14 | CZ13 | V3 | CZ13-V3-eSH-14 | CZ13-V3-eSH-14-MM | 12.6199 | 3.4885 | 2850.6213 | 1370.1184 | 3.8 | 4220.7397 | 2976.8397
DEER-SFAM-CZ13-V3-eSH-15-HH-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-HH | 12.7489 | 3.172 | 2737.6494 | 1591.4422 | 3.8 | 4329.0916 | 2841.8916
DEER-SFAM-CZ13-V3-eSH-15-HL-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-HL | 12.9451 | 3.3409 | 2766.5305 | 1232.8076 | 3.8 | 3999.3381 | 2869.6381
DEER-SFAM-CZ13-V3-eSH-15-HM-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-HM | 13.3103 | 3.2545 | 2683.7504 | 1289.9511 | 3.8 | 3973.7015 | 2786.1015
DEER-SFAM-CZ13-V3-eSH-15-MH-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-MH | 13.2235 | 3.3971 | 2757.1476 | 1410.3171 | 3.8 | 4167.4647 | 2855.8647
DEER-SFAM-CZ13-V3-eSH-15-ML-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-ML | 13.6285 | 3.3968 | 2655.054 | 1339.9484 | 3.8 | 3995.0024 | 2757.9024
DEER-SFAM-CZ13-V3-eSH-15-MM-s1 | 15 | CZ13 | V3 | CZ13-V3-eSH-15 | CZ13-V3-eSH-15-MM | 13.4874 | 3.228 | 2668.2579 | 1447.2003 | 3.8 | 4115.4582 | 2778.1582
DEER-SFAM-CZ13-V3-eSH-16-CH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-CH | 13.7175 | 3.3012 | 2951.8823 | 1450.2195 | 3.8 | 4402.1018 | 3041.5018
DEER-SFAM-CZ13-V3-eSH-16-CL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-CL | 13.847 | 3.577 | 3046.9219 | 1354.4254 | 3.8 | 4401.3473 | 3140.2473
DEER-SFAM-CZ13-V3-eSH-16-LH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-LH | 13.1651 | 3.2839 | 2751.7526 | 1505.2022 | 3.8 | 4256.9548 | 2855.1548
DEER-SFAM-CZ13-V3-eSH-16-LL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-LL | 13.0936 | 3.2879 | 2797.4265 | 1382.2691 | 3.5 | 4179.6956 | 2880.6956
DEER-SFAM-CZ13-V3-eSH-16-LM-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-LM | 12.9625 | 3.1918 | 2797.6389 | 1507.9395 | 3.5 | 4305.5784 | 2913.3784
DEER-SFAM-CZ13-V3-eSH-16-TH-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-TH | 13.8896 | 3.5402 | 2853.633 | 1811.1682 | 3.8 | 4664.8012 | 2939.8012
DEER-SFAM-CZ13-V3-eSH-16-TL-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-TL | 13.1571 | 3.8081 | 3181.0556 | 1775.7446 | 3.8 | 4956.8002 | 3258.9002
DEER-SFAM-CZ13-V3-eSH-16-TM-s2 | 16 | CZ13 | V3 | CZ13-V3-eSH-16 | CZ13-V3-eSH-16-TM | 13.3035 | 3.7371 | 3146.8511 | 1803.6642 | 3.8 | 4950.5153 | 3227.0153
DEER-SFAM-CZ13-V3-eSH-17-CM-s2 | 17 | CZ13 | V3 | CZ13-V3-eSH-17 | CZ13-V3-eSH-17-CM | 14.5872 | 3.4092 | 2888.0021 | 1410.5647 | 3.8 | 4298.5668 | 2985.7668
DEER-SFAM-CZ13-V3-eSH-17-LM-s2 | 17 | CZ13 | V3 | CZ13-V3-eSH-17 | CZ13-V3-eSH-17-LM | 13.5797 | 3.4156 | 2811.7401 | 1337.3225 | 3.8 | 4149.0626 | 2858.4626
DEER-SFAM-CZ13-V3-eSH-17-TH-s2 | 17 | CZ13 | V3 | CZ13-V3-eSH-17 | CZ13-V3-eSH-17-TH | 14.5749 | 3.3295 | 2711.9688 | 1808.121 | 3.8 | 4520.0898 | 2805.2898
DEER-SFAM-CZ13-V3-eSH-17-TL-s2 | 17 | CZ13 | V3 | CZ13-V3-eSH-17 | CZ13-V3-eSH-17-TL | 14.5273 | 3.4074 | 2729.8631 | 1787.887 | 3.8 | 4517.7501 | 2821.7501
DEER-SFAM-CZ13-V3-eSH-18-LH-s2 | 18 | CZ13 | V3 | CZ13-V3-eSH-18 | CZ13-V3-eSH-18-LH | 14.4613 | 3.0019 | 2535.7812 | 1528.2649 | 3.5 | 4064.0461 | 2611.3461
DEER-SFAM-CZ13-V3-eSH-18-LL-s2 | 18 | CZ13 | V3 | CZ13-V3-eSH-18 | CZ13-V3-eSH-18-LL | 13.8726 | 3.0829 | 2624.9872 | 1378.0046 | 3.5 | 4002.9918 | 2696.6918
DEER-SFAM-CZ13-V3-eSH-18-LM-s2 | 18 | CZ13 | V3 | CZ13-V3-eSH-18 | CZ13-V3-eSH-18-LM | 14.481 | 3.0263 | 2548.6354 | 1604.759 | 3.5 | 4153.3944 | 2634.8944
DEER-SFAM-CZ13-V3-eSH-18-TM-s2 | 18 | CZ13 | V3 | CZ13-V3-eSH-18 | CZ13-V3-eSH-18-TM | 15.2771 | 3.1358 | 2620.2056 | 1809.9652 | 3.5 | 4430.1708 | 2768.9708
DEER-SFAM-CZ13-V4-eSA-10-HH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-HH | 9.1864 | 4.0568 | 3512.9423 | 0 | 3.5 | 3512.9423 | 3572.57
DEER-SFAM-CZ13-V4-eSA-10-HL-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-HL | 8.483 | 4.4393 | 3721.6257 | 0 | 3.5 | 3721.6257 | 3781.2858
DEER-SFAM-CZ13-V4-eSA-10-HM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-HM | 8.5795 | 4.1205 | 3593.6687 | 0 | 3.5 | 3593.6687 | 3653.3233
DEER-SFAM-CZ13-V4-eSA-10-LH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-LH | 9.7123 | 3.918 | 3428.6875 | 0 | 3.5 | 3428.6875 | 3488.3795
DEER-SFAM-CZ13-V4-eSA-10-LL-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-LL | 8.8991 | 4.0721 | 3559.7999 | 0 | 3.5 | 3559.7999 | 3619.4675
DEER-SFAM-CZ13-V4-eSA-10-LM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-LM | 9.6151 | 3.9461 | 3430.3886 | 0 | 3.5 | 3430.3886 | 3490.0821
DEER-SFAM-CZ13-V4-eSA-10-MH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-MH | 9.5364 | 3.8249 | 3453.2861 | 0 | 3.5 | 3453.2861 | 3512.9671
DEER-SFAM-CZ13-V4-eSA-10-ML-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-ML | 8.6931 | 4.2199 | 3666.8224 | 0 | 3.5 | 3666.8224 | 3726.4835
DEER-SFAM-CZ13-V4-eSA-10-MM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSA-10 | CZ13-V4-eSA-10-MM | 9.3401 | 3.9381 | 3442.5358 | 0 | 3.5 | 3442.5358 | 3502.2004
DEER-SFAM-CZ13-V4-eSA-13-HH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-HH | 11.4145 | 3.3904 | 2793.189 | 0 | 3.5 | 2793.189 | 2846.9672
DEER-SFAM-CZ13-V4-eSA-13-HL-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-HL | 11.4468 | 3.6687 | 2793.6379 | 0 | 3.5 | 2793.6379 | 2840.7069
DEER-SFAM-CZ13-V4-eSA-13-HM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-HM | 11.2529 | 3.5636 | 2792.983 | 0 | 3.8 | 2792.983 | 2846.7772
DEER-SFAM-CZ13-V4-eSA-13-LH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-LH | 12.2308 | 3.1212 | 2635.6746 | 0 | 3.5 | 2635.6746 | 2695.3447
DEER-SFAM-CZ13-V4-eSA-13-LL-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-LL | 11.7385 | 3.3813 | 2761.8254 | 0 | 3.5 | 2761.8254 | 2821.4191
DEER-SFAM-CZ13-V4-eSA-13-LM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-LM | 11.6701 | 3.2628 | 2755.9257 | 0 | 3.5 | 2755.9257 | 2815.5637
DEER-SFAM-CZ13-V4-eSA-13-MH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-MH | 11.9899 | 3.222 | 2704.8556 | 0 | 3.5 | 2704.8556 | 2764.5102
DEER-SFAM-CZ13-V4-eSA-13-ML-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-ML | 11.2868 | 3.4455 | 2724.0509 | 0 | 3.5 | 2724.0509 | 2783.5285
DEER-SFAM-CZ13-V4-eSA-13-MM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSA-13 | CZ13-V4-eSA-13-MM | 12.0957 | 3.4534 | 2659.6941 | 0 | 3.8 | 2659.6941 | 2719.3749
DEER-SFAM-CZ13-V4-eSA-14-HH-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-HH | 11.4543 | 3.2837 | 2672.4048 | 0 | 3.5 | 2672.4048 | 2722.4069
DEER-SFAM-CZ13-V4-eSA-14-HL-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-HL | 12.3522 | 3.373 | 2590.7423 | 0 | 3.8 | 2590.7423 | 2627.5296
DEER-SFAM-CZ13-V4-eSA-14-HM-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-HM | 12.1752 | 3.3674 | 2669.9917 | 0 | 3.5 | 2669.9917 | 2726.3909
DEER-SFAM-CZ13-V4-eSA-14-MH-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-MH | 12.5054 | 3.046 | 2621.1956 | 0 | 3.5 | 2621.1956 | 2660.4012
DEER-SFAM-CZ13-V4-eSA-14-ML-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-ML | 12.2107 | 3.2912 | 2596.0331 | 0 | 3.5 | 2596.0331 | 2658.6314
DEER-SFAM-CZ13-V4-eSA-14-MM-s1 | 14 | CZ13 | V4 | CZ13-V4-eSA-14 | CZ13-V4-eSA-14-MM | 12.4455 | 3.0717 | 2577.3213 | 0 | 3.5 | 2577.3213 | 2620.2978
DEER-SFAM-CZ13-V4-eSA-15-HH-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-HH | 12.7029 | 3.1401 | 2463.2128 | 0 | 3.8 | 2463.2128 | 2504.913
DEER-SFAM-CZ13-V4-eSA-15-HL-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-HL | 13.1935 | 3.1842 | 2400.7579 | 0 | 3.8 | 2400.7579 | 2452.742
DEER-SFAM-CZ13-V4-eSA-15-HM-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-HM | 12.8793 | 3.026 | 2412.9217 | 0 | 3.8 | 2412.9217 | 2454.7796
DEER-SFAM-CZ13-V4-eSA-15-MH-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-MH | 12.7386 | 3.167 | 2496.8044 | 0 | 3.5 | 2496.8044 | 2527.8603
DEER-SFAM-CZ13-V4-eSA-15-ML-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-ML | 13.417 | 3.0418 | 2424.8276 | 0 | 3.5 | 2424.8276 | 2466.6171
DEER-SFAM-CZ13-V4-eSA-15-MM-s1 | 15 | CZ13 | V4 | CZ13-V4-eSA-15 | CZ13-V4-eSA-15-MM | 13.243 | 3.0955 | 2421.8538 | 0 | 3.5 | 2421.8538 | 2459.9358
DEER-SFAM-CZ13-V4-eSA-16-CH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-CH | 13.6019 | 3.1756 | 2736.6244 | 0 | 3.5 | 2736.6244 | 2760.7293
DEER-SFAM-CZ13-V4-eSA-16-CL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-CL | 13.9161 | 3.163 | 2569.4738 | 0 | 3.8 | 2569.4738 | 2599.9699
DEER-SFAM-CZ13-V4-eSA-16-CM-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-CM | 13.5602 | 3.2575 | 2678.5787 | 0 | 3.8 | 2678.5787 | 2710.7425
DEER-SFAM-CZ13-V4-eSA-16-LH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-LH | 13.4686 | 2.929 | 2401.3917 | 0 | 3.5 | 2401.3917 | 2442.7281
DEER-SFAM-CZ13-V4-eSA-16-LL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-LL | 13.0491 | 3.1652 | 2520.6183 | 0 | 3.5 | 2520.6183 | 2547.7252
DEER-SFAM-CZ13-V4-eSA-16-LM-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-LM | 13.115 | 3.0518 | 2501.0397 | 0 | 3.5 | 2501.0397 | 2525.6154
DEER-SFAM-CZ13-V4-eSA-16-NM-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-NM | 14.8493 | 2.7763 | 2233.6423 | 0 | 3.5 | 2233.6423 | 2257.7884
DEER-SFAM-CZ13-V4-eSA-16-TH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-TH | 13.0004 | 3.3109 | 2847.3293 | 0 | 3.5 | 2847.3293 | 2862.8223
DEER-SFAM-CZ13-V4-eSA-16-TL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSA-16 | CZ13-V4-eSA-16-TL | 13.9448 | 3.2774 | 2570.9961 | 0 | 3.8 | 2570.9961 | 2587.7108
DEER-SFAM-CZ13-V4-eSA-17-CH-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-CH | 14.3698 | 3.0586 | 2541.2592 | 0 | 3.5 | 2541.2592 | 2571.7269
DEER-SFAM-CZ13-V4-eSA-17-CL-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-CL | 14.3473 | 3.0529 | 2520.2717 | 0 | 3.5 | 2520.2717 | 2550.7312
DEER-SFAM-CZ13-V4-eSA-17-CM-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-CM | 14.4365 | 3.0641 | 2550.4781 | 0 | 3.5 | 2550.4781 | 2574.5105
DEER-SFAM-CZ13-V4-eSA-17-LH-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-LH | 13.9363 | 2.8657 | 2321.4738 | 0 | 3.5 | 2321.4738 | 2353.8577
DEER-SFAM-CZ13-V4-eSA-17-LL-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-LL | 13.7202 | 3.0514 | 2417.911 | 0 | 3.5 | 2417.911 | 2435.5215
DEER-SFAM-CZ13-V4-eSA-17-LM-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-LM | 13.6112 | 2.9912 | 2412.8751 | 0 | 3.5 | 2412.8751 | 2428.0853
DEER-SFAM-CZ13-V4-eSA-17-TH-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-TH | 14.4881 | 2.9355 | 2451.3896 | 0 | 3.5 | 2451.3896 | 2476.1522
DEER-SFAM-CZ13-V4-eSA-17-TL-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-TL | 15.2499 | 2.8506 | 2248.6443 | 0 | 3.5 | 2248.6443 | 2287.3399
DEER-SFAM-CZ13-V4-eSA-17-TM-s2 | 17 | CZ13 | V4 | CZ13-V4-eSA-17 | CZ13-V4-eSA-17-TM | 14.9402 | 3.337 | 2638.6705 | 0 | 3.8 | 2638.6705 | 2651.6228
DEER-SFAM-CZ13-V4-eSA-18-LH-s2 | 18 | CZ13 | V4 | CZ13-V4-eSA-18 | CZ13-V4-eSA-18-LH | 14.497 | 2.8292 | 2270.021 | 0 | 3.5 | 2270.021 | 2291.2133
DEER-SFAM-CZ13-V4-eSA-18-LL-s2 | 18 | CZ13 | V4 | CZ13-V4-eSA-18 | CZ13-V4-eSA-18-LL | 14.7637 | 2.8 | 2206.8656 | 0 | 3.5 | 2206.8656 | 2234.5414
DEER-SFAM-CZ13-V4-eSA-18-TH-s2 | 18 | CZ13 | V4 | CZ13-V4-eSA-18 | CZ13-V4-eSA-18-TH | 15.0559 | 2.9018 | 2381.5727 | 0 | 3.8 | 2381.5727 | 2398.3914
DEER-SFAM-CZ13-V4-eSA-18-TL-s2 | 18 | CZ13 | V4 | CZ13-V4-eSA-18 | CZ13-V4-eSA-18-TL | 14.6949 | 3.1759 | 2548.3491 | 0 | 3.5 | 2548.3491 | 2566.8379
DEER-SFAM-CZ13-V4-eSA-18-TM-s2 | 18 | CZ13 | V4 | CZ13-V4-eSA-18 | CZ13-V4-eSA-18-TM | 14.6675 | 2.8505 | 2406.3882 | 0 | 3.5 | 2406.3882 | 2423.5781
DEER-SFAM-CZ13-V4-eSH-10-HH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-HH | 9.1049 | 4.1718 | 3498.8837 | 1368.3498 | 3.8 | 4867.2335 | 3632.1335
DEER-SFAM-CZ13-V4-eSH-10-HL-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-HL | 8.8619 | 4.3519 | 3596.0822 | 1370.7027 | 3.8 | 4966.7849 | 3726.6849
DEER-SFAM-CZ13-V4-eSH-10-HM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-HM | 9.3349 | 4.1569 | 3514.1129 | 1348.8498 | 3.5 | 4862.9627 | 3639.4627
DEER-SFAM-CZ13-V4-eSH-10-LH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-LH | 9.6459 | 3.8366 | 3406.3803 | 1419.9075 | 3.5 | 4826.2878 | 3543.5878
DEER-SFAM-CZ13-V4-eSH-10-LL-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-LL | 9.3213 | 3.974 | 3462.8796 | 1385.5953 | 3.5 | 4848.4749 | 3606.0749
DEER-SFAM-CZ13-V4-eSH-10-LM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-LM | 9.5506 | 3.8206 | 3398.2074 | 1379.0738 | 3.5 | 4777.2812 | 3529.7812
DEER-SFAM-CZ13-V4-eSH-10-MH-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-MH | 9.6495 | 3.999 | 3435.2729 | 1403.107 | 3.5 | 4838.3799 | 3580.7799
DEER-SFAM-CZ13-V4-eSH-10-ML-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-ML | 9.2458 | 4.182 | 3525.616 | 1312.287 | 3.5 | 4837.903 | 3658.903
DEER-SFAM-CZ13-V4-eSH-10-MM-s1 | 10 | CZ13 | V4 | CZ13-V4-eSH-10 | CZ13-V4-eSH-10-MM | 9.4144 | 4.1305 | 3509.4637 | 1370.0676 | 3.5 | 4879.5313 | 3633.2313
DEER-SFAM-CZ13-V4-eSH-13-HH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-HH | 10.7103 | 3.6156 | 2926.3438 | 1318.0546 | 3.8 | 4244.3984 | 3048.0984
DEER-SFAM-CZ13-V4-eSH-13-HL-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-HL | 11.9528 | 3.7684 | 2745.366 | 1132.8153 | 3.8 | 3878.1813 | 2866.4813
DEER-SFAM-CZ13-V4-eSH-13-HM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-HM | 11.0205 | 3.5309 | 2854.5937 | 1180.936 | 3.8 | 4035.5297 | 2964.6297
DEER-SFAM-CZ13-V4-eSH-13-LH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-LH | 12.0196 | 3.1702 | 2695.5656 | 1329.8557 | 3.5 | 4025.4213 | 2877.0213
DEER-SFAM-CZ13-V4-eSH-13-LL-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-LL | 12.4335 | 3.2731 | 2624.4763 | 1184.9691 | 3.5 | 3809.4454 | 2735.9454
DEER-SFAM-CZ13-V4-eSH-13-LM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-LM | 11.4579 | 3.3366 | 2790.1176 | 1031.0647 | 3.5 | 3821.1823 | 2915.9823
DEER-SFAM-CZ13-V4-eSH-13-MH-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-MH | 11.8307 | 3.3602 | 2709.5677 | 1335.9368 | 3.8 | 4045.5045 | 2831.0045
DEER-SFAM-CZ13-V4-eSH-13-ML-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-ML | 11.3001 | 3.5924 | 2852.3515 | 1196.2247 | 3.5 | 4048.5762 | 2976.7762
DEER-SFAM-CZ13-V4-eSH-13-MM-s1 | 13 | CZ13 | V4 | CZ13-V4-eSH-13 | CZ13-V4-eSH-13-MM | 11.7737 | 3.4836 | 2773.7767 | 1230.7018 | 3.5 | 4004.4785 | 2870.9785
DEER-SFAM-CZ13-V4-eSH-14-HH-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-HH | 11.3791 | 3.4397 | 2754.0931 | 1206.4522 | 3.8 | 3960.5453 | 2846.8453
DEER-SFAM-CZ13-V4-eSH-14-HL-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-HL | 11.83 | 3.3563 | 2645.1739 | 1171.8699 | 3.8 | 3817.0438 | 2756.2438
DEER-SFAM-CZ13-V4-eSH-14-HM-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-HM | 11.7652 | 3.2445 | 2648.0016 | 1178.6776 | 3.8 | 3826.6792 | 2727.4792
DEER-SFAM-CZ13-V4-eSH-14-MH-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-MH | 12.821 | 2.9907 | 2514.3169 | 1223.2991 | 3.5 | 3737.616 | 2635.216
DEER-SFAM-CZ13-V4-eSH-14-ML-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-ML | 12.716 | 3.3603 | 2529.2322 | 1244.7245 | 3.8 | 3773.9567 | 2679.5567
DEER-SFAM-CZ13-V4-eSH-14-MM-s1 | 14 | CZ13 | V4 | CZ13-V4-eSH-14 | CZ13-V4-eSH-14-MM | 12.6335 | 3.1546 | 2530.7284 | 1134.0721 | 3.5 | 3664.8005 | 2634.9005
DEER-SFAM-CZ13-V4-eSH-15-HH-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-HH | 12.6288 | 3.0087 | 2451.6385 | 1324.9981 | 3.8 | 3776.6366 | 2537.7366
DEER-SFAM-CZ13-V4-eSH-15-HL-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-HL | 12.879 | 3.1607 | 2468.7768 | 1023.1295 | 3.8 | 3491.9063 | 2553.9063
DEER-SFAM-CZ13-V4-eSH-15-HM-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-HM | 13.2402 | 3.0704 | 2397.5151 | 1072.6983 | 3.8 | 3470.2134 | 2482.0134
DEER-SFAM-CZ13-V4-eSH-15-MH-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-MH | 13.245 | 3.0762 | 2449.4847 | 1167.0679 | 3.5 | 3616.5526 | 2530.9526
DEER-SFAM-CZ13-V4-eSH-15-ML-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-ML | 13.5897 | 3.1861 | 2368.0845 | 1111.0308 | 3.8 | 3479.1153 | 2453.0153
DEER-SFAM-CZ13-V4-eSH-15-MM-s1 | 15 | CZ13 | V4 | CZ13-V4-eSH-15 | CZ13-V4-eSH-15-MM | 13.421 | 3.0582 | 2382.9057 | 1202.4758 | 3.8 | 3585.3815 | 2473.6815
DEER-SFAM-CZ13-V4-eSH-16-CH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-CH | 13.7559 | 2.9834 | 2630.4821 | 1200.866 | 3.5 | 3831.3481 | 2704.7481
DEER-SFAM-CZ13-V4-eSH-16-CL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-CL | 13.8901 | 3.2373 | 2712.6085 | 1120.1609 | 3.5 | 3832.7694 | 2789.9694
DEER-SFAM-CZ13-V4-eSH-16-LH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-LH | 13.1156 | 2.9538 | 2456.3845 | 1252.7413 | 3.5 | 3709.1258 | 2541.8258
DEER-SFAM-CZ13-V4-eSH-16-LL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-LL | 13.0578 | 3.1435 | 2503.1325 | 1139.3028 | 3.5 | 3642.4353 | 2571.8353
DEER-SFAM-CZ13-V4-eSH-16-LM-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-LM | 12.8227 | 3.0618 | 2520.2831 | 1246.2883 | 3.5 | 3766.5714 | 2615.7714
DEER-SFAM-CZ13-V4-eSH-16-TH-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-TH | 13.7766 | 3.3254 | 2580.8875 | 1491.2731 | 3.8 | 4072.1606 | 2648.8606
DEER-SFAM-CZ13-V4-eSH-16-TL-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-TL | 13.2245 | 3.4256 | 2830.771 | 1469.1377 | 3.5 | 4299.9087 | 2895.0087
DEER-SFAM-CZ13-V4-eSH-16-TM-s2 | 16 | CZ13 | V4 | CZ13-V4-eSH-16 | CZ13-V4-eSH-16-TM | 13.3678 | 3.3631 | 2801.0422 | 1493.5489 | 3.5 | 4294.5911 | 2867.0911
DEER-SFAM-CZ13-V4-eSH-17-CM-s2 | 17 | CZ13 | V4 | CZ13-V4-eSH-17 | CZ13-V4-eSH-17-CM | 14.6344 | 3.0853 | 2570.8604 | 1164.15 | 3.5 | 3735.0104 | 2651.9104
DEER-SFAM-CZ13-V4-eSH-17-LM-s2 | 17 | CZ13 | V4 | CZ13-V4-eSH-17 | CZ13-V4-eSH-17-LM | 13.5623 | 3.0988 | 2508.8314 | 1109.6942 | 3.5 | 3618.5256 | 2547.4256
DEER-SFAM-CZ13-V4-eSH-17-TH-s2 | 17 | CZ13 | V4 | CZ13-V4-eSH-17 | CZ13-V4-eSH-17-TH | 14.5005 | 3.1476 | 2448.5602 | 1490.1066 | 3.8 | 3938.6668 | 2521.4668
DEER-SFAM-CZ13-V4-eSH-17-TL-s2 | 17 | CZ13 | V4 | CZ13-V4-eSH-17 | CZ13-V4-eSH-17-TL | 14.4773 | 3.214 | 2458.2968 | 1470.6977 | 3.8 | 3928.9945 | 2530.2945
DEER-SFAM-CZ13-V4-eSH-18-LH-s2 | 18 | CZ13 | V4 | CZ13-V4-eSH-18 | CZ13-V4-eSH-18-LH | 14.4038 | 2.8795 | 2272.7519 | 1245.3151 | 3.5 | 3518.067 | 2334.567
DEER-SFAM-CZ13-V4-eSH-18-LL-s2 | 18 | CZ13 | V4 | CZ13-V4-eSH-18 | CZ13-V4-eSH-18-LL | 13.8254 | 2.9591 | 2348.4233 | 1131.7264 | 3.5 | 3480.1497 | 2407.5497
DEER-SFAM-CZ13-V4-eSH-18-LM-s2 | 18 | CZ13 | V4 | CZ13-V4-eSH-18 | CZ13-V4-eSH-18-LM | 14.4293 | 2.8981 | 2282.3681 | 1302.548 | 3.5 | 3584.9161 | 2352.7161
DEER-SFAM-CZ13-V4-eSH-18-TM-s2 | 18 | CZ13 | V4 | CZ13-V4-eSH-18 | CZ13-V4-eSH-18-TM | 15.3024 | 3.01 | 2363.3023 | 1489.8884 | 3.5 | 3853.1907 | 2478.9907
DEER-SFAM-CZ14-V1-eSA-10-HH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-HH | 8.7266 | 5.0762 | 4866.475 | 0 | 4.0811 | 4866.475 | 5068.569
DEER-SFAM-CZ14-V1-eSA-10-HL-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-HL | 8.54 | 5.8371 | 5005.6654 | 0 | 4.0811 | 5005.6654 | 5207.8146
DEER-SFAM-CZ14-V1-eSA-10-HM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-HM | 8.5675 | 5.5445 | 4886.845 | 0 | 4.0811 | 4886.845 | 5088.9876
DEER-SFAM-CZ14-V1-eSA-10-LH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-LH | 9.2446 | 4.8867 | 4836.8609 | 0 | 4.0811 | 4836.8609 | 5039.0431
DEER-SFAM-CZ14-V1-eSA-10-LL-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-LL | 9.0832 | 5.199 | 4777.6806 | 0 | 4.0811 | 4777.6806 | 4979.8428
DEER-SFAM-CZ14-V1-eSA-10-LM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-LM | 9.1265 | 4.9137 | 4828.3666 | 0 | 4.0811 | 4828.3666 | 5030.5427
DEER-SFAM-CZ14-V1-eSA-10-MH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-MH | 9.102 | 4.7566 | 4825.602 | 0 | 4.0811 | 4825.602 | 5027.7775
DEER-SFAM-CZ14-V1-eSA-10-ML-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-ML | 8.689 | 5.2801 | 4914.9267 | 0 | 4.0811 | 4914.9267 | 5117.0778
DEER-SFAM-CZ14-V1-eSA-10-MM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSA-10 | CZ14-V1-eSA-10-MM | 8.9488 | 4.2006 | 4824.8194 | 0 | 3.6217 | 4824.8194 | 5026.9175
DEER-SFAM-CZ14-V1-eSA-13-HH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-HH | 11.7111 | 4.7502 | 3797.2805 | 0 | 4.5406 | 3797.2805 | 3979.4843
DEER-SFAM-CZ14-V1-eSA-13-HL-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-HL | 10.7182 | 4.802 | 4005.9128 | 0 | 4.0811 | 4005.9128 | 4165.3892
DEER-SFAM-CZ14-V1-eSA-13-HM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-HM | 11.4341 | 4.833 | 3735.1004 | 0 | 4.5406 | 3735.1004 | 3917.3068
DEER-SFAM-CZ14-V1-eSA-13-LH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-LH | 11.483 | 4.4111 | 3728.2761 | 0 | 4.5406 | 3728.2761 | 3930.4427
DEER-SFAM-CZ14-V1-eSA-13-LL-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-LL | 11.0435 | 4.3296 | 3885.1354 | 0 | 4.0811 | 3885.1354 | 4087.1557
DEER-SFAM-CZ14-V1-eSA-13-LM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-LM | 10.7021 | 4.1385 | 3942.0644 | 0 | 4.0811 | 3942.0644 | 4144.1809
DEER-SFAM-CZ14-V1-eSA-13-MH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-MH | 11.4864 | 4.6533 | 3737.8355 | 0 | 4.5406 | 3737.8355 | 3939.9934
DEER-SFAM-CZ14-V1-eSA-13-ML-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-ML | 10.4018 | 4.523 | 3919.6642 | 0 | 4.0811 | 3919.6642 | 4121.2239
DEER-SFAM-CZ14-V1-eSA-13-MM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSA-13 | CZ14-V1-eSA-13-MM | 11.7853 | 4.6454 | 3591.2618 | 0 | 4.5406 | 3591.2618 | 3793.4183
DEER-SFAM-CZ14-V1-eSA-14-HH-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-HH | 10.7101 | 4.3173 | 3809.0311 | 0 | 4.0811 | 3809.0311 | 3978.461
DEER-SFAM-CZ14-V1-eSA-14-HL-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-HL | 11.8121 | 4.614 | 3569.9335 | 0 | 4.5406 | 3569.9335 | 3694.5152
DEER-SFAM-CZ14-V1-eSA-14-HM-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-HM | 11.351 | 4.3945 | 3836.9882 | 0 | 4.0811 | 3836.9882 | 4028.0664
DEER-SFAM-CZ14-V1-eSA-14-MH-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-MH | 11.6363 | 3.8514 | 3717.353 | 0 | 4.0811 | 3717.353 | 3850.2069
DEER-SFAM-CZ14-V1-eSA-14-ML-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-ML | 11.4595 | 4.2791 | 3721.1242 | 0 | 4.0811 | 3721.1242 | 3933.2463
DEER-SFAM-CZ14-V1-eSA-14-MM-s1 | 14 | CZ14 | V1 | CZ14-V1-eSA-14 | CZ14-V1-eSA-14-MM | 11.3762 | 3.8563 | 3700.6993 | 0 | 4.0811 | 3700.6993 | 3846.3178
DEER-SFAM-CZ14-V1-eSA-15-HH-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-HH | 13.123 | 4.258 | 3274.8203 | 0 | 4.5406 | 3274.8203 | 3416.0223
DEER-SFAM-CZ14-V1-eSA-15-HL-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-HL | 12.8818 | 4.3658 | 3250.5409 | 0 | 4.5406 | 3250.5409 | 3426.643
DEER-SFAM-CZ14-V1-eSA-15-HM-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-HM | 13.3047 | 4.1191 | 3234.6016 | 0 | 4.5406 | 3234.6016 | 3376.3588
DEER-SFAM-CZ14-V1-eSA-15-MH-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-MH | 11.7995 | 4.1219 | 3588.7052 | 0 | 4.0811 | 3588.7052 | 3693.9035
DEER-SFAM-CZ14-V1-eSA-15-ML-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-ML | 12.6884 | 3.9549 | 3405.2676 | 0 | 4.0811 | 3405.2676 | 3546.9172
DEER-SFAM-CZ14-V1-eSA-15-MM-s1 | 15 | CZ14 | V1 | CZ14-V1-eSA-15 | CZ14-V1-eSA-15-MM | 12.4092 | 4.038 | 3445.4472 | 0 | 4.0811 | 3445.4472 | 3574.459
DEER-SFAM-CZ14-V1-eSA-16-CH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-CH | 13.6275 | 4.4935 | 3783.2079 | 0 | 4.5406 | 3783.2079 | 3862.0684
DEER-SFAM-CZ14-V1-eSA-16-CL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-CL | 13.9492 | 4.6273 | 3511.9598 | 0 | 4.5406 | 3511.9598 | 3612.4958
DEER-SFAM-CZ14-V1-eSA-16-CM-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-CM | 13.6954 | 4.5816 | 3637.7578 | 0 | 4.5406 | 3637.7578 | 3744.0609
DEER-SFAM-CZ14-V1-eSA-16-LH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-LH | 13.8073 | 3.8111 | 3170.6888 | 0 | 4.0811 | 3170.6888 | 3307.5985
DEER-SFAM-CZ14-V1-eSA-16-LL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-LL | 12.9401 | 4.1027 | 3425.3836 | 0 | 4.0811 | 3425.3836 | 3515.9942
DEER-SFAM-CZ14-V1-eSA-16-LM-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-LM | 12.8417 | 3.9558 | 3444.5093 | 0 | 4.0811 | 3444.5093 | 3526.6741
DEER-SFAM-CZ14-V1-eSA-16-NM-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-NM | 14.1381 | 3.7972 | 3127.0829 | 0 | 4.0811 | 3127.0829 | 3207.5375
DEER-SFAM-CZ14-V1-eSA-16-TH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-TH | 12.5839 | 4.6328 | 3892.5735 | 0 | 4.0811 | 3892.5735 | 3943.0189
DEER-SFAM-CZ14-V1-eSA-16-TL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSA-16 | CZ14-V1-eSA-16-TL | 14.0515 | 4.8032 | 3451.8121 | 0 | 4.5406 | 3451.8121 | 3506.8333
DEER-SFAM-CZ14-V1-eSA-17-CH-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-CH | 14.3352 | 4.3559 | 3510.7449 | 0 | 4.5406 | 3510.7449 | 3611.2149
DEER-SFAM-CZ14-V1-eSA-17-CL-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-CL | 14.2238 | 4.3796 | 3477.1736 | 0 | 4.5406 | 3477.1736 | 3577.6228
DEER-SFAM-CZ14-V1-eSA-17-CM-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-CM | 14.3836 | 4.3644 | 3526.3365 | 0 | 4.5406 | 3526.3365 | 3604.9567
DEER-SFAM-CZ14-V1-eSA-17-LH-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-LH | 13.6996 | 3.6925 | 3199.9053 | 0 | 4.0811 | 3199.9053 | 3307.4682
DEER-SFAM-CZ14-V1-eSA-17-LL-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-LL | 13.3801 | 3.9439 | 3349.6496 | 0 | 4.0811 | 3349.6496 | 3408.7486
DEER-SFAM-CZ14-V1-eSA-17-LM-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-LM | 13.2279 | 3.9681 | 3343.878 | 0 | 4.0811 | 3343.878 | 3394.8258
DEER-SFAM-CZ14-V1-eSA-17-TH-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-TH | 14.4783 | 3.9216 | 3331.8385 | 0 | 4.0811 | 3331.8385 | 3413.0623
DEER-SFAM-CZ14-V1-eSA-17-TL-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-TL | 15.4309 | 4.4525 | 2999.0527 | 0 | 4.5406 | 2999.0527 | 3126.1586
DEER-SFAM-CZ14-V1-eSA-17-TM-s2 | 17 | CZ14 | V1 | CZ14-V1-eSA-17 | CZ14-V1-eSA-17-TM | 15.3597 | 4.3975 | 3536.253 | 0 | 4.5406 | 3536.253 | 3578.6878
DEER-SFAM-CZ14-V1-eSA-18-LH-s2 | 18 | CZ14 | V1 | CZ14-V1-eSA-18 | CZ14-V1-eSA-18-LH | 14.2907 | 3.6854 | 3094.1071 | 0 | 4.0811 | 3094.1071 | 3164.9636
DEER-SFAM-CZ14-V1-eSA-18-LL-s2 | 18 | CZ14 | V1 | CZ14-V1-eSA-18 | CZ14-V1-eSA-18-LL | 14.5135 | 3.6763 | 3047.3482 | 0 | 4.0811 | 3047.3482 | 3139.7202
DEER-SFAM-CZ14-V1-eSA-18-TH-s2 | 18 | CZ14 | V1 | CZ14-V1-eSA-18 | CZ14-V1-eSA-18-TH | 15.3128 | 4.1681 | 3224.5025 | 0 | 4.5406 | 3224.5025 | 3279.9595
DEER-SFAM-CZ14-V1-eSA-18-TL-s2 | 18 | CZ14 | V1 | CZ14-V1-eSA-18 | CZ14-V1-eSA-18-TL | 14.6273 | 4.5565 | 3531.1618 | 0 | 4.5406 | 3531.1618 | 3591.2798
DEER-SFAM-CZ14-V1-eSA-18-TM-s2 | 18 | CZ14 | V1 | CZ14-V1-eSA-18 | CZ14-V1-eSA-18-TM | 14.2994 | 3.897 | 3347.3695 | 0 | 4.0811 | 3347.3695 | 3403.8552
DEER-SFAM-CZ14-V1-eSH-10-HH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-HH | 9.0016 | 5.5841 | 4659.6936 | 5536.73 | 4.5406 | 10196.4236 | 5221.9497
DEER-SFAM-CZ14-V1-eSH-10-HL-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-HL | 8.7159 | 5.8858 | 4816.5899 | 5417.1076 | 4.5406 | 10233.6975 | 5355.2367
DEER-SFAM-CZ14-V1-eSH-10-HM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-HM | 9.0219 | 5.3374 | 4811.2484 | 5391.1854 | 4.0811 | 10202.4339 | 5331.778
DEER-SFAM-CZ14-V1-eSH-10-LH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-LH | 9.1778 | 4.8219 | 4758.6575 | 5974.7761 | 4.0811 | 10733.4336 | 5325.355
DEER-SFAM-CZ14-V1-eSH-10-LL-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-LL | 9.0081 | 5.5883 | 4741.3009 | 6009.8592 | 4.5406 | 10751.1601 | 5348.9482
DEER-SFAM-CZ14-V1-eSH-10-LM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-LM | 9.2381 | 5.3397 | 4627.3179 | 5735.7413 | 4.5406 | 10363.0593 | 5181.1626
DEER-SFAM-CZ14-V1-eSH-10-MH-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-MH | 9.2197 | 5.0432 | 4808.6669 | 6049.3845 | 4.0811 | 10858.0514 | 5414.3378
DEER-SFAM-CZ14-V1-eSH-10-ML-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-ML | 8.8627 | 5.9371 | 4858.4931 | 5763.8288 | 4.5406 | 10622.3219 | 5433.1413
DEER-SFAM-CZ14-V1-eSH-10-MM-s1 | 10 | CZ14 | V1 | CZ14-V1-eSH-10 | CZ14-V1-eSH-10-MM | 9.0401 | 5.1509 | 4873.4514 | 5650.2716 | 4.0811 | 10523.723 | 5384.051
DEER-SFAM-CZ14-V1-eSH-13-HH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-HH | 10.698 | 4.9977 | 3951.6259 | 5580.8012 | 4.5406 | 9532.4271 | 4457.2294
DEER-SFAM-CZ14-V1-eSH-13-HL-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-HL | 11.6391 | 4.9646 | 3747.6869 | 4898.3932 | 4.5406 | 8646.0802 | 4258.5289
DEER-SFAM-CZ14-V1-eSH-13-HM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-HM | 10.9988 | 4.8498 | 3841.9301 | 4978.3888 | 4.5406 | 8820.3189 | 4304.3478
DEER-SFAM-CZ14-V1-eSH-13-LH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-LH | 11.2448 | 4.0372 | 3833.323 | 6697.7148 | 4.0811 | 10531.0379 | 4565.1988
DEER-SFAM-CZ14-V1-eSH-13-LL-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-LL | 11.9794 | 4.5108 | 3573.3882 | 5252.9521 | 4.5406 | 8826.3403 | 4041.404
DEER-SFAM-CZ14-V1-eSH-13-LM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-LM | 10.4021 | 4.2485 | 4023.8937 | 4385.0976 | 4.0811 | 8408.9913 | 4543.3141
DEER-SFAM-CZ14-V1-eSH-13-MH-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-MH | 11.6305 | 4.5632 | 3632.1442 | 5696.8676 | 4.5406 | 9329.0118 | 4132.3678
DEER-SFAM-CZ14-V1-eSH-13-ML-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-ML | 10.397 | 4.5718 | 4144.0595 | 5514.2486 | 4.0811 | 9658.3081 | 4655.8419
DEER-SFAM-CZ14-V1-eSH-13-MM-s1 | 13 | CZ14 | V1 | CZ14-V1-eSH-13 | CZ14-V1-eSH-13-MM | 11.3111 | 4.5597 | 3828.5136 | 5179.1726 | 4.0811 | 9007.6861 | 4222.0576
DEER-SFAM-CZ14-V1-eSH-14-HH-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-HH | 11.3811 | 4.7984 | 3726.8446 | 5159.4128 | 4.5406 | 8886.2575 | 4113.1448
DEER-SFAM-CZ14-V1-eSH-14-HL-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-HL | 11.8819 | 4.6455 | 3575.1087 | 5304.5598 | 4.5406 | 8879.6685 | 4039.2963
DEER-SFAM-CZ14-V1-eSH-14-HM-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-HM | 11.9646 | 4.4758 | 3539.6568 | 5302.0879 | 4.5406 | 8841.7447 | 3873.2253
DEER-SFAM-CZ14-V1-eSH-14-MH-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-MH | 12.0434 | 3.853 | 3558.494 | 6208.1332 | 4.0811 | 9766.6271 | 4049.7221
DEER-SFAM-CZ14-V1-eSH-14-ML-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-ML | 12.0277 | 4.5232 | 3553.3495 | 6494.7472 | 4.5406 | 10048.0967 | 4189.7999
DEER-SFAM-CZ14-V1-eSH-14-MM-s1 | 14 | CZ14 | V1 | CZ14-V1-eSH-14 | CZ14-V1-eSH-14-MM | 11.7924 | 4.1283 | 3589.9722 | 5424.4861 | 4.0811 | 9014.4583 | 4017.3165
DEER-SFAM-CZ14-V1-eSH-15-HH-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-HH | 13.0366 | 4.1303 | 3277.2643 | 6457.209 | 4.5406 | 9734.4732 | 3627.9385
DEER-SFAM-CZ14-V1-eSH-15-HL-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-HL | 13.016 | 4.2833 | 3327.0359 | 4396.7897 | 4.5406 | 7723.8256 | 3682.1565
DEER-SFAM-CZ14-V1-eSH-15-HM-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-HM | 13.0267 | 4.2148 | 3213.084 | 4613.8275 | 4.5406 | 7826.9116 | 3564.9244
DEER-SFAM-CZ14-V1-eSH-15-MH-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-MH | 12.3667 | 4.0457 | 3497.2584 | 5936.7667 | 4.0811 | 9434.0251 | 3832.5956
DEER-SFAM-CZ14-V1-eSH-15-ML-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-ML | 12.8829 | 4.3069 | 3319.2737 | 5628.0158 | 4.5406 | 8947.2895 | 3681.471
DEER-SFAM-CZ14-V1-eSH-15-MM-s1 | 15 | CZ14 | V1 | CZ14-V1-eSH-15 | CZ14-V1-eSH-15-MM | 13.2131 | 4.1221 | 3190.058 | 5728.4716 | 4.5406 | 8918.5295 | 3568.2063
DEER-SFAM-CZ14-V1-eSH-16-CH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-CH | 13.8085 | 4.4968 | 3600.0676 | 6318.916 | 4.5406 | 9918.9836 | 4035.875
DEER-SFAM-CZ14-V1-eSH-16-CL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-CL | 13.9726 | 4.5408 | 3705.2688 | 5871.8745 | 4.5406 | 9577.1433 | 4155.2272
DEER-SFAM-CZ14-V1-eSH-16-LH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-LH | 13.2952 | 3.8726 | 3288.0099 | 6557.7468 | 4.0811 | 9845.7567 | 3708.7199
DEER-SFAM-CZ14-V1-eSH-16-LL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-LL | 12.7841 | 4.0166 | 3474.0883 | 6235.7804 | 4.0811 | 9709.8687 | 3837.2678
DEER-SFAM-CZ14-V1-eSH-16-LM-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-LM | 12.6593 | 3.9429 | 3467.5865 | 6731.386 | 4.0811 | 10198.9725 | 3943.2998
DEER-SFAM-CZ14-V1-eSH-16-TH-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-TH | 14.1776 | 4.7632 | 3494.4131 | 8051.5131 | 4.5406 | 11545.9262 | 4020.8411
DEER-SFAM-CZ14-V1-eSH-16-TL-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-TL | 12.778 | 4.5368 | 3882.7553 | 7718.0914 | 4.0811 | 11600.8467 | 4353.2587
DEER-SFAM-CZ14-V1-eSH-16-TM-s2 | 16 | CZ14 | V1 | CZ14-V1-eSH-16 | CZ14-V1-eSH-16-TM | 13.0444 | 4.4513 | 3811.3276 | 7764.0709 | 4.0811 | 11575.3985 | 4289.2964
DEER-SFAM-CZ14-V1-eSH-17-CM-s2 | 17 | CZ14 | V1 | CZ14-V1-eSH-17 | CZ14-V1-eSH-17-CM | 14.7337 | 4.3325 | 3509.4595 | 5943.4337 | 4.5406 | 9452.8932 | 3966.8065
DEER-SFAM-CZ14-V1-eSH-17-LM-s2 | 17 | CZ14 | V1 | CZ14-V1-eSH-17 | CZ14-V1-eSH-17-LM | 13.5785 | 3.8835 | 3323.5471 | 5984.2812 | 4.0811 | 9307.8283 | 3526.2406
DEER-SFAM-CZ14-V1-eSH-17-TH-s2 | 17 | CZ14 | V1 | CZ14-V1-eSH-17 | CZ14-V1-eSH-17-TH | 14.6509 | 4.439 | 3357.7148 | 8035.8197 | 4.5406 | 11393.5344 | 3905.5021
DEER-SFAM-CZ14-V1-eSH-17-TL-s2 | 17 | CZ14 | V1 | CZ14-V1-eSH-17 | CZ14-V1-eSH-17-TL | 14.5999 | 4.536 | 3394.436 | 8058.7287 | 4.5406 | 11453.1647 | 3941.2013
DEER-SFAM-CZ14-V1-eSH-18-LH-s2 | 18 | CZ14 | V1 | CZ14-V1-eSH-18 | CZ14-V1-eSH-18-LH | 13.7835 | 3.7289 | 3251.6505 | 7166.6564 | 4.0811 | 10418.3069 | 3618.6191
DEER-SFAM-CZ14-V1-eSH-18-LL-s2 | 18 | CZ14 | V1 | CZ14-V1-eSH-18 | CZ14-V1-eSH-18-LL | 13.0844 | 3.8742 | 3378.6272 | 6388.6537 | 4.0811 | 9767.2809 | 3691.0696
DEER-SFAM-CZ14-V1-eSH-18-LM-s2 | 18 | CZ14 | V1 | CZ14-V1-eSH-18 | CZ14-V1-eSH-18-LM | 14.1005 | 3.7787 | 3182.7442 | 7599.5839 | 4.0811 | 10782.3281 | 3603.9214
DEER-SFAM-CZ14-V1-eSH-18-TM-s2 | 18 | CZ14 | V1 | CZ14-V1-eSH-18 | CZ14-V1-eSH-18-TM | 14.4422 | 3.8464 | 3456.7975 | 8192.0486 | 4.0811 | 11648.8461 | 4186.4242
DEER-SFAM-CZ14-V2-eSA-10-HH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-HH | 8.6351 | 4.0055 | 3621.3719 | 0 | 3.2375 | 3621.3719 | 3750.9089
DEER-SFAM-CZ14-V2-eSA-10-HL-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-HL | 8.3868 | 5.0218 | 3744.5943 | 0 | 3.6782 | 3744.5943 | 3874.2981
DEER-SFAM-CZ14-V2-eSA-10-HM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-HM | 8.3787 | 4.7679 | 3662.1302 | 0 | 3.6782 | 3662.1302 | 3791.8218
DEER-SFAM-CZ14-V2-eSA-10-LH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-LH | 9.0966 | 3.8809 | 3595.4286 | 0 | 3.2375 | 3595.4286 | 3725.1232
DEER-SFAM-CZ14-V2-eSA-10-LL-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-LL | 8.9623 | 4.4921 | 3567.0259 | 0 | 3.6782 | 3567.0259 | 3696.7441
DEER-SFAM-CZ14-V2-eSA-10-LM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-LM | 9.0015 | 3.8981 | 3585.7385 | 0 | 3.2375 | 3585.7385 | 3715.4349
DEER-SFAM-CZ14-V2-eSA-10-MH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-MH | 8.9458 | 3.7796 | 3599.6048 | 0 | 3.2375 | 3599.6048 | 3729.272
DEER-SFAM-CZ14-V2-eSA-10-ML-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-ML | 8.6261 | 4.1866 | 3637.0093 | 0 | 3.2375 | 3637.0093 | 3766.6257
DEER-SFAM-CZ14-V2-eSA-10-MM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSA-10 | CZ14-V2-eSA-10-MM | 8.7513 | 3.6968 | 3677.528 | 0 | 3.2375 | 3677.528 | 3807.1519
DEER-SFAM-CZ14-V2-eSA-13-HH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-HH | 11.5587 | 3.8335 | 2837.2017 | 0 | 3.6782 | 2837.2017 | 2954.113
DEER-SFAM-CZ14-V2-eSA-13-HL-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-HL | 10.5277 | 4.1302 | 2993.1116 | 0 | 3.6782 | 2993.1116 | 3095.4363
DEER-SFAM-CZ14-V2-eSA-13-HM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-HM | 11.3623 | 3.8492 | 2768.6569 | 0 | 3.6782 | 2768.6569 | 2885.5427
DEER-SFAM-CZ14-V2-eSA-13-LH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-LH | 11.3261 | 3.5267 | 2776.891 | 0 | 3.6782 | 2776.891 | 2906.6143
DEER-SFAM-CZ14-V2-eSA-13-LL-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-LL | 10.9598 | 3.432 | 2883.4163 | 0 | 3.2375 | 2883.4163 | 3012.8684
DEER-SFAM-CZ14-V2-eSA-13-LM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-LM | 10.5636 | 3.2907 | 2938.3959 | 0 | 3.2375 | 2938.3959 | 3067.9578
DEER-SFAM-CZ14-V2-eSA-13-MH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-MH | 11.3467 | 3.7032 | 2779.5286 | 0 | 3.6782 | 2779.5286 | 2909.2199
DEER-SFAM-CZ14-V2-eSA-13-ML-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-ML | 10.2911 | 3.5819 | 2898.5514 | 0 | 3.2375 | 2898.5514 | 3027.766
DEER-SFAM-CZ14-V2-eSA-13-MM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSA-13 | CZ14-V2-eSA-13-MM | 11.7249 | 3.6827 | 2659.5777 | 0 | 3.6782 | 2659.5777 | 2789.2563
DEER-SFAM-CZ14-V2-eSA-14-HH-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-HH | 10.5703 | 3.4222 | 2822.2672 | 0 | 3.2375 | 2822.2672 | 2930.8922
DEER-SFAM-CZ14-V2-eSA-14-HL-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-HL | 11.7339 | 3.6581 | 2640.3584 | 0 | 3.6782 | 2640.3584 | 2720.2855
DEER-SFAM-CZ14-V2-eSA-14-HM-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-HM | 11.0871 | 3.7962 | 2866.8479 | 0 | 3.6782 | 2866.8479 | 2989.4602
DEER-SFAM-CZ14-V2-eSA-14-MH-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-MH | 11.4661 | 3.0654 | 2775.5726 | 0 | 3.2375 | 2775.5726 | 2860.7371
DEER-SFAM-CZ14-V2-eSA-14-ML-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-ML | 11.2197 | 3.7092 | 2788.1731 | 0 | 3.6782 | 2788.1731 | 2924.2653
DEER-SFAM-CZ14-V2-eSA-14-MM-s1 | 14 | CZ14 | V2 | CZ14-V2-eSA-14 | CZ14-V2-eSA-14-MM | 11.2062 | 3.0577 | 2760.9494 | 0 | 3.2375 | 2760.9494 | 2854.3102
DEER-SFAM-CZ14-V2-eSA-15-HH-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-HH | 12.9514 | 3.4118 | 2441.8824 | 0 | 3.6782 | 2441.8824 | 2532.488
DEER-SFAM-CZ14-V2-eSA-15-HL-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-HL | 12.7608 | 3.5037 | 2412.2064 | 0 | 3.6782 | 2412.2064 | 2525.1577
DEER-SFAM-CZ14-V2-eSA-15-HM-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-HM | 13.184 | 3.2876 | 2404.0794 | 0 | 3.6782 | 2404.0794 | 2495.0265
DEER-SFAM-CZ14-V2-eSA-15-MH-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-MH | 11.4397 | 3.5792 | 2709.0448 | 0 | 3.6782 | 2709.0448 | 2776.5537
DEER-SFAM-CZ14-V2-eSA-15-ML-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-ML | 12.5993 | 3.1276 | 2522.7741 | 0 | 3.2375 | 2522.7741 | 2613.5427
DEER-SFAM-CZ14-V2-eSA-15-MM-s1 | 15 | CZ14 | V2 | CZ14-V2-eSA-15 | CZ14-V2-eSA-15-MM | 12.1223 | 3.4625 | 2579.6273 | 0 | 3.6782 | 2579.6273 | 2662.4125
DEER-SFAM-CZ14-V2-eSA-16-CH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-CH | 13.644 | 3.584 | 2753.8305 | 0 | 3.6782 | 2753.8305 | 2805.6667
DEER-SFAM-CZ14-V2-eSA-16-CL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-CL | 14.0466 | 3.5905 | 2543.2221 | 0 | 3.6782 | 2543.2221 | 2608.9536
DEER-SFAM-CZ14-V2-eSA-16-CM-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-CM | 13.7516 | 3.5674 | 2644.2687 | 0 | 3.6782 | 2644.2687 | 2713.7399
DEER-SFAM-CZ14-V2-eSA-16-LH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-LH | 13.7324 | 3.0025 | 2321.486 | 0 | 3.2375 | 2321.486 | 2410.388
DEER-SFAM-CZ14-V2-eSA-16-LL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-LL | 12.9359 | 3.2361 | 2496.2897 | 0 | 3.2375 | 2496.2897 | 2555.09
DEER-SFAM-CZ14-V2-eSA-16-LM-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-LM | 12.7969 | 3.1227 | 2518.8264 | 0 | 3.2375 | 2518.8264 | 2572.1496
DEER-SFAM-CZ14-V2-eSA-16-NM-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-NM | 14.2845 | 3.0059 | 2257.6905 | 0 | 3.2375 | 2257.6905 | 2309.9859
DEER-SFAM-CZ14-V2-eSA-16-TH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-TH | 12.5816 | 4.0946 | 2914.2244 | 0 | 3.6782 | 2914.2244 | 2947.6001
DEER-SFAM-CZ14-V2-eSA-16-TL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSA-16 | CZ14-V2-eSA-16-TL | 14.1691 | 3.7498 | 2487.6398 | 0 | 3.6782 | 2487.6398 | 2523.8663
DEER-SFAM-CZ14-V2-eSA-17-CH-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-CH | 14.3733 | 3.4615 | 2553.6618 | 0 | 3.6782 | 2553.6618 | 2619.363
DEER-SFAM-CZ14-V2-eSA-17-CL-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-CL | 14.3251 | 3.4322 | 2521.8704 | 0 | 3.6782 | 2521.8704 | 2587.5564
DEER-SFAM-CZ14-V2-eSA-17-CM-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-CM | 14.4699 | 3.4332 | 2561.6166 | 0 | 3.6782 | 2561.6166 | 2613.295
DEER-SFAM-CZ14-V2-eSA-17-LH-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-LH | 13.6545 | 2.9053 | 2338.1848 | 0 | 3.2375 | 2338.1848 | 2408.0162
DEER-SFAM-CZ14-V2-eSA-17-LL-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-LL | 13.3808 | 3.1117 | 2434.4555 | 0 | 3.2375 | 2434.4555 | 2472.7252
DEER-SFAM-CZ14-V2-eSA-17-LM-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-LM | 13.2253 | 3.1362 | 2434.8581 | 0 | 3.2375 | 2434.8581 | 2467.8855
DEER-SFAM-CZ14-V2-eSA-17-TH-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-TH | 14.2662 | 3.463 | 2508.0846 | 0 | 3.6782 | 2508.0846 | 2561.5733
DEER-SFAM-CZ14-V2-eSA-17-TL-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-TL | 15.6523 | 3.4623 | 2154.8177 | 0 | 3.6782 | 2154.8177 | 2238.2651
DEER-SFAM-CZ14-V2-eSA-17-TM-s2 | 17 | CZ14 | V2 | CZ14-V2-eSA-17 | CZ14-V2-eSA-17-TM | 15.4115 | 3.5047 | 2562.7748 | 0 | 3.6782 | 2562.7748 | 2590.8183
DEER-SFAM-CZ14-V2-eSA-18-LH-s2 | 18 | CZ14 | V2 | CZ14-V2-eSA-18 | CZ14-V2-eSA-18-LH | 14.264 | 2.9106 | 2255.8959 | 0 | 3.2375 | 2255.8959 | 2301.8823
DEER-SFAM-CZ14-V2-eSA-18-LL-s2 | 18 | CZ14 | V2 | CZ14-V2-eSA-18 | CZ14-V2-eSA-18-LL | 14.5053 | 2.9002 | 2221.428 | 0 | 3.2375 | 2221.428 | 2281.426
DEER-SFAM-CZ14-V2-eSA-18-TH-s2 | 18 | CZ14 | V2 | CZ14-V2-eSA-18 | CZ14-V2-eSA-18-TH | 15.1863 | 3.3125 | 2378.8494 | 0 | 3.6782 | 2378.8494 | 2415.2843
DEER-SFAM-CZ14-V2-eSA-18-TL-s2 | 18 | CZ14 | V2 | CZ14-V2-eSA-18 | CZ14-V2-eSA-18-TL | 14.6024 | 3.6806 | 2592.3165 | 0 | 3.6782 | 2592.3165 | 2631.9567
DEER-SFAM-CZ14-V2-eSA-18-TM-s2 | 18 | CZ14 | V2 | CZ14-V2-eSA-18 | CZ14-V2-eSA-18-TM | 14.2299 | 3.0938 | 2457.6663 | 0 | 3.2375 | 2457.6663 | 2494.7868
DEER-SFAM-CZ14-V2-eSH-10-HH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-HH | 8.8737 | 4.4516 | 3470.7754 | 3307.4806 | 3.6782 | 6778.256 | 3821.6427
DEER-SFAM-CZ14-V2-eSH-10-HL-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-HL | 8.6185 | 4.6752 | 3576.4068 | 3279.0385 | 3.6782 | 6855.4454 | 3911.5256
DEER-SFAM-CZ14-V2-eSH-10-HM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-HM | 8.7929 | 4.5947 | 3614.7196 | 3215.0696 | 3.6782 | 6829.7892 | 3939.5878
DEER-SFAM-CZ14-V2-eSH-10-LH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-LH | 9.0336 | 3.8211 | 3551.7275 | 3524.9898 | 3.2375 | 7076.7173 | 3910.3856
DEER-SFAM-CZ14-V2-eSH-10-LL-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-LL | 8.9138 | 4.4367 | 3514.9045 | 3552.3562 | 3.6782 | 7067.2608 | 3894.6265
DEER-SFAM-CZ14-V2-eSH-10-LM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-LM | 9.121 | 4.2425 | 3441.8049 | 3437.9296 | 3.6782 | 6879.7345 | 3788.4853
DEER-SFAM-CZ14-V2-eSH-10-MH-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-MH | 9.0805 | 3.9986 | 3578.6214 | 3561.7232 | 3.2375 | 7140.3446 | 3960.5474
DEER-SFAM-CZ14-V2-eSH-10-ML-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-ML | 8.7855 | 4.71 | 3595.8189 | 3434.3927 | 3.6782 | 7030.2116 | 3955.8436
DEER-SFAM-CZ14-V2-eSH-10-MM-s1 | 10 | CZ14 | V2 | CZ14-V2-eSH-10 | CZ14-V2-eSH-10-MM | 8.926 | 4.0763 | 3618.9048 | 3361.826 | 3.2375 | 6980.7308 | 3939.1021
DEER-SFAM-CZ14-V2-eSH-13-HH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-HH | 10.5872 | 3.9809 | 2943.4667 | 3286.3334 | 3.6782 | 6229.8001 | 3263.2673
DEER-SFAM-CZ14-V2-eSH-13-HL-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-HL | 11.502 | 3.9898 | 2781.778 | 2866.4673 | 3.6782 | 5648.2453 | 3101.5169
DEER-SFAM-CZ14-V2-eSH-13-HM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-HM | 10.9135 | 3.8597 | 2855.0995 | 2936.162 | 3.6782 | 5791.2615 | 3145.7132
DEER-SFAM-CZ14-V2-eSH-13-LH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-LH | 11.0656 | 3.2187 | 2857.4409 | 3791.5568 | 3.2375 | 6648.9977 | 3326.5375
DEER-SFAM-CZ14-V2-eSH-13-LL-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-LL | 11.8586 | 3.5823 | 2652.8341 | 3033.573 | 3.6782 | 5686.4071 | 2947.6616
DEER-SFAM-CZ14-V2-eSH-13-LM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-LM | 10.2652 | 3.3834 | 2995.3028 | 2552.0276 | 3.2375 | 5547.3304 | 3321.0423
DEER-SFAM-CZ14-V2-eSH-13-MH-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-MH | 11.4309 | 3.6675 | 2715.5572 | 3331.5863 | 3.6782 | 6047.1435 | 3030.1548
DEER-SFAM-CZ14-V2-eSH-13-ML-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-ML | 10.2844 | 3.6303 | 3081.4814 | 3169.1931 | 3.2375 | 6250.6745 | 3404.0034
DEER-SFAM-CZ14-V2-eSH-13-MM-s1 | 13 | CZ14 | V2 | CZ14-V2-eSH-13 | CZ14-V2-eSH-13-MM | 11.0802 | 3.8905 | 2869.8826 | 3016.4978 | 3.6782 | 5886.3803 | 3118.6961
DEER-SFAM-CZ14-V2-eSH-14-HH-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-HH | 11.2898 | 3.8206 | 2770.3537 | 3029.1312 | 3.6782 | 5799.4849 | 3014.1225
DEER-SFAM-CZ14-V2-eSH-14-HL-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-HL | 11.8339 | 3.69 | 2645.8626 | 3055.8067 | 3.6782 | 5701.6692 | 2938.1229
DEER-SFAM-CZ14-V2-eSH-14-HM-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-HM | 11.8714 | 3.566 | 2629.062 | 3075.3662 | 3.6782 | 5704.4282 | 2839.9375
DEER-SFAM-CZ14-V2-eSH-14-MH-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-MH | 11.8658 | 3.0751 | 2650.3823 | 3536.8316 | 3.2375 | 6187.2139 | 2966.0507
DEER-SFAM-CZ14-V2-eSH-14-ML-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-ML | 11.9104 | 3.5888 | 2627.5206 | 3590.1549 | 3.6782 | 6217.6755 | 3030.3629
DEER-SFAM-CZ14-V2-eSH-14-MM-s1 | 14 | CZ14 | V2 | CZ14-V2-eSH-14 | CZ14-V2-eSH-14-MM | 11.5317 | 3.5852 | 2693.127 | 3001.8349 | 3.6782 | 5694.962 | 2966.6761
DEER-SFAM-CZ14-V2-eSH-15-HH-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-HH | 12.8817 | 3.3059 | 2442.9676 | 3621.9153 | 3.6782 | 6064.883 | 2668.2104
DEER-SFAM-CZ14-V2-eSH-15-HL-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-HL | 12.9847 | 3.4074 | 2466.0921 | 2574.2419 | 3.6782 | 5040.334 | 2688.5135
DEER-SFAM-CZ14-V2-eSH-15-HM-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-HM | 12.8774 | 3.373 | 2389.8258 | 2690.726 | 3.6782 | 5080.5518 | 2610.3732
DEER-SFAM-CZ14-V2-eSH-15-MH-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-MH | 12.0385 | 3.4736 | 2622.838 | 3166.1971 | 3.6782 | 5789.0351 | 2838.1956
DEER-SFAM-CZ14-V2-eSH-15-ML-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-ML | 12.7676 | 3.4143 | 2452.9649 | 3121.8294 | 3.6782 | 5574.7943 | 2680.6272
DEER-SFAM-CZ14-V2-eSH-15-MM-s1 | 15 | CZ14 | V2 | CZ14-V2-eSH-15 | CZ14-V2-eSH-15-MM | 13.0646 | 3.3051 | 2371.6635 | 3287.9272 | 3.6782 | 5659.5907 | 2612.5081
DEER-SFAM-CZ14-V2-eSH-16-CH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-CH | 13.8394 | 3.5365 | 2624.209 | 3613.943 | 3.6782 | 6238.152 | 2893.7416
DEER-SFAM-CZ14-V2-eSH-16-CL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-CL | 13.9983 | 3.5903 | 2687.6942 | 3365.8536 | 3.6782 | 6053.5478 | 2964.0109
DEER-SFAM-CZ14-V2-eSH-16-LH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-LH | 13.1678 | 3.0577 | 2419.7705 | 3669.5337 | 3.2375 | 6089.3042 | 2675.5738
DEER-SFAM-CZ14-V2-eSH-16-LL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-LL | 12.762 | 3.1675 | 2535.7921 | 3469.3671 | 3.2375 | 6005.1593 | 2751.3771
DEER-SFAM-CZ14-V2-eSH-16-LM-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-LM | 12.5735 | 3.1063 | 2543.1694 | 3746.728 | 3.2375 | 6289.8975 | 2831.3548
DEER-SFAM-CZ14-V2-eSH-16-TH-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-TH | 14.1703 | 3.7553 | 2552.7073 | 4622.005 | 3.6782 | 7174.7122 | 2874.8098
DEER-SFAM-CZ14-V2-eSH-16-TL-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-TL | 12.916 | 4.0027 | 2885.2836 | 4439.8191 | 3.6782 | 7325.1027 | 3178.9224
DEER-SFAM-CZ14-V2-eSH-16-TM-s2 | 16 | CZ14 | V2 | CZ14-V2-eSH-16 | CZ14-V2-eSH-16-TM | 13.1485 | 3.9148 | 2837.7098 | 4474.2718 | 3.6782 | 7311.9816 | 3138.3761
DEER-SFAM-CZ14-V2-eSH-17-CM-s2 | 17 | CZ14 | V2 | CZ14-V2-eSH-17 | CZ14-V2-eSH-17-CM | 14.7506 | 3.4211 | 2547.7594 | 3321.4601 | 3.6782 | 5869.2195 | 2817.2189
DEER-SFAM-CZ14-V2-eSH-17-LM-s2 | 17 | CZ14 | V2 | CZ14-V2-eSH-17 | CZ14-V2-eSH-17-LM | 13.4852 | 3.0677 | 2440.505 | 3328.5429 | 3.2375 | 5769.0479 | 2560.7408
DEER-SFAM-CZ14-V2-eSH-17-TH-s2 | 17 | CZ14 | V2 | CZ14-V2-eSH-17 | CZ14-V2-eSH-17-TH | 14.5934 | 3.5228 | 2456.0619 | 4609.6491 | 3.6782 | 7065.711 | 2796.9867
DEER-SFAM-CZ14-V2-eSH-17-TL-s2 | 17 | CZ14 | V2 | CZ14-V2-eSH-17 | CZ14-V2-eSH-17-TL | 14.5962 | 3.6083 | 2479.8563 | 4610.4139 | 3.6782 | 7090.2702 | 2818.4462
DEER-SFAM-CZ14-V2-eSH-18-LH-s2 | 18 | CZ14 | V2 | CZ14-V2-eSH-18 | CZ14-V2-eSH-18-LH | 13.7148 | 2.9445 | 2375.95 | 3990.7567 | 3.2375 | 6366.7067 | 2594.7254
DEER-SFAM-CZ14-V2-eSH-18-LL-s2 | 18 | CZ14 | V2 | CZ14-V2-eSH-18 | CZ14-V2-eSH-18-LL | 13.0303 | 3.0609 | 2469.3761 | 3532.5559 | 3.2375 | 6001.932 | 2655.9717
DEER-SFAM-CZ14-V2-eSH-18-LM-s2 | 18 | CZ14 | V2 | CZ14-V2-eSH-18 | CZ14-V2-eSH-18-LM | 14.0598 | 2.9829 | 2320.0739 | 4236.9304 | 3.2375 | 6557.0044 | 2572.4158
DEER-SFAM-CZ14-V2-eSH-18-TM-s2 | 18 | CZ14 | V2 | CZ14-V2-eSH-18 | CZ14-V2-eSH-18-TM | 14.4132 | 3.0375 | 2546.5533 | 4690.8096 | 3.2375 | 7237.3629 | 3019.7247
DEER-SFAM-CZ14-V3-eSA-10-HH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-HH | 8.3699 | 3.9349 | 3022.8835 | 0 | 3.4 | 3022.8835 | 3094.8874
DEER-SFAM-CZ14-V3-eSA-10-HL-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-HL | 8.347 | 4.4057 | 3046.0952 | 0 | 3.4 | 3046.0952 | 3118.1365
DEER-SFAM-CZ14-V3-eSA-10-HM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-HM | 8.3187 | 4.1881 | 2985.0288 | 0 | 3.4 | 2985.0288 | 3057.064
DEER-SFAM-CZ14-V3-eSA-10-LH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-LH | 8.6972 | 3.8426 | 2992.8901 | 0 | 3.4 | 2992.8901 | 3064.9677
DEER-SFAM-CZ14-V3-eSA-10-LL-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-LL | 8.9007 | 3.9558 | 2905.0219 | 0 | 3.4 | 2905.0219 | 2977.0712
DEER-SFAM-CZ14-V3-eSA-10-LM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-LM | 8.6743 | 3.8657 | 2973.7109 | 0 | 3.4 | 2973.7109 | 3045.7906
DEER-SFAM-CZ14-V3-eSA-10-MH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-MH | 8.5054 | 3.7746 | 3029.233 | 0 | 3.4 | 3029.233 | 3101.2979
DEER-SFAM-CZ14-V3-eSA-10-ML-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-ML | 8.4841 | 4.0373 | 2993.3984 | 0 | 3.4 | 2993.3984 | 3065.4404
DEER-SFAM-CZ14-V3-eSA-10-MM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSA-10 | CZ14-V3-eSA-10-MM | 8.5477 | 3.3418 | 3030.859 | 0 | 3 | 3030.859 | 3102.8511
DEER-SFAM-CZ14-V3-eSA-13-HH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-HH | 11.1484 | 3.4016 | 2349.9193 | 0 | 3.4 | 2349.9193 | 2414.857
DEER-SFAM-CZ14-V3-eSA-13-HL-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-HL | 10.4114 | 3.6159 | 2432.8911 | 0 | 3.4 | 2432.8911 | 2489.7281
DEER-SFAM-CZ14-V3-eSA-13-HM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-HM | 11.286 | 3.3685 | 2256.5932 | 0 | 3.4 | 2256.5932 | 2321.5173
DEER-SFAM-CZ14-V3-eSA-13-LH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-LH | 11.1152 | 3.1157 | 2275.1232 | 0 | 3.4 | 2275.1232 | 2347.1752
DEER-SFAM-CZ14-V3-eSA-13-LL-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-LL | 10.6829 | 3.3068 | 2385.43 | 0 | 3.4 | 2385.43 | 2457.3917
DEER-SFAM-CZ14-V3-eSA-13-LM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-LM | 10.3571 | 2.9927 | 2423.064 | 0 | 3 | 2423.064 | 2495.0212
DEER-SFAM-CZ14-V3-eSA-13-MH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-MH | 11.2264 | 3.2461 | 2263.1131 | 0 | 3.4 | 2263.1131 | 2335.1483
DEER-SFAM-CZ14-V3-eSA-13-ML-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-ML | 10.2046 | 3.403 | 2368.4539 | 0 | 3.4 | 2368.4539 | 2440.2755
DEER-SFAM-CZ14-V3-eSA-13-MM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSA-13 | CZ14-V3-eSA-13-MM | 11.7342 | 3.1685 | 2155.5023 | 0 | 3.4 | 2155.5023 | 2227.5309
DEER-SFAM-CZ14-V3-eSA-14-HH-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-HH | 10.411 | 3.2712 | 2320.2466 | 0 | 3.4 | 2320.2466 | 2380.6256
DEER-SFAM-CZ14-V3-eSA-14-HL-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-HL | 11.6882 | 3.1784 | 2142.432 | 0 | 3.4 | 2142.432 | 2186.8305
DEER-SFAM-CZ14-V3-eSA-14-HM-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-HM | 10.9249 | 3.3223 | 2329.0781 | 0 | 3.4 | 2329.0781 | 2397.1808
DEER-SFAM-CZ14-V3-eSA-14-MH-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-MH | 11.1196 | 2.7948 | 2302.2243 | 0 | 3 | 2302.2243 | 2349.5274
DEER-SFAM-CZ14-V3-eSA-14-ML-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-ML | 11.0813 | 3.251 | 2271.4446 | 0 | 3.4 | 2271.4446 | 2347.0347
DEER-SFAM-CZ14-V3-eSA-14-MM-s1 | 14 | CZ14 | V3 | CZ14-V3-eSA-14 | CZ14-V3-eSA-14-MM | 10.9847 | 2.7843 | 2277.6779 | 0 | 3 | 2277.6779 | 2329.5318
DEER-SFAM-CZ14-V3-eSA-15-HH-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-HH | 12.7754 | 2.9614 | 2000.3506 | 0 | 3.4 | 2000.3506 | 2050.679
DEER-SFAM-CZ14-V3-eSA-15-HL-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-HL | 12.7239 | 3.0027 | 1958.025 | 0 | 3.4 | 1958.025 | 2020.7635
DEER-SFAM-CZ14-V3-eSA-15-HM-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-HM | 12.9739 | 2.8657 | 1974.6488 | 0 | 3.4 | 1974.6488 | 2025.1678
DEER-SFAM-CZ14-V3-eSA-15-MH-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-MH | 11.2677 | 3.1583 | 2212.5128 | 0 | 3.4 | 2212.5128 | 2250.013
DEER-SFAM-CZ14-V3-eSA-15-ML-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-ML | 12.3046 | 2.9715 | 2080.8033 | 0 | 3.4 | 2080.8033 | 2131.2656
DEER-SFAM-CZ14-V3-eSA-15-MM-s1 | 15 | CZ14 | V3 | CZ14-V3-eSA-15 | CZ14-V3-eSA-15-MM | 11.969 | 3.0328 | 2098.8241 | 0 | 3.4 | 2098.8241 | 2144.8093
DEER-SFAM-CZ14-V3-eSA-16-CH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-CH | 13.8808 | 2.9136 | 2104.5368 | 0 | 3.4 | 2104.5368 | 2133.4315
DEER-SFAM-CZ14-V3-eSA-16-CL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-CL | 14.2971 | 2.8753 | 1962.2541 | 0 | 3.4 | 1962.2541 | 1998.8038
DEER-SFAM-CZ14-V3-eSA-16-CM-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-CM | 13.9715 | 2.8892 | 2041.5666 | 0 | 3.4 | 2041.5666 | 2080.1403
DEER-SFAM-CZ14-V3-eSA-16-LH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-LH | 13.5374 | 2.8367 | 1870.8183 | 0 | 3.4 | 1870.8183 | 1920.43
DEER-SFAM-CZ14-V3-eSA-16-LL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-LL | 12.9594 | 3.0767 | 1972.1912 | 0 | 3.4 | 1972.1912 | 2004.9387
DEER-SFAM-CZ14-V3-eSA-16-LM-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-LM | 12.7535 | 2.999 | 2001.658 | 0 | 3.4 | 2001.658 | 2031.3531
DEER-SFAM-CZ14-V3-eSA-16-NM-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-NM | 14.6053 | 2.7766 | 1757.8472 | 0 | 3.4 | 1757.8472 | 1787.0006
DEER-SFAM-CZ14-V3-eSA-16-TH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-TH | 12.6551 | 3.4467 | 2257 | 0 | 3.4 | 2257 | 2275.6355
DEER-SFAM-CZ14-V3-eSA-16-TL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSA-16 | CZ14-V3-eSA-16-TL | 14.4133 | 3.143 | 1900.1984 | 0 | 3.4 | 1900.1984 | 1920.389
DEER-SFAM-CZ14-V3-eSA-17-CH-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-CH | 14.6381 | 2.8305 | 1960.283 | 0 | 3.4 | 1960.283 | 1996.8251
DEER-SFAM-CZ14-V3-eSA-17-CL-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-CL | 14.6264 | 2.8007 | 1937.5094 | 0 | 3.4 | 1937.5094 | 1974.0423
DEER-SFAM-CZ14-V3-eSA-17-CM-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-CM | 14.7868 | 2.8234 | 1956.8704 | 0 | 3.4 | 1956.8704 | 1985.6778
DEER-SFAM-CZ14-V3-eSA-17-LH-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-LH | 13.6794 | 2.5855 | 1851.5654 | 0 | 3 | 1851.5654 | 1890.4731
DEER-SFAM-CZ14-V3-eSA-17-LL-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-LL | 13.4563 | 2.9879 | 1913.6375 | 0 | 3.4 | 1913.6375 | 1934.9108
DEER-SFAM-CZ14-V3-eSA-17-LM-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-LM | 13.2772 | 2.9778 | 1924.4403 | 0 | 3.4 | 1924.4403 | 1942.8204
DEER-SFAM-CZ14-V3-eSA-17-TH-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-TH | 14.2027 | 2.9773 | 1968.6999 | 0 | 3.4 | 1968.6999 | 1998.5441
DEER-SFAM-CZ14-V3-eSA-17-TL-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-TL | 16.0562 | 2.8792 | 1654.2653 | 0 | 3.4 | 1654.2653 | 1700.691
DEER-SFAM-CZ14-V3-eSA-17-TM-s2 | 17 | CZ14 | V3 | CZ14-V3-eSA-17 | CZ14-V3-eSA-17-TM | 15.7483 | 2.9409 | 1916.3911 | 0 | 3.4 | 1916.3911 | 1932.027
DEER-SFAM-CZ14-V3-eSA-18-LH-s2 | 18 | CZ14 | V3 | CZ14-V3-eSA-18 | CZ14-V3-eSA-18-LH | 14.2341 | 2.7634 | 1792.3074 | 0 | 3.4 | 1792.3074 | 1817.915
DEER-SFAM-CZ14-V3-eSA-18-LL-s2 | 18 | CZ14 | V3 | CZ14-V3-eSA-18 | CZ14-V3-eSA-18-LL | 14.5707 | 2.7629 | 1750.0967 | 0 | 3.4 | 1750.0967 | 1783.5257
DEER-SFAM-CZ14-V3-eSA-18-TH-s2 | 18 | CZ14 | V3 | CZ14-V3-eSA-18 | CZ14-V3-eSA-18-TH | 15.1204 | 2.7745 | 1856.7257 | 0 | 3.4 | 1856.7257 | 1877.0304
DEER-SFAM-CZ14-V3-eSA-18-TL-s2 | 18 | CZ14 | V3 | CZ14-V3-eSA-18 | CZ14-V3-eSA-18-TL | 14.7692 | 3.0533 | 1983.526 | 0 | 3.4 | 1983.526 | 2005.6722
DEER-SFAM-CZ14-V3-eSA-18-TM-s2 | 18 | CZ14 | V3 | CZ14-V3-eSA-18 | CZ14-V3-eSA-18-TM | 14.1003 | 2.9455 | 1965.0153 | 0 | 3.4 | 1965.0153 | 1985.7498
DEER-SFAM-CZ14-V3-eSH-10-HH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-HH | 8.7356 | 3.9216 | 2849.1651 | 1784.1889 | 3.4 | 4633.354 | 3036.554
DEER-SFAM-CZ14-V3-eSH-10-HL-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-HL | 8.5284 | 4.1266 | 2919.9015 | 1775.3585 | 3.4 | 4695.26 | 3098.86
DEER-SFAM-CZ14-V3-eSH-10-HM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-HM | 8.6507 | 4.0207 | 2951.2518 | 1773.3067 | 3.4 | 4724.5585 | 3124.2585
DEER-SFAM-CZ14-V3-eSH-10-LH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-LH | 8.5755 | 3.7792 | 3000.1036 | 1845.1254 | 3.4 | 4845.229 | 3193.629
DEER-SFAM-CZ14-V3-eSH-10-LL-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-LL | 8.8207 | 3.8606 | 2861.2068 | 1881.6656 | 3.4 | 4742.8724 | 3063.6724
DEER-SFAM-CZ14-V3-eSH-10-LM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-LM | 8.9811 | 3.707 | 2817.8268 | 1854.8989 | 3.4 | 4672.7257 | 3003.6257
DEER-SFAM-CZ14-V3-eSH-10-MH-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-MH | 8.6664 | 3.9294 | 2993.0045 | 1854.996 | 3.4 | 4848.0005 | 3198.1005
DEER-SFAM-CZ14-V3-eSH-10-ML-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-ML | 8.7144 | 4.1016 | 2916.5822 | 1828.6746 | 3.4 | 4745.2568 | 3109.6568
DEER-SFAM-CZ14-V3-eSH-10-MM-s1 | 10 | CZ14 | V3 | CZ14-V3-eSH-10 | CZ14-V3-eSH-10-MM | 8.6117 | 3.9566 | 2995.9168 | 1785.0635 | 3.4 | 4780.9803 | 3168.0803
DEER-SFAM-CZ14-V3-eSH-13-HH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-HH | 10.4908 | 3.5142 | 2408.9602 | 1734.7685 | 3.4 | 4143.7287 | 2580.7287
DEER-SFAM-CZ14-V3-eSH-13-HL-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-HL | 11.2959 | 3.4364 | 2268.5371 | 1513.1708 | 3.4 | 3781.7079 | 2439.6079
DEER-SFAM-CZ14-V3-eSH-13-HM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-HM | 10.8346 | 3.3941 | 2332.5331 | 1565.4163 | 3.4 | 3897.9494 | 2488.6494
DEER-SFAM-CZ14-V3-eSH-13-LH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-LH | 10.608 | 3.1926 | 2392.6836 | 1808.7463 | 3.4 | 4201.4299 | 2648.6299
DEER-SFAM-CZ14-V3-eSH-13-LL-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-LL | 11.7423 | 3.1288 | 2158.1558 | 1570.5725 | 3.4 | 3728.7283 | 2316.0283
DEER-SFAM-CZ14-V3-eSH-13-LM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-LM | 10.0996 | 3.0823 | 2465.0461 | 1327.6244 | 3 | 3792.6705 | 2640.1705
DEER-SFAM-CZ14-V3-eSH-13-MH-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-MH | 11.2726 | 3.1395 | 2224.423 | 1760.8965 | 3.4 | 3985.3195 | 2392.2195
DEER-SFAM-CZ14-V3-eSH-13-ML-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-ML | 9.9825 | 3.5449 | 2551.7423 | 1587.2987 | 3.4 | 4139.041 | 2724.741
DEER-SFAM-CZ14-V3-eSH-13-MM-s1 | 13 | CZ14 | V3 | CZ14-V3-eSH-13 | CZ14-V3-eSH-13-MM | 10.9423 | 3.4068 | 2338.447 | 1625.8951 | 3.4 | 3964.3421 | 2472.3421
DEER-SFAM-CZ14-V3-eSH-14-HH-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-HH | 11.213 | 3.3682 | 2261.5256 | 1599.2373 | 3.4 | 3860.7629 | 2392.4629
DEER-SFAM-CZ14-V3-eSH-14-HL-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-HL | 11.8168 | 3.2408 | 2147.3642 | 1574.161 | 3.4 | 3721.5252 | 2303.4252
DEER-SFAM-CZ14-V3-eSH-14-HM-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-HM | 11.7834 | 3.1276 | 2147.3366 | 1597.7799 | 3.4 | 3745.1165 | 2260.6165
DEER-SFAM-CZ14-V3-eSH-14-MH-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-MH | 11.4089 | 3.0088 | 2217.4285 | 1699.5405 | 3.4 | 3916.969 | 2391.269
DEER-SFAM-CZ14-V3-eSH-14-ML-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-ML | 11.7972 | 3.1226 | 2129.7909 | 1713.5181 | 3.4 | 3843.309 | 2342.909
DEER-SFAM-CZ14-V3-eSH-14-MM-s1 | 14 | CZ14 | V3 | CZ14-V3-eSH-14 | CZ14-V3-eSH-14-MM | 11.3901 | 3.1691 | 2198.5285 | 1536.613 | 3.4 | 3735.1415 | 2344.7415
DEER-SFAM-CZ14-V3-eSH-15-HH-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-HH | 12.6777 | 2.8776 | 2008.1169 | 1752.5889 | 3.4 | 3760.7058 | 2129.6058
DEER-SFAM-CZ14-V3-eSH-15-HL-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-HL | 12.9122 | 2.9972 | 2005.9688 | 1370.0384 | 3.4 | 3376.0072 | 2125.2072
DEER-SFAM-CZ14-V3-eSH-15-HM-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-HM | 12.8117 | 2.8363 | 1944.4086 | 1436.2251 | 3.4 | 3380.6337 | 2061.8337
DEER-SFAM-CZ14-V3-eSH-15-MH-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-MH | 11.8408 | 3.0435 | 2136.6459 | 1550.0705 | 3.4 | 3686.7164 | 2250.5164
DEER-SFAM-CZ14-V3-eSH-15-ML-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-ML | 12.6654 | 2.9575 | 1986.101 | 1525.9049 | 3.4 | 3512.0059 | 2106.5059
DEER-SFAM-CZ14-V3-eSH-15-MM-s1 | 15 | CZ14 | V3 | CZ14-V3-eSH-15 | CZ14-V3-eSH-15-MM | 13.0026 | 2.7983 | 1928.7698 | 1655.4138 | 3.4 | 3584.1836 | 2058.4836
DEER-SFAM-CZ14-V3-eSH-16-CH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-CH | 14.0112 | 2.9109 | 2030.7885 | 1749.8625 | 3.4 | 3780.651 | 2158.551
DEER-SFAM-CZ14-V3-eSH-16-CL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-CL | 14.2433 | 2.949 | 2045.6897 | 1637.9295 | 3.4 | 3683.6192 | 2176.3192
DEER-SFAM-CZ14-V3-eSH-16-LH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-LH | 12.8351 | 2.9233 | 1969.5965 | 1703.7127 | 3.4 | 3673.3092 | 2091.5092
DEER-SFAM-CZ14-V3-eSH-16-LL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-LL | 12.8228 | 2.8137 | 1993.4347 | 1615.8499 | 3 | 3609.2846 | 2094.7846
DEER-SFAM-CZ14-V3-eSH-16-LM-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-LM | 12.5258 | 2.7766 | 2025.4667 | 1734.2113 | 3 | 3759.678 | 2165.378
DEER-SFAM-CZ14-V3-eSH-16-TH-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-TH | 14.2467 | 3.0571 | 1968.7326 | 2203.3295 | 3.4 | 4172.0621 | 2109.3621
DEER-SFAM-CZ14-V3-eSH-16-TL-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-TL | 13.1585 | 3.3573 | 2204.0508 | 2122.7181 | 3.4 | 4326.7689 | 2331.6689
DEER-SFAM-CZ14-V3-eSH-16-TM-s2 | 16 | CZ14 | V3 | CZ14-V3-eSH-16 | CZ14-V3-eSH-16-TM | 13.3658 | 3.2703 | 2170.3264 | 2147.4056 | 3.4 | 4317.732 | 2302.132
DEER-SFAM-CZ14-V3-eSH-17-CM-s2 | 17 | CZ14 | V3 | CZ14-V3-eSH-17 | CZ14-V3-eSH-17-CM | 15.0051 | 2.8077 | 1940.5783 | 1586.8627 | 3.4 | 3527.441 | 2060.341
DEER-SFAM-CZ14-V3-eSH-17-LM-s2 | 17 | CZ14 | V3 | CZ14-V3-eSH-17 | CZ14-V3-eSH-17-LM | 13.3682 | 3.0016 | 1954.3327 | 1534.6196 | 3.4 | 3488.9523 | 2009.2523
DEER-SFAM-CZ14-V3-eSH-17-TH-s2 | 17 | CZ14 | V3 | CZ14-V3-eSH-17 | CZ14-V3-eSH-17-TH | 14.6544 | 2.9378 | 1903.2028 | 2203.7137 | 3.4 | 4106.9165 | 2055.8165
DEER-SFAM-CZ14-V3-eSH-17-TL-s2 | 17 | CZ14 | V3 | CZ14-V3-eSH-17 | CZ14-V3-eSH-17-TL | 14.7165 | 2.999 | 1907.8176 | 2191.3747 | 3.4 | 4099.1923 | 2058.0923
DEER-SFAM-CZ14-V3-eSH-18-LH-s2 | 18 | CZ14 | V3 | CZ14-V3-eSH-18 | CZ14-V3-eSH-18-LH | 13.7583 | 2.6344 | 1867.0868 | 1808.0005 | 3 | 3675.0873 | 1966.6873
DEER-SFAM-CZ14-V3-eSH-18-LL-s2 | 18 | CZ14 | V3 | CZ14-V3-eSH-18 | CZ14-V3-eSH-18-LL | 13.1015 | 2.7434 | 1943.5419 | 1619.6274 | 3 | 3563.1693 | 2031.5693
DEER-SFAM-CZ14-V3-eSH-18-LM-s2 | 18 | CZ14 | V3 | CZ14-V3-eSH-18 | CZ14-V3-eSH-18-LM | 14.0778 | 2.8891 | 1830.3577 | 1850.9614 | 3.4 | 3681.3191 | 1938.0191
DEER-SFAM-CZ14-V3-eSH-18-TM-s2 | 18 | CZ14 | V3 | CZ14-V3-eSH-18 | CZ14-V3-eSH-18-TM | 14.556 | 2.733 | 1992.6602 | 2216.8186 | 3 | 4209.4788 | 2227.9788
DEER-SFAM-CZ14-V4-eSA-10-HH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-HH | 8.4455 | 4.5135 | 3644.3896 | 0 | 3.8 | 3644.3896 | 3716.426
DEER-SFAM-CZ14-V4-eSA-10-HL-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-HL | 8.3798 | 5.3214 | 3694.5666 | 0 | 4.2 | 3694.5666 | 3766.6796
DEER-SFAM-CZ14-V4-eSA-10-HM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-HM | 8.3466 | 5.0531 | 3623.5525 | 0 | 4.2 | 3623.5525 | 3695.6595
DEER-SFAM-CZ14-V4-eSA-10-LH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-LH | 8.7789 | 4.4104 | 3608.472 | 0 | 3.8 | 3608.472 | 3680.59
DEER-SFAM-CZ14-V4-eSA-10-LL-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-LL | 8.9231 | 4.7995 | 3527.7698 | 0 | 4.2 | 3527.7698 | 3599.8912
DEER-SFAM-CZ14-V4-eSA-10-LM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-LM | 8.7458 | 4.4378 | 3587.8155 | 0 | 3.8 | 3587.8155 | 3659.9348
DEER-SFAM-CZ14-V4-eSA-10-MH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-MH | 8.605 | 4.3246 | 3642.1118 | 0 | 3.8 | 3642.1118 | 3714.2167
DEER-SFAM-CZ14-V4-eSA-10-ML-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-ML | 8.5424 | 4.6605 | 3619.0738 | 0 | 3.8 | 3619.0738 | 3691.1514
DEER-SFAM-CZ14-V4-eSA-10-MM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSA-10 | CZ14-V4-eSA-10-MM | 8.5211 | 4.259 | 3693.5859 | 0 | 3.8 | 3693.5859 | 3765.668
DEER-SFAM-CZ14-V4-eSA-13-HH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-HH | 11.202 | 4.1538 | 2848.9877 | 0 | 4.2 | 2848.9877 | 2913.9899
DEER-SFAM-CZ14-V4-eSA-13-HL-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-HL | 10.4438 | 4.3363 | 2951.8322 | 0 | 4.2 | 2951.8322 | 3008.7258
DEER-SFAM-CZ14-V4-eSA-13-HM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-HM | 11.3375 | 4.0059 | 2736.5909 | 0 | 4.2 | 2736.5909 | 2801.5802
DEER-SFAM-CZ14-V4-eSA-13-LH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-LH | 11.1279 | 3.7262 | 2765.801 | 0 | 4.2 | 2765.801 | 2837.9251
DEER-SFAM-CZ14-V4-eSA-13-LL-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-LL | 10.7648 | 3.8071 | 2881.5036 | 0 | 3.8 | 2881.5036 | 2953.4944
DEER-SFAM-CZ14-V4-eSA-13-LM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-LM | 10.3208 | 3.76 | 2955.3378 | 0 | 3.8 | 2955.3378 | 3027.3869
DEER-SFAM-CZ14-V4-eSA-13-MH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-MH | 11.2738 | 3.8701 | 2744.5265 | 0 | 4.2 | 2744.5265 | 2816.6336
DEER-SFAM-CZ14-V4-eSA-13-ML-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-ML | 10.2618 | 3.9329 | 2866.3527 | 0 | 3.8 | 2866.3527 | 2938.2084
DEER-SFAM-CZ14-V4-eSA-13-MM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSA-13 | CZ14-V4-eSA-13-MM | 11.7834 | 3.7452 | 2613.6047 | 0 | 4.2 | 2613.6047 | 2685.7059
DEER-SFAM-CZ14-V4-eSA-14-HH-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-HH | 10.4948 | 3.7763 | 2801.3966 | 0 | 3.8 | 2801.3966 | 2861.8046
DEER-SFAM-CZ14-V4-eSA-14-HL-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-HL | 11.7326 | 3.7511 | 2598.9679 | 0 | 4.2 | 2598.9679 | 2643.4102
DEER-SFAM-CZ14-V4-eSA-14-HM-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-HM | 10.9604 | 3.9896 | 2825.8307 | 0 | 4.2 | 2825.8307 | 2894.0014
DEER-SFAM-CZ14-V4-eSA-14-MH-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-MH | 11.0775 | 3.5115 | 2808.8521 | 0 | 3.8 | 2808.8521 | 2856.2156
DEER-SFAM-CZ14-V4-eSA-14-ML-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-ML | 11.1079 | 3.9297 | 2756.7652 | 0 | 4.2 | 2756.7652 | 2832.4298
DEER-SFAM-CZ14-V4-eSA-14-MM-s1 | 14 | CZ14 | V4 | CZ14-V4-eSA-14 | CZ14-V4-eSA-14-MM | 10.9465 | 3.5344 | 2776.6618 | 0 | 3.8 | 2776.6618 | 2828.5822
DEER-SFAM-CZ14-V4-eSA-15-HH-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-HH | 12.8404 | 3.5428 | 2425.3652 | 0 | 4.2 | 2425.3652 | 2475.7431
DEER-SFAM-CZ14-V4-eSA-15-HL-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-HL | 12.7918 | 3.5819 | 2372.7991 | 0 | 4.2 | 2372.7991 | 2435.6005
DEER-SFAM-CZ14-V4-eSA-15-HM-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-HM | 13.0291 | 3.406 | 2394.7651 | 0 | 4.2 | 2394.7651 | 2445.3337
DEER-SFAM-CZ14-V4-eSA-15-MH-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-MH | 11.3865 | 3.6294 | 2665.2689 | 0 | 3.8 | 2665.2689 | 2702.7884
DEER-SFAM-CZ14-V4-eSA-15-ML-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-ML | 12.4027 | 3.427 | 2512.1878 | 0 | 3.8 | 2512.1878 | 2562.67
DEER-SFAM-CZ14-V4-eSA-15-MM-s1 | 15 | CZ14 | V4 | CZ14-V4-eSA-15 | CZ14-V4-eSA-15-MM | 12.0059 | 3.6162 | 2547.1136 | 0 | 4.2 | 2547.1136 | 2593.1441
DEER-SFAM-CZ14-V4-eSA-16-CH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-CH | 13.9087 | 3.5592 | 2552.0944 | 0 | 4.2 | 2552.0944 | 2581.0477
DEER-SFAM-CZ14-V4-eSA-16-CL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-CL | 14.3214 | 3.4973 | 2380.9618 | 0 | 4.2 | 2380.9618 | 2417.582
DEER-SFAM-CZ14-V4-eSA-16-CM-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-CM | 14.008 | 3.5167 | 2476.2528 | 0 | 4.2 | 2476.2528 | 2514.9077
DEER-SFAM-CZ14-V4-eSA-16-LH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-LH | 13.6886 | 3.2988 | 2249.0416 | 0 | 3.8 | 2249.0416 | 2298.6688
DEER-SFAM-CZ14-V4-eSA-16-LL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-LL | 13.0467 | 3.5787 | 2380.5196 | 0 | 3.8 | 2380.5196 | 2413.2884
DEER-SFAM-CZ14-V4-eSA-16-LM-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-LM | 12.8335 | 3.4766 | 2417.0795 | 0 | 3.8 | 2417.0795 | 2446.7947
DEER-SFAM-CZ14-V4-eSA-16-NM-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-NM | 14.609 | 3.2463 | 2135.8253 | 0 | 3.8 | 2135.8253 | 2164.9945
DEER-SFAM-CZ14-V4-eSA-16-TH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-TH | 12.7609 | 4.0218 | 2702.6722 | 0 | 3.8 | 2702.6722 | 2721.3201
DEER-SFAM-CZ14-V4-eSA-16-TL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSA-16 | CZ14-V4-eSA-16-TL | 14.4586 | 3.7053 | 2300.0185 | 0 | 4.2 | 2300.0185 | 2320.249
DEER-SFAM-CZ14-V4-eSA-17-CH-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-CH | 14.6671 | 3.4532 | 2375.9446 | 0 | 4.2 | 2375.9446 | 2412.5594
DEER-SFAM-CZ14-V4-eSA-17-CL-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-CL | 14.6521 | 3.4008 | 2349.998 | 0 | 4.2 | 2349.998 | 2386.6035
DEER-SFAM-CZ14-V4-eSA-17-CM-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-CM | 14.8141 | 3.4319 | 2374.0434 | 0 | 4.2 | 2374.0434 | 2402.9089
DEER-SFAM-CZ14-V4-eSA-17-LH-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-LH | 13.6999 | 3.2844 | 2249.9823 | 0 | 3.8 | 2249.9823 | 2288.9472
DEER-SFAM-CZ14-V4-eSA-17-LL-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-LL | 13.5327 | 3.4687 | 2312.2087 | 0 | 3.8 | 2312.2087 | 2333.4983
DEER-SFAM-CZ14-V4-eSA-17-LM-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-LM | 13.3557 | 3.4511 | 2323.6429 | 0 | 3.8 | 2323.6429 | 2342.0357
DEER-SFAM-CZ14-V4-eSA-17-TH-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-TH | 14.369 | 3.4545 | 2355.3093 | 0 | 3.8 | 2355.3093 | 2385.1741
DEER-SFAM-CZ14-V4-eSA-17-TL-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-TL | 16.1024 | 3.4323 | 2004.4143 | 0 | 4.2 | 2004.4143 | 2050.9469
DEER-SFAM-CZ14-V4-eSA-17-TM-s2 | 17 | CZ14 | V4 | CZ14-V4-eSA-17 | CZ14-V4-eSA-17-TM | 15.7671 | 3.5351 | 2322.4166 | 0 | 4.2 | 2322.4166 | 2338.0814
DEER-SFAM-CZ14-V4-eSA-18-LH-s2 | 18 | CZ14 | V4 | CZ14-V4-eSA-18 | CZ14-V4-eSA-18-LH | 14.3415 | 3.2074 | 2161.2724 | 0 | 3.8 | 2161.2724 | 2186.8975
DEER-SFAM-CZ14-V4-eSA-18-LL-s2 | 18 | CZ14 | V4 | CZ14-V4-eSA-18 | CZ14-V4-eSA-18-LL | 14.6581 | 3.2102 | 2114.4215 | 0 | 3.8 | 2114.4215 | 2147.8708
DEER-SFAM-CZ14-V4-eSA-18-TH-s2 | 18 | CZ14 | V4 | CZ14-V4-eSA-18 | CZ14-V4-eSA-18-TH | 15.141 | 3.3694 | 2251.8397 | 0 | 4.2 | 2251.8397 | 2272.1797
DEER-SFAM-CZ14-V4-eSA-18-TL-s2 | 18 | CZ14 | V4 | CZ14-V4-eSA-18 | CZ14-V4-eSA-18-TL | 14.802 | 3.7155 | 2402.6697 | 0 | 4.2 | 2402.6697 | 2424.8573
DEER-SFAM-CZ14-V4-eSA-18-TM-s2 | 18 | CZ14 | V4 | CZ14-V4-eSA-18 | CZ14-V4-eSA-18-TM | 14.2486 | 3.4231 | 2354.2184 | 0 | 3.8 | 2354.2184 | 2374.9676
DEER-SFAM-CZ14-V4-eSH-10-HH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-HH | 8.7581 | 4.6958 | 3459.7875 | 1817.7 | 4.2 | 5277.4875 | 3649.5875
DEER-SFAM-CZ14-V4-eSH-10-HL-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-HL | 8.553 | 4.9432 | 3544.5279 | 1803.0936 | 4.2 | 5347.6215 | 3725.4215
DEER-SFAM-CZ14-V4-eSH-10-HM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-HM | 8.7368 | 4.6292 | 3561.0582 | 1794.2405 | 3.8 | 5355.2987 | 3735.9987
DEER-SFAM-CZ14-V4-eSH-10-LH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-LH | 8.6805 | 4.3272 | 3607.5039 | 1867.4402 | 3.8 | 5474.9441 | 3803.5441
DEER-SFAM-CZ14-V4-eSH-10-LL-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-LL | 8.8386 | 4.6434 | 3475.9574 | 1914.5635 | 4.2 | 5390.5209 | 3681.1209
DEER-SFAM-CZ14-V4-eSH-10-LM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-LM | 8.9992 | 4.4346 | 3424.4451 | 1891.7116 | 4.2 | 5316.1567 | 3612.6567
DEER-SFAM-CZ14-V4-eSH-10-MH-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-MH | 8.761 | 4.5052 | 3604.9579 | 1880.0779 | 3.8 | 5485.0358 | 3812.7358
DEER-SFAM-CZ14-V4-eSH-10-ML-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-ML | 8.7461 | 4.898 | 3540.9336 | 1862.6838 | 4.2 | 5403.6174 | 3736.9174
DEER-SFAM-CZ14-V4-eSH-10-MM-s1 | 10 | CZ14 | V4 | CZ14-V4-eSH-10 | CZ14-V4-eSH-10-MM | 8.6923 | 4.553 | 3615.5958 | 1805.7451 | 3.8 | 5421.3409 | 3789.7409
DEER-SFAM-CZ14-V4-eSH-13-HH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-HH | 10.5365 | 4.1755 | 2921.6062 | 1765.5114 | 4.2 | 4687.1176 | 3095.6176
DEER-SFAM-CZ14-V4-eSH-13-HL-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-HL | 11.3555 | 4.1278 | 2751.01 | 1535.3242 | 4.2 | 4286.3342 | 2924.3342
DEER-SFAM-CZ14-V4-eSH-13-HM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-HM | 10.8808 | 4.021 | 2829.4826 | 1592.1036 | 4.2 | 4421.5862 | 2987.6862
DEER-SFAM-CZ14-V4-eSH-13-LH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-LH | 10.724 | 3.6567 | 2880.9732 | 1836.042 | 3.8 | 4717.0152 | 3140.4152
DEER-SFAM-CZ14-V4-eSH-13-LL-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-LL | 11.7918 | 3.7149 | 2616.912 | 1594.6744 | 4.2 | 4211.5864 | 2776.8864
DEER-SFAM-CZ14-V4-eSH-13-LM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-LM | 10.0674 | 3.8733 | 3005.8149 | 1345.6246 | 3.8 | 4351.4395 | 3183.0395
DEER-SFAM-CZ14-V4-eSH-13-MH-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-MH | 11.319 | 3.7813 | 2698.5 | 1796.9434 | 4.2 | 4495.4434 | 2868.2434
DEER-SFAM-CZ14-V4-eSH-13-ML-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-ML | 10.0655 | 4.0774 | 3080.9086 | 1608.1504 | 3.8 | 4689.059 | 3255.959
DEER-SFAM-CZ14-V4-eSH-13-MM-s1 | 13 | CZ14 | V4 | CZ14-V4-eSH-13 | CZ14-V4-eSH-13-MM | 10.9904 | 4.0415 | 2835.0396 | 1651.7536 | 4.2 | 4486.7932 | 2970.3932
DEER-SFAM-CZ14-V4-eSH-14-HH-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-HH | 11.2636 | 3.9958 | 2741.9315 | 1626.0482 | 4.2 | 4367.9797 | 2874.5797
DEER-SFAM-CZ14-V4-eSH-14-HL-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-HL | 11.8675 | 3.8324 | 2604.3267 | 1594.8772 | 4.2 | 4199.2039 | 2762.4039
DEER-SFAM-CZ14-V4-eSH-14-HM-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-HM | 11.8311 | 3.709 | 2604.6497 | 1624.7506 | 4.2 | 4229.4003 | 2719.5003
DEER-SFAM-CZ14-V4-eSH-14-MH-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-MH | 11.5269 | 3.4579 | 2669.9905 | 1727.8237 | 3.8 | 4397.8142 | 2846.4142
DEER-SFAM-CZ14-V4-eSH-14-ML-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-ML | 11.8327 | 3.7033 | 2584.8005 | 1732.5349 | 4.2 | 4317.3354 | 2801.0354
DEER-SFAM-CZ14-V4-eSH-14-MM-s1 | 14 | CZ14 | V4 | CZ14-V4-eSH-14 | CZ14-V4-eSH-14-MM | 11.4741 | 3.6442 | 2655.2682 | 1558.1759 | 3.8 | 4213.4441 | 2803.3441
DEER-SFAM-CZ14-V4-eSH-15-HH-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-HH | 12.7343 | 3.4205 | 2434.7154 | 1767.1392 | 4.2 | 4201.8546 | 2557.9546
DEER-SFAM-CZ14-V4-eSH-15-HL-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-HL | 12.9671 | 3.5414 | 2432.7187 | 1390.9179 | 4.2 | 3823.6366 | 2553.4366
DEER-SFAM-CZ14-V4-eSH-15-HM-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-HM | 12.8718 | 3.4065 | 2357.6121 | 1458.9499 | 4.2 | 3816.562 | 2476.462
DEER-SFAM-CZ14-V4-eSH-15-MH-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-MH | 11.8788 | 3.6236 | 2593.0444 | 1570.7601 | 4.2 | 4163.8045 | 2708.4045
DEER-SFAM-CZ14-V4-eSH-15-ML-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-ML | 12.7062 | 3.4953 | 2409.6891 | 1547.2135 | 4.2 | 3956.9026 | 2531.8026
DEER-SFAM-CZ14-V4-eSH-15-MM-s1 | 15 | CZ14 | V4 | CZ14-V4-eSH-15 | CZ14-V4-eSH-15-MM | 13.0745 | 3.3729 | 2336.3473 | 1678.0964 | 4.2 | 4014.4437 | 2467.9437
DEER-SFAM-CZ14-V4-eSH-16-CH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-CH | 14.0308 | 3.5389 | 2465.5837 | 1784.3933 | 4.2 | 4249.977 | 2592.477
DEER-SFAM-CZ14-V4-eSH-16-CL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-CL | 14.2719 | 3.6014 | 2480.3278 | 1667.3616 | 4.2 | 4147.6894 | 2610.0894
DEER-SFAM-CZ14-V4-eSH-16-LH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-LH | 13.0171 | 3.3896 | 2361.0638 | 1731.3201 | 3.8 | 4092.3839 | 2484.7839
DEER-SFAM-CZ14-V4-eSH-16-LL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-LL | 12.8607 | 3.5511 | 2419.0882 | 1614.0985 | 3.8 | 4033.1867 | 2518.6867
DEER-SFAM-CZ14-V4-eSH-16-LM-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-LM | 12.523 | 3.5387 | 2465.4241 | 1733.3499 | 3.8 | 4198.774 | 2603.574
DEER-SFAM-CZ14-V4-eSH-16-TH-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-TH | 14.2619 | 3.7121 | 2387.5164 | 2258.4158 | 4.2 | 4645.9322 | 2524.5322
DEER-SFAM-CZ14-V4-eSH-16-TL-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-TL | 13.1787 | 3.9273 | 2656.592 | 2174.7467 | 3.8 | 4831.3387 | 2788.1387
DEER-SFAM-CZ14-V4-eSH-16-TM-s2 | 16 | CZ14 | V4 | CZ14-V4-eSH-16 | CZ14-V4-eSH-16-TM | 13.4037 | 3.9781 | 2630.2938 | 2201.3626 | 4.2 | 4831.6564 | 2757.7564
DEER-SFAM-CZ14-V4-eSH-17-CM-s2 | 17 | CZ14 | V4 | CZ14-V4-eSH-17 | CZ14-V4-eSH-17-CM | 15.0341 | 3.4313 | 2353.2037 | 1607.2697 | 4.2 | 3960.4734 | 2471.2734
DEER-SFAM-CZ14-V4-eSH-17-LM-s2 | 17 | CZ14 | V4 | CZ14-V4-eSH-17 | CZ14-V4-eSH-17-LM | 13.4944 | 3.4711 | 2351.8294 | 1560.5082 | 3.8 | 3912.3376 | 2407.5376
DEER-SFAM-CZ14-V4-eSH-17-TH-s2 | 17 | CZ14 | V4 | CZ14-V4-eSH-17 | CZ14-V4-eSH-17-TH | 14.6898 | 3.5739 | 2304.8378 | 2263.3546 | 4.2 | 4568.1924 | 2454.2924
DEER-SFAM-CZ14-V4-eSH-17-TL-s2 | 17 | CZ14 | V4 | CZ14-V4-eSH-17 | CZ14-V4-eSH-17-TL | 14.7568 | 3.6438 | 2309.7482 | 2248.2991 | 4.2 | 4558.0473 | 2456.7473
DEER-SFAM-CZ14-V4-eSH-18-LH-s2 | 18 | CZ14 | V4 | CZ14-V4-eSH-18 | CZ14-V4-eSH-18-LH | 13.7876 | 3.3448 | 2267.8225 | 1804.736 | 3.8 | 4072.5585 | 2363.1585
DEER-SFAM-CZ14-V4-eSH-18-LL-s2 | 18 | CZ14 | V4 | CZ14-V4-eSH-18 | CZ14-V4-eSH-18-LL | 13.1333 | 3.4874 | 2359.5978 | 1613.2698 | 3.8 | 3972.8676 | 2445.7676
DEER-SFAM-CZ14-V4-eSH-18-LM-s2 | 18 | CZ14 | V4 | CZ14-V4-eSH-18 | CZ14-V4-eSH-18-LM | 14.1826 | 3.3502 | 2207.2841 | 1886.6458 | 3.8 | 4093.9299 | 2317.1299
DEER-SFAM-CZ14-V4-eSH-18-TM-s2 | 18 | CZ14 | V4 | CZ14-V4-eSH-18 | CZ14-V4-eSH-18-TM | 14.641 | 3.4836 | 2421.7717 | 2278.3534 | 3.8 | 4700.1251 | 2656.0251
DEER-SFAM-CZ15-V1-eSA-10-HH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-HH | 9.1216 | 5.4089 | 10330.5189 | 0 | 4.0811 | 10330.5189 | 10383.3937
DEER-SFAM-CZ15-V1-eSA-10-HL-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-HL | 8.126 | 6.1579 | 11114.1175 | 0 | 4.0811 | 11114.1175 | 11167.0342
DEER-SFAM-CZ15-V1-eSA-10-HM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-HM | 8.2788 | 5.814 | 10640.5426 | 0 | 4.0811 | 10640.5426 | 10693.4523
DEER-SFAM-CZ15-V1-eSA-10-LH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-LH | 10.0197 | 4.9983 | 9972.6196 | 0 | 4.0811 | 9972.6196 | 10025.5819
DEER-SFAM-CZ15-V1-eSA-10-LL-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-LL | 8.7967 | 5.3412 | 10340.0977 | 0 | 4.0811 | 10340.0977 | 10393.0252
DEER-SFAM-CZ15-V1-eSA-10-LM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-LM | 9.8361 | 5.0516 | 10035.6754 | 0 | 4.0811 | 10035.6754 | 10088.6399
DEER-SFAM-CZ15-V1-eSA-10-MH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-MH | 10.1225 | 4.3152 | 9535.0433 | 0 | 3.6217 | 9535.0433 | 9587.9432
DEER-SFAM-CZ15-V1-eSA-10-ML-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-ML | 8.6328 | 5.4481 | 10617.4794 | 0 | 4.0811 | 10617.4794 | 10670.3973
DEER-SFAM-CZ15-V1-eSA-10-MM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSA-10 | CZ15-V1-eSA-10-MM | 9.3735 | 4.5852 | 9834.6717 | 0 | 3.6217 | 9834.6717 | 9887.5461
DEER-SFAM-CZ15-V1-eSA-13-HH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-HH | 11.0645 | 4.6827 | 8279.4081 | 0 | 4.0811 | 8279.4081 | 8327.1095
DEER-SFAM-CZ15-V1-eSA-13-HL-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-HL | 10.9394 | 5.0417 | 8613.6436 | 0 | 4.0811 | 8613.6436 | 8655.391
DEER-SFAM-CZ15-V1-eSA-13-HM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-HM | 10.7715 | 4.7988 | 8299.8083 | 0 | 4.0811 | 8299.8083 | 8347.4931
DEER-SFAM-CZ15-V1-eSA-13-LH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-LH | 12.3668 | 4.1903 | 7718.3586 | 0 | 4.0811 | 7718.3586 | 7771.2893
DEER-SFAM-CZ15-V1-eSA-13-LL-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-LL | 11.4452 | 4.5638 | 8222.6102 | 0 | 4.0811 | 8222.6102 | 8275.4374
DEER-SFAM-CZ15-V1-eSA-13-LM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-LM | 11.7414 | 3.8164 | 7858.4606 | 0 | 3.6217 | 7858.4606 | 7911.2951
DEER-SFAM-CZ15-V1-eSA-13-MH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-MH | 11.3759 | 4.523 | 8071.0331 | 0 | 4.0811 | 8071.0331 | 8123.9428
DEER-SFAM-CZ15-V1-eSA-13-ML-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-ML | 10.4844 | 4.7496 | 8371.0212 | 0 | 4.0811 | 8371.0212 | 8423.7675
DEER-SFAM-CZ15-V1-eSA-13-MM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSA-13 | CZ15-V1-eSA-13-MM | 11.5599 | 5.1703 | 8093.9444 | 0 | 4.5406 | 8093.9444 | 8146.8879
DEER-SFAM-CZ15-V1-eSA-14-HH-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-HH | 10.8619 | 4.5259 | 8091.2606 | 0 | 4.0811 | 8091.2606 | 8135.6051
DEER-SFAM-CZ15-V1-eSA-14-HL-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-HL | 11.6402 | 4.6023 | 7825.8552 | 0 | 4.0811 | 7825.8552 | 7858.4643
DEER-SFAM-CZ15-V1-eSA-14-HM-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-HM | 11.8433 | 4.5488 | 8086.0777 | 0 | 4.0811 | 8086.0777 | 8136.107
DEER-SFAM-CZ15-V1-eSA-14-MH-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-MH | 12.846 | 3.5476 | 7373.1981 | 0 | 3.6217 | 7373.1981 | 7407.9263
DEER-SFAM-CZ15-V1-eSA-14-ML-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-ML | 11.8934 | 4.4568 | 7844.1834 | 0 | 4.0811 | 7844.1834 | 7899.7045
DEER-SFAM-CZ15-V1-eSA-14-MM-s1 | 14 | CZ15 | V1 | CZ15-V1-eSA-14 | CZ15-V1-eSA-14-MM | 12.538 | 3.5788 | 7356.5774 | 0 | 3.6217 | 7356.5774 | 7394.6551
DEER-SFAM-CZ15-V1-eSA-15-HH-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-HH | 12.2752 | 4.26 | 7290.5965 | 0 | 4.0811 | 7290.5965 | 7327.5651
DEER-SFAM-CZ15-V1-eSA-15-HL-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-HL | 12.1746 | 4.8938 | 7354.2224 | 0 | 4.5406 | 7354.2224 | 7400.3325
DEER-SFAM-CZ15-V1-eSA-15-HM-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-HM | 12.4791 | 4.1249 | 7126.9495 | 0 | 4.0811 | 7126.9495 | 7164.0543
DEER-SFAM-CZ15-V1-eSA-15-MH-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-MH | 12.5524 | 4.2537 | 7527.9767 | 0 | 4.0811 | 7527.9767 | 7555.5236
DEER-SFAM-CZ15-V1-eSA-15-ML-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-ML | 12.7891 | 4.1872 | 7289.034 | 0 | 4.0811 | 7289.034 | 7326.0754
DEER-SFAM-CZ15-V1-eSA-15-MM-s1 | 15 | CZ15 | V1 | CZ15-V1-eSA-15 | CZ15-V1-eSA-15-MM | 12.8333 | 4.2232 | 7328.4725 | 0 | 4.0811 | 7328.4725 | 7362.2502
DEER-SFAM-CZ15-V1-eSA-16-CH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-CH | 12.8761 | 4.1267 | 8290.6106 | 0 | 4.0811 | 8290.6106 | 8311.7559
DEER-SFAM-CZ15-V1-eSA-16-CL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-CL | 12.4728 | 4.3762 | 8067.9879 | 0 | 4.0811 | 8067.9879 | 8094.8716
DEER-SFAM-CZ15-V1-eSA-16-CM-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-CM | 12.4317 | 4.3255 | 8204.3736 | 0 | 4.0811 | 8204.3736 | 8232.7785
DEER-SFAM-CZ15-V1-eSA-16-LH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-LH | 12.5989 | 4.1531 | 7443.8513 | 0 | 4.0811 | 7443.8513 | 7480.1745
DEER-SFAM-CZ15-V1-eSA-16-LL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-LL | 12.0375 | 4.4421 | 7969.8012 | 0 | 4.0811 | 7969.8012 | 7993.6802
DEER-SFAM-CZ15-V1-eSA-16-LM-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-LM | 12.2601 | 4.2496 | 7817.0168 | 0 | 4.0811 | 7817.0168 | 7838.653
DEER-SFAM-CZ15-V1-eSA-16-NM-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-NM | 13.2783 | 4.0087 | 7189.4514 | 0 | 4.0811 | 7189.4514 | 7210.679
DEER-SFAM-CZ15-V1-eSA-16-TH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-TH | 11.6533 | 4.8364 | 8889.6744 | 0 | 4.0811 | 8889.6744 | 8903.136
DEER-SFAM-CZ15-V1-eSA-16-TL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSA-16 | CZ15-V1-eSA-16-TL | 12.3345 | 5.1707 | 8411.3439 | 0 | 4.5406 | 8411.3439 | 8425.9115
DEER-SFAM-CZ15-V1-eSA-17-CH-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-CH | 13.3475 | 4.0525 | 7824.6824 | 0 | 4.0811 | 7824.6824 | 7851.55
DEER-SFAM-CZ15-V1-eSA-17-CL-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-CL | 13.0535 | 4.1409 | 7836.6186 | 0 | 4.0811 | 7836.6186 | 7863.4802
DEER-SFAM-CZ15-V1-eSA-17-CM-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-CM | 13.1892 | 4.1152 | 7889.8169 | 0 | 4.0811 | 7889.8169 | 7910.8979
DEER-SFAM-CZ15-V1-eSA-17-LH-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-LH | 12.9632 | 3.6065 | 7081.6171 | 0 | 3.6217 | 7081.6171 | 7110.058
DEER-SFAM-CZ15-V1-eSA-17-LL-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-LL | 12.6271 | 4.2527 | 7712.194 | 0 | 4.0811 | 7712.194 | 7727.6888
DEER-SFAM-CZ15-V1-eSA-17-LM-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-LM | 12.4829 | 4.2532 | 7615.4136 | 0 | 4.0811 | 7615.4136 | 7628.8075
DEER-SFAM-CZ15-V1-eSA-17-TH-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-TH | 13.3245 | 4.1192 | 7547.8309 | 0 | 4.0811 | 7547.8309 | 7569.4205
DEER-SFAM-CZ15-V1-eSA-17-TL-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-TL | 13.0444 | 4.4002 | 7329.2214 | 0 | 4.0811 | 7329.2214 | 7363.2632
DEER-SFAM-CZ15-V1-eSA-17-TM-s2 | 17 | CZ15 | V1 | CZ15-V1-eSA-17 | CZ15-V1-eSA-17-TM | 13.8189 | 4.7119 | 8531.4606 | 0 | 4.5406 | 8531.4606 | 8542.6648
DEER-SFAM-CZ15-V1-eSA-18-LH-s2 | 18 | CZ15 | V1 | CZ15-V1-eSA-18 | CZ15-V1-eSA-18-LH | 13.4341 | 3.9631 | 7153.9982 | 0 | 4.0811 | 7153.9982 | 7172.6569
DEER-SFAM-CZ15-V1-eSA-18-LL-s2 | 18 | CZ15 | V1 | CZ15-V1-eSA-18 | CZ15-V1-eSA-18-LL | 13.4169 | 3.9783 | 7042.9454 | 0 | 4.0811 | 7042.9454 | 7067.3041
DEER-SFAM-CZ15-V1-eSA-18-TH-s2 | 18 | CZ15 | V1 | CZ15-V1-eSA-18 | CZ15-V1-eSA-18-TH | 14.0942 | 3.9574 | 7204.427 | 0 | 4.0811 | 7204.427 | 7219.1081
DEER-SFAM-CZ15-V1-eSA-18-TL-s2 | 18 | CZ15 | V1 | CZ15-V1-eSA-18 | CZ15-V1-eSA-18-TL | 13.4 | 4.2954 | 7953.6625 | 0 | 4.0811 | 7953.6625 | 7969.7775
DEER-SFAM-CZ15-V1-eSA-18-TM-s2 | 18 | CZ15 | V1 | CZ15-V1-eSA-18 | CZ15-V1-eSA-18-TM | 13.4281 | 4.0789 | 7464.4849 | 0 | 4.0811 | 7464.4849 | 7479.4849
DEER-SFAM-CZ15-V1-eSH-10-HH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-HH | 9.1342 | 5.472 | 10000.8891 | 1141.4841 | 4.0811 | 11142.3732 | 10122.4879
DEER-SFAM-CZ15-V1-eSH-10-HL-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-HL | 8.7006 | 5.742 | 10468.0609 | 1150.6206 | 4.0811 | 11618.6815 | 10587.9442
DEER-SFAM-CZ15-V1-eSH-10-HM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-HM | 9.0165 | 5.6359 | 10382.832 | 1106.1731 | 4.0811 | 11489.0051 | 10497.9848
DEER-SFAM-CZ15-V1-eSH-10-LH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-LH | 9.9072 | 5.0366 | 9754.0089 | 1202.181 | 4.0811 | 10956.1899 | 9879.4253
DEER-SFAM-CZ15-V1-eSH-10-LL-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-LL | 9.0793 | 5.3504 | 10160.8586 | 1159.2371 | 4.0811 | 11320.0957 | 10291.534
DEER-SFAM-CZ15-V1-eSH-10-LM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-LM | 9.4203 | 5.1497 | 9808.6866 | 1145.7475 | 4.0811 | 10954.4341 | 9928.0215
DEER-SFAM-CZ15-V1-eSH-10-MH-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-MH | 9.8232 | 5.2827 | 10037.8398 | 1188.3801 | 4.0811 | 11226.2199 | 10171.1581
DEER-SFAM-CZ15-V1-eSH-10-ML-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-ML | 8.8686 | 5.6975 | 10507.9053 | 1083.1354 | 4.0811 | 11591.0407 | 10628.2233
DEER-SFAM-CZ15-V1-eSH-10-MM-s1 | 10 | CZ15 | V1 | CZ15-V1-eSH-10 | CZ15-V1-eSH-10-MM | 9.256 | 5.451 | 10358.6243 | 1152.1965 | 4.0811 | 11510.8208 | 10471.0562
DEER-SFAM-CZ15-V1-eSH-13-HH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-HH | 10.2541 | 4.9835 | 8620.6468 | 1090.1628 | 4.0811 | 9710.8095 | 8731.4921
DEER-SFAM-CZ15-V1-eSH-13-HL-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-HL | 11.5259 | 5.542 | 8413.058 | 947.0124 | 4.5406 | 9360.0705 | 8523.472
DEER-SFAM-CZ15-V1-eSH-13-HM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-HM | 10.492 | 4.8403 | 8433.6124 | 973.1784 | 4.0811 | 9406.7908 | 8533.2998
DEER-SFAM-CZ15-V1-eSH-13-LH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-LH | 12.2301 | 4.1579 | 7870.7885 | 1160.926 | 4.0811 | 9031.7146 | 8039.2613
DEER-SFAM-CZ15-V1-eSH-13-LL-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-LL | 11.9205 | 4.4081 | 7813.6124 | 1000.0191 | 4.0811 | 8813.6315 | 7915.0046
DEER-SFAM-CZ15-V1-eSH-13-LM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-LM | 11.4674 | 3.8935 | 8001.5296 | 874.1845 | 3.6217 | 8875.7141 | 8116.2119
DEER-SFAM-CZ15-V1-eSH-13-MH-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-MH | 11.3755 | 5.0328 | 8018.3245 | 1119.9488 | 4.5406 | 9138.2733 | 8130.0644
DEER-SFAM-CZ15-V1-eSH-13-ML-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-ML | 10.9678 | 4.7876 | 8602.4453 | 1031.828 | 4.0811 | 9634.2732 | 8716.7945
DEER-SFAM-CZ15-V1-eSH-13-MM-s1 | 13 | CZ15 | V1 | CZ15-V1-eSH-13 | CZ15-V1-eSH-13-MM | 11.0596 | 4.8349 | 8360.1829 | 1023.9902 | 4.0811 | 9384.1732 | 8448.5728
DEER-SFAM-CZ15-V1-eSH-14-HH-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-HH | 10.7981 | 4.8019 | 8190.3688 | 994.0979 | 4.0811 | 9184.4667 | 8274.6776
DEER-SFAM-CZ15-V1-eSH-14-HL-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-HL | 11.1539 | 4.6378 | 7940.588 | 980.0461 | 4.0811 | 8920.634 | 8042.3855
DEER-SFAM-CZ15-V1-eSH-14-HM-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-HM | 11.3343 | 4.4872 | 7779.717 | 974.0604 | 4.0811 | 8753.7774 | 7851.9072
DEER-SFAM-CZ15-V1-eSH-14-MH-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-MH | 12.9545 | 3.9822 | 7361.7556 | 1047.4472 | 4.0811 | 8409.2028 | 7472.4533
DEER-SFAM-CZ15-V1-eSH-14-ML-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-ML | 12.3227 | 4.4252 | 7649.392 | 1105.5007 | 4.0811 | 8754.8927 | 7789.8583
DEER-SFAM-CZ15-V1-eSH-14-MM-s1 | 14 | CZ15 | V1 | CZ15-V1-eSH-14 | CZ15-V1-eSH-14-MM | 12.484 | 4.2645 | 7572.5504 | 959.3811 | 4.0811 | 8531.9315 | 7668.1566
DEER-SFAM-CZ15-V1-eSH-15-HH-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-HH | 12.3144 | 4.1396 | 7181.3365 | 1160.2328 | 4.0811 | 8341.5693 | 7260.965
DEER-SFAM-CZ15-V1-eSH-15-HL-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-HL | 12.1863 | 4.2958 | 7351.385 | 842.9098 | 4.0811 | 8194.2948 | 7428.8869
DEER-SFAM-CZ15-V1-eSH-15-HM-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-HM | 12.4943 | 4.6839 | 7197.5804 | 870.5016 | 4.5406 | 8068.0819 | 7275.4844
DEER-SFAM-CZ15-V1-eSH-15-MH-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-MH | 12.9674 | 4.2213 | 7400.3423 | 1028.3314 | 4.0811 | 8428.6737 | 7476.3563
DEER-SFAM-CZ15-V1-eSH-15-ML-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-ML | 13.0628 | 4.26 | 7199.3047 | 963.2606 | 4.0811 | 8162.5653 | 7278.114
DEER-SFAM-CZ15-V1-eSH-15-MM-s1 | 15 | CZ15 | V1 | CZ15-V1-eSH-15 | CZ15-V1-eSH-15-MM | 12.6184 | 4.5087 | 7170.0544 | 1009.9046 | 4.5406 | 8179.959 | 7252.885
DEER-SFAM-CZ15-V1-eSH-16-CH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-CH | 12.557 | 4.2314 | 8071.5461 | 1094.7134 | 4.0811 | 9166.2595 | 8144.5393
DEER-SFAM-CZ15-V1-eSH-16-CL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-CL | 13.2076 | 4.2361 | 8330.3755 | 1012.7148 | 4.0811 | 9343.0904 | 8405.4523
DEER-SFAM-CZ15-V1-eSH-16-LH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-LH | 12.4117 | 4.1826 | 7538.9638 | 1157.395 | 4.0811 | 8696.3588 | 7620.083
DEER-SFAM-CZ15-V1-eSH-16-LL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-LL | 12.1056 | 3.8728 | 7659.9467 | 1066.0934 | 3.6217 | 8726.0401 | 7725.9143
DEER-SFAM-CZ15-V1-eSH-16-LM-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-LM | 12.1014 | 3.8288 | 7567.6664 | 1171.6506 | 3.6217 | 8739.317 | 7659.9873
DEER-SFAM-CZ15-V1-eSH-16-TH-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-TH | 12.5608 | 4.5449 | 8099.8181 | 1401.9844 | 4.0811 | 9501.8025 | 8178.2549
DEER-SFAM-CZ15-V1-eSH-16-TL-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-TL | 11.7681 | 4.7434 | 8880.3528 | 1392.8384 | 4.0811 | 10273.1913 | 8950.738
DEER-SFAM-CZ15-V1-eSH-16-TM-s2 | 16 | CZ15 | V1 | CZ15-V1-eSH-16 | CZ15-V1-eSH-16-TM | 11.9778 | 4.6521 | 8732.6613 | 1414.034 | 4.0811 | 10146.6953 | 8804.9986
DEER-SFAM-CZ15-V1-eSH-17-CM-s2 | 17 | CZ15 | V1 | CZ15-V1-eSH-17 | CZ15-V1-eSH-17-CM | 13.8803 | 4.0505 | 7908.7567 | 1127.0972 | 4.0811 | 9035.8539 | 7992.58
DEER-SFAM-CZ15-V1-eSH-17-LM-s2 | 17 | CZ15 | V1 | CZ15-V1-eSH-17 | CZ15-V1-eSH-17-LM | 13.212 | 4.1499 | 7687.9406 | 1020.6602 | 4.0811 | 8708.6008 | 7724.2042
DEER-SFAM-CZ15-V1-eSH-17-TH-s2 | 17 | CZ15 | V1 | CZ15-V1-eSH-17 | CZ15-V1-eSH-17-TH | 13.2515 | 4.2242 | 7638.9694 | 1402.3729 | 4.0811 | 9041.3423 | 7722.9164
DEER-SFAM-CZ15-V1-eSH-17-TL-s2 | 17 | CZ15 | V1 | CZ15-V1-eSH-17 | CZ15-V1-eSH-17-TL | 13.0974 | 4.3181 | 7763.4021 | 1393.8533 | 4.0811 | 9157.2554 | 7846.5324
DEER-SFAM-CZ15-V1-eSH-18-LH-s2 | 18 | CZ15 | V1 | CZ15-V1-eSH-18 | CZ15-V1-eSH-18-LH | 13.2708 | 3.5847 | 7032.7055 | 1217.0677 | 3.6217 | 8249.7732 | 7097.0379
DEER-SFAM-CZ15-V1-eSH-18-LL-s2 | 18 | CZ15 | V1 | CZ15-V1-eSH-18 | CZ15-V1-eSH-18-LL | 12.7 | 3.7061 | 7265.3024 | 1074.339 | 3.6217 | 8339.6414 | 7322.8938
DEER-SFAM-CZ15-V1-eSH-18-LM-s2 | 18 | CZ15 | V1 | CZ15-V1-eSH-18 | CZ15-V1-eSH-18-LM | 13.2875 | 3.6385 | 7084.2621 | 1293.7517 | 3.6217 | 8378.0138 | 7158.602
DEER-SFAM-CZ15-V1-eSH-18-TM-s2 | 18 | CZ15 | V1 | CZ15-V1-eSH-18 | CZ15-V1-eSH-18-TM | 13.5017 | 3.6386 | 7297.1172 | 1417.835 | 3.6217 | 8714.9522 | 7422.2443
DEER-SFAM-CZ15-V2-eSA-10-HH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-HH | 8.9905 | 4.2618 | 8166.3556 | 0 | 3.2375 | 8166.3556 | 8186.8491
DEER-SFAM-CZ15-V2-eSA-10-HL-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-HL | 8.0135 | 4.8798 | 8785.9432 | 0 | 3.2375 | 8785.9432 | 8806.4575
DEER-SFAM-CZ15-V2-eSA-10-HM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-HM | 8.1816 | 4.6074 | 8401.4732 | 0 | 3.2375 | 8401.4732 | 8421.9838
DEER-SFAM-CZ15-V2-eSA-10-LH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-LH | 9.7658 | 3.9593 | 7904.0832 | 0 | 3.2375 | 7904.0832 | 7924.6181
DEER-SFAM-CZ15-V2-eSA-10-LL-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-LL | 8.6703 | 4.2273 | 8180.1226 | 0 | 3.2375 | 8180.1226 | 8200.6422
DEER-SFAM-CZ15-V2-eSA-10-LM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-LM | 9.6185 | 3.9948 | 7948.5107 | 0 | 3.2375 | 7948.5107 | 7969.0465
DEER-SFAM-CZ15-V2-eSA-10-MH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-MH | 9.6901 | 3.8498 | 7849.6457 | 0 | 3.2375 | 7849.6457 | 7870.1739
DEER-SFAM-CZ15-V2-eSA-10-ML-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-ML | 8.487 | 4.3097 | 8413.282 | 0 | 3.2375 | 8413.282 | 8433.7974
DEER-SFAM-CZ15-V2-eSA-10-MM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSA-10 | CZ15-V2-eSA-10-MM | 9.1522 | 3.9676 | 8021.503 | 0 | 3.2375 | 8021.503 | 8042.0205
DEER-SFAM-CZ15-V2-eSA-13-HH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-HH | 10.937 | 3.7105 | 6552.9735 | 0 | 3.2375 | 6552.9735 | 6571.4665
DEER-SFAM-CZ15-V2-eSA-13-HL-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-HL | 10.8048 | 4.0072 | 6793.7062 | 0 | 3.2375 | 6793.7062 | 6809.8901
DEER-SFAM-CZ15-V2-eSA-13-HM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-HM | 10.4854 | 4.3089 | 6639.482 | 0 | 3.6782 | 6639.482 | 6657.988
DEER-SFAM-CZ15-V2-eSA-13-LH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-LH | 12.1267 | 3.3466 | 6112.0561 | 0 | 3.2375 | 6112.0561 | 6132.5773
DEER-SFAM-CZ15-V2-eSA-13-LL-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-LL | 11.2794 | 3.6127 | 6506.3575 | 0 | 3.2375 | 6506.3575 | 6526.8281
DEER-SFAM-CZ15-V2-eSA-13-LM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-LM | 11.3184 | 3.4142 | 6433.6001 | 0 | 3.2375 | 6433.6001 | 6454.1
DEER-SFAM-CZ15-V2-eSA-13-MH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-MH | 11.002 | 4.0785 | 6484.5302 | 0 | 3.6782 | 6484.5302 | 6505.0646
DEER-SFAM-CZ15-V2-eSA-13-ML-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-ML | 10.3811 | 3.7674 | 6596.118 | 0 | 3.2375 | 6596.118 | 6616.5636
DEER-SFAM-CZ15-V2-eSA-13-MM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSA-13 | CZ15-V2-eSA-13-MM | 11.3894 | 4.1665 | 6357.2617 | 0 | 3.6782 | 6357.2617 | 6377.7924
DEER-SFAM-CZ15-V2-eSA-14-HH-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-HH | 10.7138 | 3.5922 | 6389.3535 | 0 | 3.2375 | 6389.3535 | 6406.5431
DEER-SFAM-CZ15-V2-eSA-14-HL-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-HL | 11.3485 | 4.1236 | 6222.4098 | 0 | 3.6782 | 6222.4098 | 6235.065
DEER-SFAM-CZ15-V2-eSA-14-HM-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-HM | 11.5917 | 3.6203 | 6371.6192 | 0 | 3.2375 | 6371.6192 | 6391.0153
DEER-SFAM-CZ15-V2-eSA-14-MH-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-MH | 12.3141 | 3.1805 | 6056.8838 | 0 | 3.2375 | 6056.8838 | 6070.3585
DEER-SFAM-CZ15-V2-eSA-14-ML-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-ML | 11.749 | 3.5479 | 6206.5403 | 0 | 3.2375 | 6206.5403 | 6228.0636
DEER-SFAM-CZ15-V2-eSA-14-MM-s1 | 14 | CZ15 | V2 | CZ15-V2-eSA-14 | CZ15-V2-eSA-14-MM | 12.3405 | 2.757 | 5817.1412 | 0 | 2.7969 | 5817.1412 | 5831.8912
DEER-SFAM-CZ15-V2-eSA-15-HH-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-HH | 11.8713 | 3.8276 | 5866.0895 | 0 | 3.6782 | 5866.0895 | 5880.4375
DEER-SFAM-CZ15-V2-eSA-15-HL-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-HL | 12.0564 | 3.9447 | 5778.3489 | 0 | 3.6782 | 5778.3489 | 5796.2294
DEER-SFAM-CZ15-V2-eSA-15-HM-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-HM | 12.1388 | 3.6942 | 5710.7526 | 0 | 3.6782 | 5710.7526 | 5725.1531
DEER-SFAM-CZ15-V2-eSA-15-MH-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-MH | 12.2807 | 3.3851 | 5949.9438 | 0 | 3.2375 | 5949.9438 | 5960.6236
DEER-SFAM-CZ15-V2-eSA-15-ML-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-ML | 12.6431 | 3.3193 | 5752.0048 | 0 | 3.2375 | 5752.0048 | 5766.3577
DEER-SFAM-CZ15-V2-eSA-15-MM-s1 | 15 | CZ15 | V2 | CZ15-V2-eSA-15 | CZ15-V2-eSA-15-MM | 12.5903 | 3.358 | 5776.6332 | 0 | 3.2375 | 5776.6332 | 5789.7285
DEER-SFAM-CZ15-V2-eSA-16-CH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-CH | 12.7763 | 3.2891 | 6484.1106 | 0 | 3.2375 | 6484.1106 | 6492.4531
DEER-SFAM-CZ15-V2-eSA-16-CL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-CL | 12.5489 | 3.9505 | 6363.9731 | 0 | 3.6782 | 6363.9731 | 6374.555
DEER-SFAM-CZ15-V2-eSA-16-CM-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-CM | 12.3632 | 3.9068 | 6550.7287 | 0 | 3.6782 | 6550.7287 | 6561.9088
DEER-SFAM-CZ15-V2-eSA-16-LH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-LH | 12.585 | 3.273 | 5779.9633 | 0 | 3.2375 | 5779.9633 | 5794.1885
DEER-SFAM-CZ15-V2-eSA-16-LL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-LL | 11.9999 | 3.5035 | 6188.2659 | 0 | 3.2375 | 6188.2659 | 6197.6018
DEER-SFAM-CZ15-V2-eSA-16-LM-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-LM | 12.1782 | 3.3525 | 6087.2439 | 0 | 3.2375 | 6087.2439 | 6095.7064
DEER-SFAM-CZ15-V2-eSA-16-NM-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-NM | 13.3658 | 3.1661 | 5532.6813 | 0 | 3.2375 | 5532.6813 | 5540.9906
DEER-SFAM-CZ15-V2-eSA-16-TH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-TH | 11.6596 | 3.8509 | 6882.844 | 0 | 3.2375 | 6882.844 | 6888.1897
DEER-SFAM-CZ15-V2-eSA-16-TL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSA-16 | CZ15-V2-eSA-16-TL | 12.486 | 4.1793 | 6441.8587 | 0 | 3.6782 | 6441.8587 | 6447.6259
DEER-SFAM-CZ15-V2-eSA-17-CH-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-CH | 13.2625 | 3.2197 | 6105.4881 | 0 | 3.2375 | 6105.4881 | 6116.0477
DEER-SFAM-CZ15-V2-eSA-17-CL-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-CL | 13.0062 | 3.2878 | 6088.1944 | 0 | 3.2375 | 6088.1944 | 6098.7514
DEER-SFAM-CZ15-V2-eSA-17-CM-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-CM | 13.1366 | 3.2674 | 6137.1009 | 0 | 3.2375 | 6137.1009 | 6145.4185
DEER-SFAM-CZ15-V2-eSA-17-LH-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-LH | 12.8477 | 3.1854 | 5684.0545 | 0 | 3.2375 | 5684.0545 | 5695.1991
DEER-SFAM-CZ15-V2-eSA-17-LL-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-LL | 12.5605 | 3.3536 | 5992.6096 | 0 | 3.2375 | 5992.6096 | 5998.6722
DEER-SFAM-CZ15-V2-eSA-17-LM-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-LM | 12.4783 | 3.3614 | 5909.6126 | 0 | 3.2375 | 5909.6126 | 5914.8499
DEER-SFAM-CZ15-V2-eSA-17-TH-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-TH | 13.2477 | 3.2736 | 5892.2287 | 0 | 3.2375 | 5892.2287 | 5900.7651
DEER-SFAM-CZ15-V2-eSA-17-TL-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-TL | 13.3873 | 3.9331 | 5718.6921 | 0 | 3.6782 | 5718.6921 | 5732.1421
DEER-SFAM-CZ15-V2-eSA-17-TM-s2 | 17 | CZ15 | V2 | CZ15-V2-eSA-17 | CZ15-V2-eSA-17-TM | 13.7119 | 3.8109 | 6635.6233 | 0 | 3.6782 | 6635.6233 | 6640.0811
DEER-SFAM-CZ15-V2-eSA-18-LH-s2 | 18 | CZ15 | V2 | CZ15-V2-eSA-18 | CZ15-V2-eSA-18-LH | 13.3763 | 3.1294 | 5559.4975 | 0 | 3.2375 | 5559.4975 | 5566.7952
DEER-SFAM-CZ15-V2-eSA-18-LL-s2 | 18 | CZ15 | V2 | CZ15-V2-eSA-18 | CZ15-V2-eSA-18-LL | 13.4182 | 3.1382 | 5462.926 | 0 | 3.2375 | 5462.926 | 5472.4559
DEER-SFAM-CZ15-V2-eSA-18-TH-s2 | 18 | CZ15 | V2 | CZ15-V2-eSA-18 | CZ15-V2-eSA-18-TH | 13.947 | 3.5795 | 5803.6555 | 0 | 3.6782 | 5803.6555 | 5809.4601
DEER-SFAM-CZ15-V2-eSA-18-TL-s2 | 18 | CZ15 | V2 | CZ15-V2-eSA-18 | CZ15-V2-eSA-18-TL | 13.3392 | 3.4248 | 6211.0118 | 0 | 3.2375 | 6211.0118 | 6217.3961
DEER-SFAM-CZ15-V2-eSA-18-TM-s2 | 18 | CZ15 | V2 | CZ15-V2-eSA-18 | CZ15-V2-eSA-18-TM | 13.3686 | 3.2461 | 5816.1363 | 0 | 3.2375 | 5816.1363 | 5822.0629
DEER-SFAM-CZ15-V2-eSH-10-HH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-HH | 8.7596 | 4.9157 | 8077.4597 | 450.5706 | 3.6782 | 8528.0303 | 8124.5918
DEER-SFAM-CZ15-V2-eSH-10-HL-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-HL | 8.4079 | 5.1638 | 8408.0859 | 450.4298 | 3.6782 | 8858.5157 | 8454.3397
DEER-SFAM-CZ15-V2-eSH-10-HM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-HM | 8.8668 | 4.4562 | 8201.3948 | 435.5494 | 3.2375 | 8636.9442 | 8245.8275
DEER-SFAM-CZ15-V2-eSH-10-LH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-LH | 9.6937 | 3.9842 | 7751.7737 | 470.0013 | 3.2375 | 8221.775 | 7800.233
DEER-SFAM-CZ15-V2-eSH-10-LL-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-LL | 8.9531 | 4.2335 | 8008.4698 | 453.6761 | 3.2375 | 8462.1459 | 8059.1135
DEER-SFAM-CZ15-V2-eSH-10-LM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-LM | 9.2691 | 4.075 | 7752.335 | 451.5291 | 3.2375 | 8203.8641 | 7798.6536
DEER-SFAM-CZ15-V2-eSH-10-MH-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-MH | 9.6038 | 4.1799 | 7953.7736 | 463.9392 | 3.2375 | 8417.7128 | 8005.2647
DEER-SFAM-CZ15-V2-eSH-10-ML-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-ML | 8.6072 | 5.129 | 8394.6912 | 427.0358 | 3.6782 | 8821.727 | 8441.62
DEER-SFAM-CZ15-V2-eSH-10-MM-s1 | 10 | CZ15 | V2 | CZ15-V2-eSH-10 | CZ15-V2-eSH-10-MM | 9.081 | 4.3026 | 8186.4686 | 449.3103 | 3.2375 | 8635.7788 | 8230.0089
DEER-SFAM-CZ15-V2-eSH-13-HH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-HH | 10.1384 | 3.9579 | 6819.6279 | 427.4957 | 3.2375 | 7247.1237 | 6862.5415
DEER-SFAM-CZ15-V2-eSH-13-HL-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-HL | 11.332 | 4.471 | 6613.2825 | 369.4807 | 3.6782 | 6982.7632 | 6656.0661
DEER-SFAM-CZ15-V2-eSH-13-HM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-HM | 10.209 | 4.3382 | 6772.839 | 384.26 | 3.6782 | 7157.099 | 6811.5705
DEER-SFAM-CZ15-V2-eSH-13-LH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-LH | 11.9494 | 3.3121 | 6251.8997 | 446.6692 | 3.2375 | 6698.569 | 6316.7588
DEER-SFAM-CZ15-V2-eSH-13-LL-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-LL | 11.7259 | 3.4942 | 6168.1785 | 389.3886 | 3.2375 | 6557.5671 | 6207.5041
DEER-SFAM-CZ15-V2-eSH-13-LM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-LM | 11.0511 | 3.4939 | 6549.7449 | 340.5554 | 3.2375 | 6890.3003 | 6594.0878
DEER-SFAM-CZ15-V2-eSH-13-MH-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-MH | 11.1616 | 4.0601 | 6344.2989 | 440.9966 | 3.6782 | 6785.2955 | 6387.3915
DEER-SFAM-CZ15-V2-eSH-13-ML-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-ML | 10.7767 | 3.7996 | 6819.9531 | 396.7585 | 3.2375 | 7216.7116 | 6864.0298
DEER-SFAM-CZ15-V2-eSH-13-MM-s1 | 13 | CZ15 | V2 | CZ15-V2-eSH-13 | CZ15-V2-eSH-13-MM | 10.9286 | 3.8334 | 6590.9232 | 400.2733 | 3.2375 | 6991.1965 | 6625.0645
DEER-SFAM-CZ15-V2-eSH-14-HH-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-HH | 10.6881 | 3.8143 | 6472.2151 | 389.2544 | 3.2375 | 6861.4695 | 6504.872
DEER-SFAM-CZ15-V2-eSH-14-HL-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-HL | 10.9274 | 4.1557 | 6325.056 | 381.8549 | 3.6782 | 6706.9109 | 6364.4417
DEER-SFAM-CZ15-V2-eSH-14-HM-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-HM | 11.0351 | 4.0143 | 6236.3633 | 383.5978 | 3.6782 | 6619.9611 | 6264.398
DEER-SFAM-CZ15-V2-eSH-14-MH-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-MH | 12.6775 | 3.1761 | 5844.6303 | 406.3232 | 3.2375 | 6250.9535 | 5887.4748
DEER-SFAM-CZ15-V2-eSH-14-ML-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-ML | 11.8705 | 3.9874 | 6090.2767 | 419.4296 | 3.6782 | 6509.7063 | 6144.4057
DEER-SFAM-CZ15-V2-eSH-14-MM-s1 | 14 | CZ15 | V2 | CZ15-V2-eSH-14 | CZ15-V2-eSH-14-MM | 12.2543 | 3.4018 | 5990.8144 | 372.6198 | 3.2375 | 6363.4342 | 6027.7026
DEER-SFAM-CZ15-V2-eSH-15-HH-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-HH | 11.9489 | 3.7038 | 5767.166 | 441.3498 | 3.6782 | 6208.5158 | 5797.9586
DEER-SFAM-CZ15-V2-eSH-15-HL-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-HL | 11.9201 | 3.8414 | 5873.5126 | 331.3567 | 3.6782 | 6204.8693 | 5903.5381
DEER-SFAM-CZ15-V2-eSH-15-HM-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-HM | 12.3361 | 3.7724 | 5669.3769 | 343.395 | 3.6782 | 6012.7718 | 5699.4061
DEER-SFAM-CZ15-V2-eSH-15-MH-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-MH | 12.6846 | 3.3575 | 5828.1895 | 392.056 | 3.2375 | 6220.2455 | 5857.3856
DEER-SFAM-CZ15-V2-eSH-15-ML-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-ML | 12.6189 | 3.8266 | 5716.9981 | 369.975 | 3.6782 | 6086.9731 | 5747.4196
DEER-SFAM-CZ15-V2-eSH-15-MM-s1 | 15 | CZ15 | V2 | CZ15-V2-eSH-15 | CZ15-V2-eSH-15-MM | 12.4691 | 3.6363 | 5645.0927 | 393.9064 | 3.6782 | 6038.999 | 5677.1985
DEER-SFAM-CZ15-V2-eSH-16-CH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-CH | 12.5342 | 3.3603 | 6266.3313 | 411.2442 | 3.2375 | 6677.5755 | 6294.0565
DEER-SFAM-CZ15-V2-eSH-16-CL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-CL | 13.0346 | 3.3694 | 6507.9915 | 381.9279 | 3.2375 | 6889.9194 | 6536.5881
DEER-SFAM-CZ15-V2-eSH-16-LH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-LH | 12.3527 | 3.3043 | 5877.3958 | 435.4318 | 3.2375 | 6312.8276 | 5908.255
DEER-SFAM-CZ15-V2-eSH-16-LL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-LL | 11.9899 | 3.4285 | 6156.4687 | 392.7567 | 3.2375 | 6549.2254 | 6181.1719
DEER-SFAM-CZ15-V2-eSH-16-LM-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-LM | 11.9309 | 3.3903 | 6111.6524 | 434.9973 | 3.2375 | 6546.6496 | 6146.1709
DEER-SFAM-CZ15-V2-eSH-16-TH-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-TH | 12.5706 | 4.0996 | 6442.2605 | 526.9651 | 3.6782 | 6969.2256 | 6469.3216
DEER-SFAM-CZ15-V2-eSH-16-TL-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-TL | 11.7592 | 3.767 | 6892.1002 | 512.0542 | 3.2375 | 7404.1544 | 6917.7849
DEER-SFAM-CZ15-V2-eSH-16-TM-s2 | 16 | CZ15 | V2 | CZ15-V2-eSH-16 | CZ15-V2-eSH-16-TM | 11.9565 | 3.6948 | 6783.7027 | 520.3176 | 3.2375 | 7304.0204 | 6810.1757
DEER-SFAM-CZ15-V2-eSH-17-CM-s2 | 17 | CZ15 | V2 | CZ15-V2-eSH-17 | CZ15-V2-eSH-17-CM | 13.6977 | 3.2227 | 6180.4003 | 411.296 | 3.2375 | 6591.6963 | 6211.3305
DEER-SFAM-CZ15-V2-eSH-17-LM-s2 | 17 | CZ15 | V2 | CZ15-V2-eSH-17 | CZ15-V2-eSH-17-LM | 12.9912 | 3.279 | 6038.131 | 382.0439 | 3.2375 | 6420.1748 | 6052.0026
DEER-SFAM-CZ15-V2-eSH-17-TH-s2 | 17 | CZ15 | V2 | CZ15-V2-eSH-17 | CZ15-V2-eSH-17-TH | 13.1981 | 3.8103 | 6111.3679 | 524.485 | 3.6782 | 6635.8528 | 6140.8051
DEER-SFAM-CZ15-V2-eSH-17-TL-s2 | 17 | CZ15 | V2 | CZ15-V2-eSH-17 | CZ15-V2-eSH-17-TL | 13.0876 | 3.8953 | 6190.0948 | 519.1023 | 3.6782 | 6709.1971 | 6219.1245
DEER-SFAM-CZ15-V2-eSH-18-LH-s2 | 18 | CZ15 | V2 | CZ15-V2-eSH-18 | CZ15-V2-eSH-18-LH | 13.0879 | 3.1827 | 5674.5366 | 437.2956 | 3.2375 | 6111.8322 | 5697.3286
DEER-SFAM-CZ15-V2-eSH-18-LL-s2 | 18 | CZ15 | V2 | CZ15-V2-eSH-18 | CZ15-V2-eSH-18-LL | 12.5287 | 3.2935 | 5859.7928 | 391.275 | 3.2375 | 6251.0678 | 5881.1331
DEER-SFAM-CZ15-V2-eSH-18-LM-s2 | 18 | CZ15 | V2 | CZ15-V2-eSH-18 | CZ15-V2-eSH-18-LM | 13.1175 | 3.2291 | 5695.9814 | 461.0936 | 3.2375 | 6157.075 | 5722.215
DEER-SFAM-CZ15-V2-eSH-18-TM-s2 | 18 | CZ15 | V2 | CZ15-V2-eSH-18 | CZ15-V2-eSH-18-TM | 13.425 | 3.2402 | 5933.7676 | 521.8478 | 3.2375 | 6455.6154 | 5980.4336
DEER-SFAM-CZ15-V3-eSA-10-HH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-HH | 8.6104 | 3.9016 | 6617.3179 | 0 | 3 | 6617.3179 | 6621.2255
DEER-SFAM-CZ15-V3-eSA-10-HL-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-HL | 7.7164 | 5.0485 | 7113.9586 | 0 | 3.4 | 7113.9586 | 7117.877
DEER-SFAM-CZ15-V3-eSA-10-HM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-HM | 7.8878 | 4.7629 | 6833.7573 | 0 | 3.4 | 6833.7573 | 6837.6748
DEER-SFAM-CZ15-V3-eSA-10-LH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-LH | 9.1586 | 3.6645 | 6452.9588 | 0 | 3 | 6452.9588 | 6456.876
DEER-SFAM-CZ15-V3-eSA-10-LL-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-LL | 8.3468 | 4.3865 | 6625.5756 | 0 | 3.4 | 6625.5756 | 6629.4954
DEER-SFAM-CZ15-V3-eSA-10-LM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-LM | 9.0891 | 3.6916 | 6467.6304 | 0 | 3 | 6467.6304 | 6471.5477
DEER-SFAM-CZ15-V3-eSA-10-MH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-MH | 9.0734 | 3.5706 | 6459.4931 | 0 | 3 | 6459.4931 | 6463.4089
DEER-SFAM-CZ15-V3-eSA-10-ML-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-ML | 8.2028 | 3.9707 | 6785.4157 | 0 | 3 | 6785.4157 | 6789.3281
DEER-SFAM-CZ15-V3-eSA-10-MM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSA-10 | CZ15-V3-eSA-10-MM | 8.8169 | 3.446 | 6530.3447 | 0 | 2.9 | 6530.3447 | 6534.2568
DEER-SFAM-CZ15-V3-eSA-13-HH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-HH | 10.409 | 3.8339 | 5391.6855 | 0 | 3.4 | 5391.6855 | 5395.2177
DEER-SFAM-CZ15-V3-eSA-13-HL-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-HL | 10.2521 | 4.137 | 5520.638 | 0 | 3.4 | 5520.638 | 5523.7295
DEER-SFAM-CZ15-V3-eSA-13-HM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-HM | 10.2701 | 3.9118 | 5314.2375 | 0 | 3.4 | 5314.2375 | 5317.7681
DEER-SFAM-CZ15-V3-eSA-13-LH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-LH | 11.2536 | 3.5006 | 5061.7287 | 0 | 3.4 | 5061.7287 | 5065.6486
DEER-SFAM-CZ15-V3-eSA-13-LL-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-LL | 10.7882 | 3.3211 | 5276.661 | 0 | 3 | 5276.661 | 5280.5637
DEER-SFAM-CZ15-V3-eSA-13-LM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-LM | 10.7413 | 3.1731 | 5276.672 | 0 | 3 | 5276.672 | 5280.581
DEER-SFAM-CZ15-V3-eSA-13-MH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-MH | 10.6546 | 3.6914 | 5211.4924 | 0 | 3.4 | 5211.4924 | 5215.4103
DEER-SFAM-CZ15-V3-eSA-13-ML-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-ML | 10.1086 | 3.8693 | 5298.2379 | 0 | 3.4 | 5298.2379 | 5302.1435
DEER-SFAM-CZ15-V3-eSA-13-MM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSA-13 | CZ15-V3-eSA-13-MM | 11.016 | 3.7259 | 5078.1358 | 0 | 3.4 | 5078.1358 | 5082.0528
DEER-SFAM-CZ15-V3-eSA-14-HH-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-HH | 10.2919 | 3.7022 | 5192.511 | 0 | 3.4 | 5192.511 | 5195.7944
DEER-SFAM-CZ15-V3-eSA-14-HL-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-HL | 11.0897 | 3.6964 | 4961.8946 | 0 | 3.4 | 4961.8946 | 4964.309
DEER-SFAM-CZ15-V3-eSA-14-HM-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-HM | 10.8604 | 3.7412 | 5189.7429 | 0 | 3.4 | 5189.7429 | 5193.448
DEER-SFAM-CZ15-V3-eSA-14-MH-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-MH | 11.5668 | 2.9627 | 4993.8679 | 0 | 3 | 4993.8679 | 4996.4372
DEER-SFAM-CZ15-V3-eSA-14-ML-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-ML | 11.1004 | 3.6821 | 5085.0122 | 0 | 3.4 | 5085.0122 | 5089.1235
DEER-SFAM-CZ15-V3-eSA-14-MM-s1 | 14 | CZ15 | V3 | CZ15-V3-eSA-14 | CZ15-V3-eSA-14-MM | 11.4541 | 2.843 | 4946.4151 | 0 | 2.9 | 4946.4151 | 4949.2321
DEER-SFAM-CZ15-V3-eSA-15-HH-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-HH | 11.5513 | 3.481 | 4724.2247 | 0 | 3.4 | 4724.2247 | 4726.9623
DEER-SFAM-CZ15-V3-eSA-15-HL-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-HL | 11.7868 | 3.569 | 4623.4672 | 0 | 3.4 | 4623.4672 | 4626.8785
DEER-SFAM-CZ15-V3-eSA-15-HM-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-HM | 11.8694 | 3.3462 | 4585.2482 | 0 | 3.4 | 4585.2482 | 4587.9956
DEER-SFAM-CZ15-V3-eSA-15-MH-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-MH | 11.4119 | 3.4955 | 4908.9797 | 0 | 3.4 | 4908.9797 | 4911.0198
DEER-SFAM-CZ15-V3-eSA-15-ML-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-ML | 12.0191 | 3.3786 | 4685.2658 | 0 | 3.4 | 4685.2658 | 4688.0071
DEER-SFAM-CZ15-V3-eSA-15-MM-s1 | 15 | CZ15 | V3 | CZ15-V3-eSA-15 | CZ15-V3-eSA-15-MM | 11.8553 | 3.4439 | 4707.4554 | 0 | 3.4 | 4707.4554 | 4709.9569
DEER-SFAM-CZ15-V3-eSA-16-CH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-CH | 12.6403 | 3.4372 | 5176.707 | 0 | 3.4 | 5176.707 | 5178.3007
DEER-SFAM-CZ15-V3-eSA-16-CL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-CL | 12.777 | 3.5433 | 4834.3303 | 0 | 3.4 | 4834.3303 | 4836.3449
DEER-SFAM-CZ15-V3-eSA-16-CM-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-CM | 12.478 | 3.5138 | 5016.8458 | 0 | 3.4 | 5016.8458 | 5018.9722
DEER-SFAM-CZ15-V3-eSA-16-LH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-LH | 12.5437 | 2.9884 | 4529.8734 | 0 | 3 | 4529.8734 | 4532.5919
DEER-SFAM-CZ15-V3-eSA-16-LL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-LL | 12.0213 | 3.2033 | 4790.1046 | 0 | 3 | 4790.1046 | 4791.8863
DEER-SFAM-CZ15-V3-eSA-16-LM-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-LM | 12.1174 | 3.0688 | 4745.44 | 0 | 3 | 4745.44 | 4747.0547
DEER-SFAM-CZ15-V3-eSA-16-NM-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-NM | 13.7314 | 2.8949 | 4195.7451 | 0 | 3 | 4195.7451 | 4197.3318
DEER-SFAM-CZ15-V3-eSA-16-TH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-TH | 11.7532 | 4.0006 | 5438.2922 | 0 | 3.4 | 5438.2922 | 5439.3165
DEER-SFAM-CZ15-V3-eSA-16-TL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSA-16 | CZ15-V3-eSA-16-TL | 12.792 | 3.7463 | 4847.1214 | 0 | 3.4 | 4847.1214 | 4848.2236
DEER-SFAM-CZ15-V3-eSA-17-CH-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-CH | 13.2006 | 3.3381 | 4842.0059 | 0 | 3.4 | 4842.0059 | 4844.0195
DEER-SFAM-CZ15-V3-eSA-17-CL-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-CL | 13.1833 | 3.3676 | 4755.1222 | 0 | 3.4 | 4755.1222 | 4757.1353
DEER-SFAM-CZ15-V3-eSA-17-CM-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-CM | 13.2723 | 3.3588 | 4816.0772 | 0 | 3.4 | 4816.0772 | 4817.6658
DEER-SFAM-CZ15-V3-eSA-17-LH-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-LH | 12.8405 | 2.9093 | 4432.2674 | 0 | 3 | 4432.2674 | 4434.397
DEER-SFAM-CZ15-V3-eSA-17-LL-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-LL | 12.56 | 3.0688 | 4629.9898 | 0 | 3 | 4629.9898 | 4631.146
DEER-SFAM-CZ15-V3-eSA-17-LM-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-LM | 12.4879 | 3.0773 | 4597.2832 | 0 | 3 | 4597.2832 | 4598.282
DEER-SFAM-CZ15-V3-eSA-17-TH-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-TH | 13.0566 | 3.4085 | 4757.4237 | 0 | 3.4 | 4757.4237 | 4759.0595
DEER-SFAM-CZ15-V3-eSA-17-TL-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-TL | 13.8748 | 3.5057 | 4317.8992 | 0 | 3.4 | 4317.8992 | 4320.4601
DEER-SFAM-CZ15-V3-eSA-17-TM-s2 | 17 | CZ15 | V3 | CZ15-V3-eSA-17 | CZ15-V3-eSA-17-TM | 13.7614 | 3.4593 | 5007.8873 | 0 | 3.4 | 5007.8873 | 5008.7391
DEER-SFAM-CZ15-V3-eSA-18-LH-s2 | 18 | CZ15 | V3 | CZ15-V3-eSA-18 | CZ15-V3-eSA-18-LH | 13.3383 | 2.8642 | 4318.6058 | 0 | 3 | 4318.6058 | 4319.9981
DEER-SFAM-CZ15-V3-eSA-18-LL-s2 | 18 | CZ15 | V3 | CZ15-V3-eSA-18 | CZ15-V3-eSA-18-LL | 13.4844 | 2.8697 | 4243.1191 | 0 | 3 | 4243.1191 | 4244.9383
DEER-SFAM-CZ15-V3-eSA-18-TH-s2 | 18 | CZ15 | V3 | CZ15-V3-eSA-18 | CZ15-V3-eSA-18-TH | 13.8073 | 3.2624 | 4518.1168 | 0 | 3.4 | 4518.1168 | 4519.226
DEER-SFAM-CZ15-V3-eSA-18-TL-s2 | 18 | CZ15 | V3 | CZ15-V3-eSA-18 | CZ15-V3-eSA-18-TL | 13.2163 | 3.582 | 4967.8658 | 0 | 3.4 | 4967.8658 | 4969.0879
DEER-SFAM-CZ15-V3-eSA-18-TM-s2 | 18 | CZ15 | V3 | CZ15-V3-eSA-18 | CZ15-V3-eSA-18-TM | 13.2141 | 3.3803 | 4677.2792 | 0 | 3.4 | 4677.2792 | 4678.4142
DEER-SFAM-CZ15-V3-eSH-10-HH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-HH | 8.416 | 4.469 | 6533.9503 | 87.1377 | 3.4 | 6621.088 | 6542.888
DEER-SFAM-CZ15-V3-eSH-10-HL-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-HL | 8.1536 | 4.6969 | 6744.6616 | 86.7309 | 3.4 | 6831.3925 | 6753.3925
DEER-SFAM-CZ15-V3-eSH-10-HM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-HM | 8.3551 | 4.5714 | 6725.4088 | 85.5996 | 3.4 | 6811.0084 | 6733.8084
DEER-SFAM-CZ15-V3-eSH-10-LH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-LH | 9.0875 | 3.6714 | 6388.3354 | 91.0806 | 3 | 6479.416 | 6397.516
DEER-SFAM-CZ15-V3-eSH-10-LL-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-LL | 8.5365 | 4.3583 | 6512.5391 | 87.9204 | 3.4 | 6600.4595 | 6522.1595
DEER-SFAM-CZ15-V3-eSH-10-LM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-LM | 8.7409 | 4.1801 | 6371.0998 | 88.5259 | 3.4 | 6459.6257 | 6379.9257
DEER-SFAM-CZ15-V3-eSH-10-MH-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-MH | 9.0213 | 3.8532 | 6505.4625 | 89.6437 | 3 | 6595.1062 | 6515.2062
DEER-SFAM-CZ15-V3-eSH-10-ML-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-ML | 8.3644 | 4.6477 | 6693.081 | 83.4687 | 3.4 | 6776.5497 | 6702.0497
DEER-SFAM-CZ15-V3-eSH-10-MM-s1 | 10 | CZ15 | V3 | CZ15-V3-eSH-10 | CZ15-V3-eSH-10-MM | 8.6404 | 3.9448 | 6633.0618 | 86.5683 | 3 | 6719.6301 | 6641.3301
DEER-SFAM-CZ15-V3-eSH-13-HH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-HH | 9.6777 | 4.0662 | 5607.5065 | 83.8567 | 3.4 | 5691.3632 | 5615.6632
DEER-SFAM-CZ15-V3-eSH-13-HL-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-HL | 10.8516 | 4.0689 | 5295.6636 | 71.1235 | 3.4 | 5366.7871 | 5303.7871
DEER-SFAM-CZ15-V3-eSH-13-HM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-HM | 9.9881 | 3.9315 | 5440.8465 | 74.8746 | 3.4 | 5515.7211 | 5448.2211
DEER-SFAM-CZ15-V3-eSH-13-LH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-LH | 11.2265 | 3.0892 | 5137.2028 | 85.5765 | 3 | 5222.7793 | 5149.3793
DEER-SFAM-CZ15-V3-eSH-13-LL-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-LL | 11.0872 | 3.5773 | 5038.8796 | 75.482 | 3.4 | 5114.3616 | 5046.3616
DEER-SFAM-CZ15-V3-eSH-13-LM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-LM | 10.5027 | 3.2595 | 5365.2157 | 65.4043 | 3 | 5430.62 | 5373.62
DEER-SFAM-CZ15-V3-eSH-13-MH-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-MH | 10.7012 | 3.6949 | 5152.0237 | 85.9266 | 3.4 | 5237.9503 | 5160.1503
DEER-SFAM-CZ15-V3-eSH-13-ML-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-ML | 10.2544 | 3.51 | 5553.9219 | 75.8182 | 3 | 5629.7401 | 5562.2401
DEER-SFAM-CZ15-V3-eSH-13-MM-s1 | 13 | CZ15 | V3 | CZ15-V3-eSH-13 | CZ15-V3-eSH-13-MM | 10.3829 | 3.906 | 5381.6509 | 77.9869 | 3.4 | 5459.6378 | 5388.1378
DEER-SFAM-CZ15-V3-eSH-14-HH-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-HH | 10.2725 | 3.9111 | 5286.6863 | 76.3134 | 3.4 | 5362.9997 | 5292.8997
DEER-SFAM-CZ15-V3-eSH-14-HL-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-HL | 10.7774 | 3.7624 | 5038.7135 | 73.8476 | 3.4 | 5112.5611 | 5046.1611
DEER-SFAM-CZ15-V3-eSH-14-HM-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-HM | 10.812 | 3.6321 | 5005.812 | 75.2311 | 3.4 | 5081.0431 | 5011.1431
DEER-SFAM-CZ15-V3-eSH-14-MH-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-MH | 11.9462 | 2.9632 | 4793.951 | 78.7137 | 3 | 4872.6647 | 4802.0647
DEER-SFAM-CZ15-V3-eSH-14-ML-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-ML | 11.4544 | 3.5897 | 4864.6407 | 79.8367 | 3.4 | 4944.4774 | 4874.7774
DEER-SFAM-CZ15-V3-eSH-14-MM-s1 | 14 | CZ15 | V3 | CZ15-V3-eSH-14 | CZ15-V3-eSH-14-MM | 11.4871 | 3.5635 | 4922.2769 | 71.9836 | 3.4 | 4994.2605 | 4929.2605
DEER-SFAM-CZ15-V3-eSH-15-HH-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-HH | 11.6651 | 3.3543 | 4643.2274 | 84.7876 | 3.4 | 4728.015 | 4649.015
DEER-SFAM-CZ15-V3-eSH-15-HL-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-HL | 11.7168 | 3.4752 | 4699.9408 | 64.0987 | 3.4 | 4764.0395 | 4705.6395
DEER-SFAM-CZ15-V3-eSH-15-HM-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-HM | 12.0049 | 3.4108 | 4552.1851 | 67.1613 | 3.4 | 4619.3464 | 4557.8464
DEER-SFAM-CZ15-V3-eSH-15-MH-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-MH | 11.8102 | 3.4424 | 4765.696 | 74.378 | 3.4 | 4840.074 | 4771.174
DEER-SFAM-CZ15-V3-eSH-15-ML-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-ML | 12.2016 | 3.4323 | 4562.8028 | 70.6203 | 3.4 | 4633.4231 | 4568.5231
DEER-SFAM-CZ15-V3-eSH-15-MM-s1 | 15 | CZ15 | V3 | CZ15-V3-eSH-15 | CZ15-V3-eSH-15-MM | 12.1447 | 3.3032 | 4526.4741 | 76.4937 | 3.4 | 4602.9678 | 4532.5678
DEER-SFAM-CZ15-V3-eSH-16-CH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-CH | 12.6552 | 3.4657 | 4943.1081 | 76.1997 | 3.4 | 5019.3078 | 4948.0078
DEER-SFAM-CZ15-V3-eSH-16-CL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-CL | 12.7818 | 3.4857 | 5199.5646 | 70.3344 | 3.4 | 5269.899 | 5204.699
DEER-SFAM-CZ15-V3-eSH-16-LH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-LH | 12.1655 | 3.0292 | 4660.005 | 81.857 | 3 | 4741.862 | 4665.762
DEER-SFAM-CZ15-V3-eSH-16-LL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-LL | 11.9856 | 3.1377 | 4792.8751 | 72.4309 | 3 | 4865.306 | 4797.506
DEER-SFAM-CZ15-V3-eSH-16-LM-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-LM | 11.8493 | 3.0112 | 4793.3358 | 80.8352 | 2.9 | 4874.171 | 4799.771
DEER-SFAM-CZ15-V3-eSH-16-TH-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-TH | 12.6488 | 3.7114 | 4927.3624 | 96.769 | 3.4 | 5024.1314 | 4931.8314
DEER-SFAM-CZ15-V3-eSH-16-TL-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-TL | 12.0063 | 3.9027 | 5389.1478 | 91.3515 | 3.4 | 5480.4993 | 5392.9993
DEER-SFAM-CZ15-V3-eSH-16-TM-s2 | 16 | CZ15 | V3 | CZ15-V3-eSH-16 | CZ15-V3-eSH-16-TM | 12.1426 | 3.8227 | 5330.2985 | 92.9377 | 3.4 | 5423.2362 | 5334.2362
DEER-SFAM-CZ15-V3-eSH-17-CM-s2 | 17 | CZ15 | V3 | CZ15-V3-eSH-17 | CZ15-V3-eSH-17-CM | 13.423 | 3.3302 | 4943.2076 | 72.5863 | 3.4 | 5015.7939 | 4948.5939
DEER-SFAM-CZ15-V3-eSH-17-LM-s2 | 17 | CZ15 | V3 | CZ15-V3-eSH-17 | CZ15-V3-eSH-17-LM | 12.4777 | 3.0145 | 4832.3125 | 70.7991 | 3 | 4903.1116 | 4834.9116
DEER-SFAM-CZ15-V3-eSH-17-TH-s2 | 17 | CZ15 | V3 | CZ15-V3-eSH-17 | CZ15-V3-eSH-17-TH | 13.2006 | 3.4692 | 4706.9914 | 95.5351 | 3.4 | 4802.5265 | 4711.7265
DEER-SFAM-CZ15-V3-eSH-17-TL-s2 | 17 | CZ15 | V3 | CZ15-V3-eSH-17 | CZ15-V3-eSH-17-TL | 13.1589 | 3.5474 | 4740.2173 | 93.8968 | 3.4 | 4834.1141 | 4744.9141
DEER-SFAM-CZ15-V3-eSH-18-LH-s2 | 18 | CZ15 | V3 | CZ15-V3-eSH-18 | CZ15-V3-eSH-18-LH | 13.0174 | 2.9205 | 4433.0594 | 78.3609 | 3 | 4511.4203 | 4437.2203
DEER-SFAM-CZ15-V3-eSH-18-LL-s2 | 18 | CZ15 | V3 | CZ15-V3-eSH-18 | CZ15-V3-eSH-18-LL | 12.4706 | 3.0268 | 4583.1667 | 71.2853 | 3 | 4654.452 | 4587.152
DEER-SFAM-CZ15-V3-eSH-18-LM-s2 | 18 | CZ15 | V3 | CZ15-V3-eSH-18 | CZ15-V3-eSH-18-LM | 13.1089 | 2.9616 | 4414.4956 | 81.8303 | 3 | 4496.3259 | 4419.2259
DEER-SFAM-CZ15-V3-eSH-18-TM-s2 | 18 | CZ15 | V3 | CZ15-V3-eSH-18 | CZ15-V3-eSH-18-TM | 13.4666 | 2.9855 | 4638.9494 | 94.3495 | 3 | 4733.2989 | 4646.3989
DEER-SFAM-CZ15-V4-eSA-10-HH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-HH | 8.5522 | 4.9534 | 8002.7345 | 0 | 3.8 | 8002.7345 | 8004.9579
DEER-SFAM-CZ15-V4-eSA-10-HL-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-HL | 7.7847 | 5.7014 | 8503.0824 | 0 | 3.8 | 8503.0824 | 8505.3082
DEER-SFAM-CZ15-V4-eSA-10-HM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-HM | 7.9554 | 5.3795 | 8164.6012 | 0 | 3.8 | 8164.6012 | 8166.8269
DEER-SFAM-CZ15-V4-eSA-10-LH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-LH | 9.0892 | 4.647 | 7806.1398 | 0 | 3.8 | 7806.1398 | 7808.3685
DEER-SFAM-CZ15-V4-eSA-10-LL-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-LL | 8.4083 | 4.9435 | 7932.3893 | 0 | 3.8 | 7932.3893 | 7934.616
DEER-SFAM-CZ15-V4-eSA-10-LM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-LM | 9.0265 | 4.6772 | 7819.4045 | 0 | 3.8 | 7819.4045 | 7821.6332
DEER-SFAM-CZ15-V4-eSA-10-MH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-MH | 8.9825 | 4.5236 | 7835.9895 | 0 | 3.8 | 7835.9895 | 7838.2176
DEER-SFAM-CZ15-V4-eSA-10-ML-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-ML | 8.1724 | 5.0443 | 8184.6344 | 0 | 3.8 | 8184.6344 | 8186.8606
DEER-SFAM-CZ15-V4-eSA-10-MM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSA-10 | CZ15-V4-eSA-10-MM | 8.8513 | 4.0443 | 7829.1544 | 0 | 3.4 | 7829.1544 | 7831.3775
DEER-SFAM-CZ15-V4-eSA-13-HH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-HH | 10.5209 | 4.3307 | 6431.8616 | 0 | 3.8 | 6431.8616 | 6433.8681
DEER-SFAM-CZ15-V4-eSA-13-HL-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-HL | 10.3496 | 4.6828 | 6596.493 | 0 | 3.8 | 6596.493 | 6598.2493
DEER-SFAM-CZ15-V4-eSA-13-HM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-HM | 10.2898 | 4.7331 | 6381.7827 | 0 | 4.2 | 6381.7827 | 6383.791
DEER-SFAM-CZ15-V4-eSA-13-LH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-LH | 11.393 | 3.9551 | 6030.4723 | 0 | 3.8 | 6030.4723 | 6032.6995
DEER-SFAM-CZ15-V4-eSA-13-LL-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-LL | 10.7498 | 4.2143 | 6363.2654 | 0 | 3.8 | 6363.2654 | 6365.4858
DEER-SFAM-CZ15-V4-eSA-13-LM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-LM | 10.6666 | 4.0229 | 6382.9009 | 0 | 3.8 | 6382.9009 | 6385.1252
DEER-SFAM-CZ15-V4-eSA-13-MH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-MH | 10.7744 | 4.1835 | 6212.6657 | 0 | 3.8 | 6212.6657 | 6214.8914
DEER-SFAM-CZ15-V4-eSA-13-ML-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-ML | 10.1676 | 4.3851 | 6346.7956 | 0 | 3.8 | 6346.7956 | 6349.0138
DEER-SFAM-CZ15-V4-eSA-13-MM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSA-13 | CZ15-V4-eSA-13-MM | 11.0366 | 4.4915 | 6099.554 | 0 | 4.2 | 6099.554 | 6101.7821
DEER-SFAM-CZ15-V4-eSA-14-HH-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-HH | 10.3751 | 4.1902 | 6206.1011 | 0 | 3.8 | 6206.1011 | 6207.9664
DEER-SFAM-CZ15-V4-eSA-14-HL-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-HL | 11.1126 | 4.4496 | 5955.6113 | 0 | 4.2 | 5955.6113 | 5956.9848
DEER-SFAM-CZ15-V4-eSA-14-HM-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-HM | 10.9714 | 4.2361 | 6199.6644 | 0 | 3.8 | 6199.6644 | 6201.7694
DEER-SFAM-CZ15-V4-eSA-14-MH-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-MH | 11.4777 | 3.7564 | 6045.9112 | 0 | 3.8 | 6045.9112 | 6047.3731
DEER-SFAM-CZ15-V4-eSA-14-ML-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-ML | 11.2115 | 4.163 | 6071.6226 | 0 | 3.8 | 6071.6226 | 6073.9582
DEER-SFAM-CZ15-V4-eSA-14-MM-s1 | 14 | CZ15 | V4 | CZ15-V4-eSA-14 | CZ15-V4-eSA-14-MM | 11.5099 | 3.3344 | 5929.5777 | 0 | 3.4 | 5929.5777 | 5931.1783
DEER-SFAM-CZ15-V4-eSA-15-HH-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-HH | 11.5683 | 4.2177 | 5675.8163 | 0 | 4.2 | 5675.8163 | 5677.3733
DEER-SFAM-CZ15-V4-eSA-15-HL-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-HL | 11.8137 | 4.3 | 5548.8922 | 0 | 4.2 | 5548.8922 | 5550.8322
DEER-SFAM-CZ15-V4-eSA-15-HM-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-HM | 11.886 | 4.043 | 5508.4932 | 0 | 4.2 | 5508.4932 | 5510.0559
DEER-SFAM-CZ15-V4-eSA-15-MH-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-MH | 11.5565 | 3.9576 | 5847.6837 | 0 | 3.8 | 5847.6837 | 5848.8424
DEER-SFAM-CZ15-V4-eSA-15-ML-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-ML | 12.1361 | 3.8376 | 5597.7348 | 0 | 3.8 | 5597.7348 | 5599.2915
DEER-SFAM-CZ15-V4-eSA-15-MM-s1 | 15 | CZ15 | V4 | CZ15-V4-eSA-15 | CZ15-V4-eSA-15-MM | 11.9757 | 3.9074 | 5622.0585 | 0 | 3.8 | 5622.0585 | 5623.4795
DEER-SFAM-CZ15-V4-eSA-16-CH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-CH | 12.6534 | 3.8751 | 6186.4167 | 0 | 3.8 | 6186.4167 | 6187.3249
DEER-SFAM-CZ15-V4-eSA-16-CL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-CL | 12.8126 | 4.3054 | 5820.0054 | 0 | 4.2 | 5820.0054 | 5821.1553
DEER-SFAM-CZ15-V4-eSA-16-CM-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-CM | 12.5173 | 4.2746 | 6043.3914 | 0 | 4.2 | 6043.3914 | 6044.6053
DEER-SFAM-CZ15-V4-eSA-16-LH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-LH | 12.5233 | 3.7998 | 5468.8427 | 0 | 3.8 | 5468.8427 | 5470.3923
DEER-SFAM-CZ15-V4-eSA-16-LL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-LL | 12.0213 | 4.075 | 5768.342 | 0 | 3.8 | 5768.342 | 5769.3572
DEER-SFAM-CZ15-V4-eSA-16-LM-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-LM | 12.1063 | 3.9006 | 5721.4114 | 0 | 3.8 | 5721.4114 | 5722.3312
DEER-SFAM-CZ15-V4-eSA-16-NM-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-NM | 13.7982 | 3.6781 | 5038.4265 | 0 | 3.8 | 5038.4265 | 5039.3307
DEER-SFAM-CZ15-V4-eSA-16-TH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-TH | 11.7867 | 4.5219 | 6467.7662 | 0 | 3.8 | 6467.7662 | 6468.3496
DEER-SFAM-CZ15-V4-eSA-16-TL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSA-16 | CZ15-V4-eSA-16-TL | 12.8143 | 4.531 | 5836.9194 | 0 | 4.2 | 5836.9194 | 5837.5475
DEER-SFAM-CZ15-V4-eSA-17-CH-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-CH | 13.2098 | 3.7737 | 5792.1702 | 0 | 3.8 | 5792.1702 | 5793.3179
DEER-SFAM-CZ15-V4-eSA-17-CL-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-CL | 13.1613 | 3.8151 | 5698.5335 | 0 | 3.8 | 5698.5335 | 5699.6808
DEER-SFAM-CZ15-V4-eSA-17-CM-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-CM | 13.2573 | 3.8008 | 5763.8717 | 0 | 3.8 | 5763.8717 | 5764.777
DEER-SFAM-CZ15-V4-eSA-17-LH-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-LH | 12.8966 | 3.3118 | 5301.7624 | 0 | 3.4 | 5301.7624 | 5302.9741
DEER-SFAM-CZ15-V4-eSA-17-LL-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-LL | 12.5643 | 3.9037 | 5574.7246 | 0 | 3.8 | 5574.7246 | 5575.3828
DEER-SFAM-CZ15-V4-eSA-17-LM-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-LM | 12.4842 | 3.9086 | 5539.2772 | 0 | 3.8 | 5539.2772 | 5539.846
DEER-SFAM-CZ15-V4-eSA-17-TH-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-TH | 13.1394 | 3.8403 | 5646.1436 | 0 | 3.8 | 5646.1436 | 5647.0751
DEER-SFAM-CZ15-V4-eSA-17-TL-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-TL | 13.8284 | 3.9923 | 5169.1103 | 0 | 3.8 | 5169.1103 | 5170.5705
DEER-SFAM-CZ15-V4-eSA-17-TM-s2 | 17 | CZ15 | V4 | CZ15-V4-eSA-17 | CZ15-V4-eSA-17-TM | 13.79 | 4.2166 | 6028.9557 | 0 | 4.2 | 6028.9557 | 6029.4408
DEER-SFAM-CZ15-V4-eSA-18-LH-s2 | 18 | CZ15 | V4 | CZ15-V4-eSA-18 | CZ15-V4-eSA-18-LH | 13.3241 | 3.641 | 5206.7721 | 0 | 3.8 | 5206.7721 | 5207.5655
DEER-SFAM-CZ15-V4-eSA-18-LL-s2 | 18 | CZ15 | V4 | CZ15-V4-eSA-18 | CZ15-V4-eSA-18-LL | 13.507 | 3.6492 | 5108.1303 | 0 | 3.8 | 5108.1303 | 5109.1671
DEER-SFAM-CZ15-V4-eSA-18-TH-s2 | 18 | CZ15 | V4 | CZ15-V4-eSA-18 | CZ15-V4-eSA-18-TH | 13.7724 | 3.9716 | 5454.1335 | 0 | 4.2 | 5454.1335 | 5454.7662
DEER-SFAM-CZ15-V4-eSA-18-TL-s2 | 18 | CZ15 | V4 | CZ15-V4-eSA-18 | CZ15-V4-eSA-18-TL | 13.265 | 4.0473 | 5911.9601 | 0 | 3.8 | 5911.9601 | 5912.6562
DEER-SFAM-CZ15-V4-eSA-18-TM-s2 | 18 | CZ15 | V4 | CZ15-V4-eSA-18 | CZ15-V4-eSA-18-TM | 13.2892 | 3.8118 | 5555.4296 | 0 | 3.8 | 5555.4296 | 5556.0762
DEER-SFAM-CZ15-V4-eSH-10-HH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-HH | 8.4117 | 5.4145 | 7859.852 | 51.5606 | 4.2 | 7911.4126 | 7865.1126
DEER-SFAM-CZ15-V4-eSH-10-HL-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-HL | 8.1556 | 5.6937 | 8104.421 | 51.413 | 4.2 | 8155.834 | 8109.534
DEER-SFAM-CZ15-V4-eSH-10-HM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-HM | 8.4465 | 5.175 | 8023.8272 | 50.3233 | 3.8 | 8074.1505 | 8028.7505
DEER-SFAM-CZ15-V4-eSH-10-LH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-LH | 9.0022 | 4.6596 | 7746.2235 | 53.6015 | 3.8 | 7799.825 | 7751.625
DEER-SFAM-CZ15-V4-eSH-10-LL-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-LL | 8.6105 | 4.9303 | 7782.6997 | 52.5647 | 3.8 | 7835.2644 | 7788.3644
DEER-SFAM-CZ15-V4-eSH-10-LM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-LM | 8.8355 | 4.7333 | 7599.8363 | 52.0941 | 3.8 | 7651.9304 | 7605.0304
DEER-SFAM-CZ15-V4-eSH-10-MH-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-MH | 8.9503 | 4.8923 | 7873.7551 | 53.0339 | 3.8 | 7926.789 | 7879.489
DEER-SFAM-CZ15-V4-eSH-10-ML-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-ML | 8.4351 | 5.2621 | 8003.5274 | 48.9013 | 3.8 | 8052.4287 | 8008.8287
DEER-SFAM-CZ15-V4-eSH-10-MM-s1 | 10 | CZ15 | V4 | CZ15-V4-eSH-10 | CZ15-V4-eSH-10-MM | 8.594 | 5.0065 | 8011.1393 | 51.2588 | 3.8 | 8062.3981 | 8015.9981
DEER-SFAM-CZ15-V4-eSH-13-HH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-HH | 9.7881 | 4.6065 | 6682.1455 | 49.1956 | 3.8 | 6731.3411 | 6686.9411
DEER-SFAM-CZ15-V4-eSH-13-HL-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-HL | 10.883 | 4.9196 | 6362.4054 | 42.1847 | 4.2 | 6404.5901 | 6367.1901
DEER-SFAM-CZ15-V4-eSH-13-HM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-HM | 10.0871 | 4.4586 | 6492.9467 | 44.0395 | 3.8 | 6536.9862 | 6497.2862
DEER-SFAM-CZ15-V4-eSH-13-LH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-LH | 11.1308 | 3.9218 | 6221.024 | 51.0768 | 3.8 | 6272.1008 | 6228.2008
DEER-SFAM-CZ15-V4-eSH-13-LL-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-LL | 11.205 | 4.0561 | 6013.4439 | 44.1058 | 3.8 | 6057.5497 | 6017.8497
DEER-SFAM-CZ15-V4-eSH-13-LM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-LM | 10.4316 | 4.1325 | 6488.355 | 38.5313 | 3.8 | 6526.8863 | 6493.2863
DEER-SFAM-CZ15-V4-eSH-13-MH-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-MH | 10.7015 | 4.4666 | 6198.0628 | 51.0698 | 4.2 | 6249.1326 | 6202.8326
DEER-SFAM-CZ15-V4-eSH-13-ML-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-ML | 10.214 | 4.4562 | 6696.6856 | 44.5849 | 3.8 | 6741.2705 | 6701.5705
DEER-SFAM-CZ15-V4-eSH-13-MM-s1 | 13 | CZ15 | V4 | CZ15-V4-eSH-13 | CZ15-V4-eSH-13-MM | 10.494 | 4.4364 | 6422.4872 | 46.2941 | 3.8 | 6468.7813 | 6426.2813
DEER-SFAM-CZ15-V4-eSH-14-HH-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-HH | 10.3769 | 4.4347 | 6307.4996 | 44.853 | 3.8 | 6352.3526 | 6311.1526
DEER-SFAM-CZ15-V4-eSH-14-HL-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-HL | 10.8026 | 4.5427 | 6046.7159 | 43.5825 | 4.2 | 6090.2984 | 6051.0984
DEER-SFAM-CZ15-V4-eSH-14-HM-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-HM | 10.8252 | 4.3842 | 6013.7118 | 44.2439 | 4.2 | 6057.9557 | 6016.8557
DEER-SFAM-CZ15-V4-eSH-14-MH-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-MH | 11.8502 | 3.7644 | 5803.4488 | 46.8948 | 3.8 | 5850.3436 | 5808.2436
DEER-SFAM-CZ15-V4-eSH-14-ML-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-ML | 11.4719 | 4.3336 | 5842.3683 | 47.0821 | 4.2 | 5889.4504 | 5848.3504
DEER-SFAM-CZ15-V4-eSH-14-MM-s1 | 14 | CZ15 | V4 | CZ15-V4-eSH-14 | CZ15-V4-eSH-14-MM | 11.6073 | 4.0206 | 5874.7277 | 42.7997 | 3.8 | 5917.5274 | 5878.8274
DEER-SFAM-CZ15-V4-eSH-15-HH-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-HH | 11.6773 | 4.0497 | 5579.4928 | 49.7128 | 4.2 | 5629.2056 | 5582.9056
DEER-SFAM-CZ15-V4-eSH-15-HL-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-HL | 11.743 | 4.1921 | 5643.2557 | 38.349 | 4.2 | 5681.6047 | 5646.6047
DEER-SFAM-CZ15-V4-eSH-15-HM-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-HM | 12.0272 | 4.1012 | 5466.9304 | 40.2243 | 4.2 | 5507.1547 | 5470.2547
DEER-SFAM-CZ15-V4-eSH-15-MH-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-MH | 11.9513 | 3.9066 | 5685.5971 | 43.8171 | 3.8 | 5729.4142 | 5688.8142
DEER-SFAM-CZ15-V4-eSH-15-ML-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-ML | 12.2255 | 4.138 | 5477.9397 | 41.6737 | 4.2 | 5519.6134 | 5481.3134
DEER-SFAM-CZ15-V4-eSH-15-MM-s1 | 15 | CZ15 | V4 | CZ15-V4-eSH-15 | CZ15-V4-eSH-15-MM | 12.1694 | 3.9954 | 5434.5825 | 45.1961 | 4.2 | 5479.7786 | 5438.1786
DEER-SFAM-CZ15-V4-eSH-16-CH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-CH | 12.663 | 3.9176 | 5903.6379 | 45.2353 | 3.8 | 5948.8732 | 5906.5732
DEER-SFAM-CZ15-V4-eSH-16-CL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-CL | 12.807 | 3.9303 | 6208.1589 | 41.6722 | 3.8 | 6249.8311 | 6211.2311
DEER-SFAM-CZ15-V4-eSH-16-LH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-LH | 12.1041 | 3.8526 | 5643.0179 | 49.1 | 3.8 | 5692.1179 | 5646.4179
DEER-SFAM-CZ15-V4-eSH-16-LL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-LL | 11.9899 | 3.9872 | 5774.4029 | 43.2355 | 3.8 | 5817.6384 | 5777.1384
DEER-SFAM-CZ15-V4-eSH-16-LM-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-LM | 11.8959 | 3.5306 | 5742.9769 | 48.0937 | 3.4 | 5791.0706 | 5746.7706
DEER-SFAM-CZ15-V4-eSH-16-TH-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-TH | 12.6205 | 4.5183 | 5945.0672 | 57.5779 | 4.2 | 6002.6451 | 5947.7451
DEER-SFAM-CZ15-V4-eSH-16-TL-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-TL | 11.9885 | 4.4082 | 6433.8766 | 54.8877 | 3.8 | 6488.7643 | 6436.1643
DEER-SFAM-CZ15-V4-eSH-16-TM-s2 | 16 | CZ15 | V4 | CZ15-V4-eSH-16 | CZ15-V4-eSH-16-TM | 12.136 | 4.3175 | 6357.694 | 55.8371 | 3.8 | 6413.5311 | 6360.0311
DEER-SFAM-CZ15-V4-eSH-17-CM-s2 | 17 | CZ15 | V4 | CZ15-V4-eSH-17 | CZ15-V4-eSH-17-CM | 13.4517 | 3.7555 | 5900.9018 | 42.5652 | 3.8 | 5943.467 | 5904.067
DEER-SFAM-CZ15-V4-eSH-17-LM-s2 | 17 | CZ15 | V4 | CZ15-V4-eSH-17 | CZ15-V4-eSH-17-LM | 12.3994 | 3.8238 | 5862.4404 | 42.434 | 3.8 | 5904.8744 | 5863.9744
DEER-SFAM-CZ15-V4-eSH-17-TH-s2 | 17 | CZ15 | V4 | CZ15-V4-eSH-17 | CZ15-V4-eSH-17-TH | 13.2567 | 3.918 | 5599.2155 | 57.7248 | 3.8 | 5656.9403 | 5602.0403
DEER-SFAM-CZ15-V4-eSH-17-TL-s2 | 17 | CZ15 | V4 | CZ15-V4-eSH-17 | CZ15-V4-eSH-17-TL | 13.2012 | 4.0073 | 5645.245 | 56.4054 | 3.8 | 5701.6504 | 5648.0504
DEER-SFAM-CZ15-V4-eSH-18-LH-s2 | 18 | CZ15 | V4 | CZ15-V4-eSH-18 | CZ15-V4-eSH-18-LH | 13.0118 | 3.7094 | 5348.1212 | 46.5663 | 3.8 | 5394.6875 | 5350.5875
DEER-SFAM-CZ15-V4-eSH-18-LL-s2 | 18 | CZ15 | V4 | CZ15-V4-eSH-18 | CZ15-V4-eSH-18-LL | 12.5182 | 3.442 | 5484.3231 | 42.3498 | 3.4 | 5526.6729 | 5486.6729
DEER-SFAM-CZ15-V4-eSH-18-LM-s2 | 18 | CZ15 | V4 | CZ15-V4-eSH-18 | CZ15-V4-eSH-18-LM | 13.1101 | 3.7625 | 5319.3304 | 48.3057 | 3.8 | 5367.6361 | 5322.1361
DEER-SFAM-CZ15-V4-eSH-18-TM-s2 | 18 | CZ15 | V4 | CZ15-V4-eSH-18 | CZ15-V4-eSH-18-TM | 13.5676 | 3.7842 | 5614.2616 | 57.6163 | 3.8 | 5671.8779 | 5618.4779
DEER-SFAM-CZ16-V1-eSA-10-HH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-HH | 10.2793 | 3.2188 | 939.9697 | 0 | 3.4688 | 939.9697 | 1404.1566
DEER-SFAM-CZ16-V1-eSA-10-HL-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-HL | 10.4415 | 3.4251 | 947.6509 | 0 | 3.4688 | 947.6509 | 1412.1677
DEER-SFAM-CZ16-V1-eSA-10-HM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-HM | 10.1645 | 3.3589 | 948.2805 | 0 | 3.4688 | 948.2805 | 1412.7392
DEER-SFAM-CZ16-V1-eSA-10-LH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-LH | 10.4779 | 3.2355 | 931.8929 | 0 | 3.4688 | 931.8929 | 1396.7329
DEER-SFAM-CZ16-V1-eSA-10-LL-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-LL | 10.604 | 3.343 | 937.7874 | 0 | 3.4688 | 937.7874 | 1402.3789
DEER-SFAM-CZ16-V1-eSA-10-LM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-LM | 10.4394 | 3.2477 | 930.675 | 0 | 3.4688 | 930.675 | 1395.527
DEER-SFAM-CZ16-V1-eSA-10-MH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-MH | 10.3258 | 3.1609 | 940.0151 | 0 | 3.4688 | 940.0151 | 1404.7432
DEER-SFAM-CZ16-V1-eSA-10-ML-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-ML | 10.3348 | 3.3983 | 959.8222 | 0 | 3.4688 | 959.8222 | 1424.3477
DEER-SFAM-CZ16-V1-eSA-10-MM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSA-10 | CZ16-V1-eSA-10-MM | 10.0972 | 3.2419 | 938.6973 | 0 | 3.4688 | 938.6973 | 1403.2578
DEER-SFAM-CZ16-V1-eSA-13-HH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-HH | 13.5501 | 2.5841 | 722.1741 | 0 | 3.4688 | 722.1741 | 1140.8873
DEER-SFAM-CZ16-V1-eSA-13-HL-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-HL | 12.7284 | 2.7101 | 737.3092 | 0 | 3.4688 | 737.3092 | 1103.7628
DEER-SFAM-CZ16-V1-eSA-13-HM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-HM | 13.9038 | 2.5779 | 709.503 | 0 | 3.4688 | 709.503 | 1128.0888
DEER-SFAM-CZ16-V1-eSA-13-LH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-LH | 13.3389 | 2.4504 | 712.2048 | 0 | 3.4688 | 712.2048 | 1176.8185
DEER-SFAM-CZ16-V1-eSA-13-LL-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-LL | 13.1549 | 2.6187 | 734.2384 | 0 | 3.4688 | 734.2384 | 1198.0656
DEER-SFAM-CZ16-V1-eSA-13-LM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-LM | 12.7887 | 2.6014 | 747.0544 | 0 | 3.4688 | 747.0544 | 1211.3415
DEER-SFAM-CZ16-V1-eSA-13-MH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-MH | 14.1136 | 2.4843 | 700.298 | 0 | 3.4688 | 700.298 | 1164.7585
DEER-SFAM-CZ16-V1-eSA-13-ML-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-ML | 12.4992 | 2.6327 | 727.7397 | 0 | 3.4688 | 727.7397 | 1190.7842
DEER-SFAM-CZ16-V1-eSA-13-MM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSA-13 | CZ16-V1-eSA-13-MM | 14.3828 | 2.4292 | 680.7269 | 0 | 3.4688 | 680.7269 | 1145.1292
DEER-SFAM-CZ16-V1-eSA-14-HH-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-HH | 12.8996 | 2.5218 | 704.9839 | 0 | 3.4688 | 704.9839 | 1094.2484
DEER-SFAM-CZ16-V1-eSA-14-HL-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-HL | 14.4574 | 2.4272 | 673.0341 | 0 | 3.4688 | 673.0341 | 959.2607
DEER-SFAM-CZ16-V1-eSA-14-HM-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-HM | 13.4995 | 2.6129 | 706.0253 | 0 | 3.4688 | 706.0253 | 1145.1642
DEER-SFAM-CZ16-V1-eSA-14-MH-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-MH | 13.8159 | 2.4287 | 706.6149 | 0 | 3.4688 | 706.6149 | 1011.7893
DEER-SFAM-CZ16-V1-eSA-14-ML-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-ML | 13.3272 | 2.5083 | 692.426 | 0 | 3.4688 | 692.426 | 1179.8156
DEER-SFAM-CZ16-V1-eSA-14-MM-s1 | 14 | CZ16 | V1 | CZ16-V1-eSA-14 | CZ16-V1-eSA-14-MM | 13.7654 | 2.4191 | 690.6199 | 0 | 3.4688 | 690.6199 | 1025.1844
DEER-SFAM-CZ16-V1-eSA-15-HH-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-HH | 16.0554 | 2.2147 | 613.7304 | 0 | 3.4688 | 613.7304 | 938.2194
DEER-SFAM-CZ16-V1-eSA-15-HL-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-HL | 15.8624 | 2.254 | 608.6096 | 0 | 3.4688 | 608.6096 | 1013.0692
DEER-SFAM-CZ16-V1-eSA-15-HM-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-HM | 15.7384 | 2.2233 | 620.0425 | 0 | 3.711 | 620.0425 | 945.8518
DEER-SFAM-CZ16-V1-eSA-15-MH-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-MH | 14.0501 | 2.3576 | 655.2167 | 0 | 3.4688 | 655.2167 | 896.9941
DEER-SFAM-CZ16-V1-eSA-15-ML-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-ML | 15.2785 | 2.303 | 636.0672 | 0 | 3.4688 | 636.0672 | 961.2775
DEER-SFAM-CZ16-V1-eSA-15-MM-s1 | 15 | CZ16 | V1 | CZ16-V1-eSA-15 | CZ16-V1-eSA-15-MM | 14.5786 | 2.3268 | 640.0751 | 0 | 3.4688 | 640.0751 | 936.5532
DEER-SFAM-CZ16-V1-eSA-16-CH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-CH | 14.9422 | 2.6454 | 765.6214 | 0 | 3.4688 | 765.6214 | 944.8262
DEER-SFAM-CZ16-V1-eSA-16-CL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-CL | 15.4383 | 2.569 | 730.8245 | 0 | 3.711 | 730.8245 | 958.9805
DEER-SFAM-CZ16-V1-eSA-16-CM-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-CM | 15.1559 | 2.6087 | 749.6221 | 0 | 3.711 | 749.6221 | 990.7429
DEER-SFAM-CZ16-V1-eSA-16-LH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-LH | 15.0887 | 2.1896 | 652.2258 | 0 | 3.4688 | 652.2258 | 968.1883
DEER-SFAM-CZ16-V1-eSA-16-LL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-LL | 14.4596 | 2.3772 | 691.0277 | 0 | 3.4688 | 691.0277 | 900.0508
DEER-SFAM-CZ16-V1-eSA-16-LM-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-LM | 14.3836 | 2.3465 | 694.3069 | 0 | 3.4688 | 694.3069 | 883.7262
DEER-SFAM-CZ16-V1-eSA-16-NM-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-NM | 15.557 | 2.1927 | 660.4311 | 0 | 3.4688 | 660.4311 | 846.0264
DEER-SFAM-CZ16-V1-eSA-16-TH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-TH | 14.6803 | 2.6653 | 788.6552 | 0 | 3.4688 | 788.6552 | 905.589
DEER-SFAM-CZ16-V1-eSA-16-TL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSA-16 | CZ16-V1-eSA-16-TL | 15.8593 | 2.438 | 709.4147 | 0 | 3.4688 | 709.4147 | 836.5315
DEER-SFAM-CZ16-V1-eSA-17-CH-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-CH | 15.9063 | 2.4808 | 705.6074 | 0 | 3.4688 | 705.6074 | 933.4831
DEER-SFAM-CZ16-V1-eSA-17-CL-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-CL | 15.8347 | 2.5123 | 708.9094 | 0 | 3.4688 | 708.9094 | 936.7173
DEER-SFAM-CZ16-V1-eSA-17-CM-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-CM | 15.9818 | 2.5104 | 715.4217 | 0 | 3.4688 | 715.4217 | 894.0434
DEER-SFAM-CZ16-V1-eSA-17-LH-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-LH | 15.3738 | 2.1801 | 636.5686 | 0 | 3.4688 | 636.5686 | 884.9452
DEER-SFAM-CZ16-V1-eSA-17-LL-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-LL | 15.1957 | 2.2948 | 663.2736 | 0 | 3.4688 | 663.2736 | 799.1325
DEER-SFAM-CZ16-V1-eSA-17-LM-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-LM | 14.9533 | 2.2827 | 671.2841 | 0 | 3.4688 | 671.2841 | 788.6142
DEER-SFAM-CZ16-V1-eSA-17-TH-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-TH | 17.0422 | 2.2585 | 658.8145 | 0 | 3.4688 | 658.8145 | 846.873
DEER-SFAM-CZ16-V1-eSA-17-TL-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-TL | 17.7992 | 2.2041 | 596.9243 | 0 | 3.4688 | 596.9243 | 885.8937
DEER-SFAM-CZ16-V1-eSA-17-TM-s2 | 17 | CZ16 | V1 | CZ16-V1-eSA-17 | CZ16-V1-eSA-17-TM | 17.1686 | 2.3687 | 708.7108 | 0 | 3.4688 | 708.7108 | 806.7351
DEER-SFAM-CZ16-V1-eSA-18-LH-s2 | 18 | CZ16 | V1 | CZ16-V1-eSA-18 | CZ16-V1-eSA-18-LH | 16.0681 | 2.1092 | 620.4157 | 0 | 3.4688 | 620.4157 | 783.775
DEER-SFAM-CZ16-V1-eSA-18-LL-s2 | 18 | CZ16 | V1 | CZ16-V1-eSA-18 | CZ16-V1-eSA-18-LL | 16.4414 | 2.1019 | 600.6454 | 0 | 3.4688 | 600.6454 | 813.7618
DEER-SFAM-CZ16-V1-eSA-18-TH-s2 | 18 | CZ16 | V1 | CZ16-V1-eSA-18 | CZ16-V1-eSA-18-TH | 17.7351 | 2.1416 | 638.504 | 0 | 3.4688 | 638.504 | 766.722
DEER-SFAM-CZ16-V1-eSA-18-TL-s2 | 18 | CZ16 | V1 | CZ16-V1-eSA-18 | CZ16-V1-eSA-18-TL | 17.0754 | 2.3688 | 671.397 | 0 | 3.4688 | 671.397 | 809.7781
DEER-SFAM-CZ16-V1-eSA-18-TM-s2 | 18 | CZ16 | V1 | CZ16-V1-eSA-18 | CZ16-V1-eSA-18-TM | 16.7662 | 2.2354 | 663.9509 | 0 | 3.4688 | 663.9509 | 794.7356
DEER-SFAM-CZ16-V1-eSH-10-HH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-HH | 10.4813 | 3.148 | 914.8272 | 15107.8103 | 3.4688 | 16022.6376 | 2130.2635
DEER-SFAM-CZ16-V1-eSH-10-HL-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-HL | 10.2228 | 3.3048 | 941.0499 | 14807.9054 | 3.4688 | 15748.9553 | 2121.8866
DEER-SFAM-CZ16-V1-eSH-10-HM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-HM | 10.6069 | 3.2329 | 933.1498 | 14498.7289 | 3.4688 | 15431.8787 | 2074.6611
DEER-SFAM-CZ16-V1-eSH-10-LH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-LH | 10.5054 | 3.0992 | 927.3658 | 15836.5603 | 3.4688 | 16763.926 | 2142.7196
DEER-SFAM-CZ16-V1-eSH-10-LL-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-LL | 10.5834 | 3.2165 | 929.084 | 16333.9049 | 3.4688 | 17262.9889 | 2231.7429
DEER-SFAM-CZ16-V1-eSH-10-LM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-LM | 10.7733 | 3.0828 | 914.2293 | 15571.29 | 3.4688 | 16485.5193 | 2109.5558
DEER-SFAM-CZ16-V1-eSH-10-MH-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-MH | 10.6077 | 3.1756 | 924.5174 | 16024.5666 | 3.4688 | 16949.084 | 2230.8315
DEER-SFAM-CZ16-V1-eSH-10-ML-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-ML | 10.605 | 3.3205 | 934.868 | 15721.3204 | 3.4688 | 16656.1884 | 2180.2165
DEER-SFAM-CZ16-V1-eSH-10-MM-s1 | 10 | CZ16 | V1 | CZ16-V1-eSH-10 | CZ16-V1-eSH-10-MM | 10.5116 | 3.2509 | 937.879 | 15059.9462 | 3.4688 | 15997.8252 | 2057.7387
DEER-SFAM-CZ16-V1-eSH-13-HH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-HH | 13.3019 | 2.6025 | 736.6711 | 15514.7197 | 3.4688 | 16251.3908 | 1789.1212
DEER-SFAM-CZ16-V1-eSH-13-HL-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-HL | 13.8282 | 2.6382 | 708.7217 | 13701.8556 | 3.711 | 14410.5773 | 1819.9435
DEER-SFAM-CZ16-V1-eSH-13-HM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-HM | 13.5927 | 2.5539 | 721.9376 | 14135.9354 | 3.4688 | 14857.873 | 1708.0168
DEER-SFAM-CZ16-V1-eSH-13-LH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-LH | 13.0627 | 2.5209 | 729.3994 | 17539.0407 | 3.4688 | 18268.4401 | 2232.2608
DEER-SFAM-CZ16-V1-eSH-13-LL-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-LL | 14.5008 | 2.4231 | 678.3347 | 14910.1867 | 3.4688 | 15588.5214 | 1662.0072
DEER-SFAM-CZ16-V1-eSH-13-LM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-LM | 12.5272 | 2.6581 | 756.3495 | 12334.9325 | 3.4688 | 13091.282 | 1895.4993
DEER-SFAM-CZ16-V1-eSH-13-MH-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-MH | 14.0707 | 2.4419 | 690.7162 | 15805.5433 | 3.4688 | 16496.2594 | 1733.2407
DEER-SFAM-CZ16-V1-eSH-13-ML-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-ML | 12.5339 | 2.7714 | 759.6213 | 15097.6221 | 3.4688 | 15857.2434 | 1857.6987
DEER-SFAM-CZ16-V1-eSH-13-MM-s1 | 13 | CZ16 | V1 | CZ16-V1-eSH-13 | CZ16-V1-eSH-13-MM | 13.7064 | 2.5792 | 716.6917 | 14224.0433 | 3.4688 | 14940.735 | 1570.947
DEER-SFAM-CZ16-V1-eSH-14-HH-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-HH | 14.1462 | 2.4856 | 693.3351 | 14672.0118 | 3.4688 | 15365.3469 | 1504.6275
DEER-SFAM-CZ16-V1-eSH-14-HL-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-HL | 14.554 | 2.4618 | 673.9682 | 15156.6762 | 3.4688 | 15830.6444 | 1642.3004
DEER-SFAM-CZ16-V1-eSH-14-HM-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-HM | 14.4011 | 2.4063 | 677.7943 | 15041.6191 | 3.4688 | 15719.4134 | 1374.8337
DEER-SFAM-CZ16-V1-eSH-14-MH-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-MH | 13.9487 | 2.3439 | 679.8245 | 16613.2555 | 3.4688 | 17293.08 | 1697.7613
DEER-SFAM-CZ16-V1-eSH-14-ML-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-ML | 14.1296 | 2.4169 | 667.544 | 17656.1993 | 3.4688 | 18323.7433 | 1949.8628
DEER-SFAM-CZ16-V1-eSH-14-MM-s1 | 14 | CZ16 | V1 | CZ16-V1-eSH-14 | CZ16-V1-eSH-14-MM | 13.8643 | 2.4167 | 676.3509 | 15001.4915 | 3.4688 | 15677.8423 | 1584.1876
DEER-SFAM-CZ16-V1-eSH-15-HH-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-HH | 15.5394 | 2.2174 | 625.5544 | 17397.7937 | 3.4688 | 18023.3481 | 1312.3655
DEER-SFAM-CZ16-V1-eSH-15-HL-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-HL | 15.6563 | 2.2716 | 629.3065 | 13016.4831 | 3.4688 | 13645.7895 | 1390.8916
DEER-SFAM-CZ16-V1-eSH-15-HM-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-HM | 15.7011 | 2.248 | 614.8561 | 13701.3102 | 3.4688 | 14316.1663 | 1353.6474
DEER-SFAM-CZ16-V1-eSH-15-MH-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-MH | 14.6802 | 2.3581 | 645.4469 | 16106.7719 | 3.4688 | 16752.2188 | 1345.8816
DEER-SFAM-CZ16-V1-eSH-15-ML-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-ML | 15.1773 | 2.2585 | 621.7368 | 15966.5423 | 3.4688 | 16588.279 | 1369.9826
DEER-SFAM-CZ16-V1-eSH-15-MM-s1 | 15 | CZ16 | V1 | CZ16-V1-eSH-15 | CZ16-V1-eSH-15-MM | 16.0763 | 2.2338 | 607.1757 | 16049.0133 | 3.4688 | 16656.189 | 1380.6517
DEER-SFAM-CZ16-V1-eSH-16-CH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-CH | 15.3195 | 2.5593 | 745.8301 | 16403.184 | 3.4688 | 17149.0141 | 1681.8398
DEER-SFAM-CZ16-V1-eSH-16-CL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-CL | 15.4604 | 2.6047 | 740.068 | 15578.3322 | 3.4688 | 16318.4001 | 1728.4722
DEER-SFAM-CZ16-V1-eSH-16-LH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-LH | 14.7418 | 2.1768 | 661.1358 | 16748.517 | 3.4688 | 17409.6528 | 1596.2142
DEER-SFAM-CZ16-V1-eSH-16-LL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-LL | 14.4081 | 2.3895 | 691.6875 | 16212.5573 | 3.4688 | 16904.2447 | 1540.1297
DEER-SFAM-CZ16-V1-eSH-16-LM-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-LM | 14.2258 | 2.3201 | 693.5649 | 17131.1413 | 3.4688 | 17824.7062 | 1753.5639
DEER-SFAM-CZ16-V1-eSH-16-TH-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-TH | 16.2059 | 2.3923 | 693.3305 | 19405.6797 | 3.4688 | 20099.0102 | 1801.6828
DEER-SFAM-CZ16-V1-eSH-16-TL-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-TL | 14.9886 | 2.7342 | 774.9265 | 18854.8207 | 3.4688 | 19629.7471 | 1792.4916
DEER-SFAM-CZ16-V1-eSH-16-TM-s2 | 16 | CZ16 | V1 | CZ16-V1-eSH-16 | CZ16-V1-eSH-16-TM | 15.2554 | 2.6753 | 761.7302 | 18915.3055 | 3.4688 | 19677.0358 | 1790.4204
DEER-SFAM-CZ16-V1-eSH-17-CM-s2 | 17 | CZ16 | V1 | CZ16-V1-eSH-17 | CZ16-V1-eSH-17-CM | 16.3648 | 2.4624 | 698.1241 | 15548.0864 | 3.4688 | 16246.2104 | 1712.4259
DEER-SFAM-CZ16-V1-eSH-17-LM-s2 | 17 | CZ16 | V1 | CZ16-V1-eSH-17 | CZ16-V1-eSH-17-LM | 15.2796 | 2.2631 | 667.8752 | 15702.4092 | 3.4688 | 16370.2845 | 1142.8656
DEER-SFAM-CZ16-V1-eSH-17-TH-s2 | 17 | CZ16 | V1 | CZ16-V1-eSH-17 | CZ16-V1-eSH-17-TH | 17.0967 | 2.2741 | 653.6741 | 19335.6903 | 3.4688 | 19989.3644 | 1784.529
DEER-SFAM-CZ16-V1-eSH-17-TL-s2 | 17 | CZ16 | V1 | CZ16-V1-eSH-17 | CZ16-V1-eSH-17-TL | 17.0005 | 2.3237 | 660.2676 | 19386.8719 | 3.4688 | 20047.1395 | 1793.7888
DEER-SFAM-CZ16-V1-eSH-18-LH-s2 | 18 | CZ16 | V1 | CZ16-V1-eSH-18 | CZ16-V1-eSH-18-LH | 16.0774 | 2.1581 | 616.5971 | 17871.4467 | 3.4688 | 18488.0438 | 1425.7954
DEER-SFAM-CZ16-V1-eSH-18-LL-s2 | 18 | CZ16 | V1 | CZ16-V1-eSH-18 | CZ16-V1-eSH-18-LL | 15.3145 | 2.2577 | 644.0984 | 16515.8815 | 3.4688 | 17159.9798 | 1357.066
DEER-SFAM-CZ16-V1-eSH-18-LM-s2 | 18 | CZ16 | V1 | CZ16-V1-eSH-18 | CZ16-V1-eSH-18-LM | 16.2191 | 2.1681 | 620.5244 | 18648.2574 | 3.4688 | 19268.7818 | 1532.468
DEER-SFAM-CZ16-V1-eSH-18-TM-s2 | 18 | CZ16 | V1 | CZ16-V1-eSH-18 | CZ16-V1-eSH-18-TM | 17.5811 | 2.3394 | 642.9518 | 19626.7542 | 3.4688 | 20269.706 | 2159.4581
DEER-SFAM-CZ16-V2-eSA-10-HH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-HH | 10.18 | 2.4246 | 573.3603 | 0 | 3.1141 | 573.3603 | 869.4549
DEER-SFAM-CZ16-V2-eSA-10-HL-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-HL | 10.3107 | 2.5682 | 578.9741 | 0 | 3.1141 | 578.9741 | 875.2022
DEER-SFAM-CZ16-V2-eSA-10-HM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-HM | 9.9938 | 2.5066 | 579.7443 | 0 | 3.1141 | 579.7443 | 875.9437
DEER-SFAM-CZ16-V2-eSA-10-LH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-LH | 10.468 | 2.4323 | 565.6068 | 0 | 3.1141 | 565.6068 | 861.9856
DEER-SFAM-CZ16-V2-eSA-10-LL-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-LL | 10.5387 | 2.504 | 569.6315 | 0 | 3.1141 | 569.6315 | 865.8963
DEER-SFAM-CZ16-V2-eSA-10-LM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-LM | 10.438 | 2.4372 | 564.0834 | 0 | 3.1141 | 564.0834 | 860.469
DEER-SFAM-CZ16-V2-eSA-10-MH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-MH | 10.216 | 2.3995 | 575.8551 | 0 | 3.1141 | 575.8551 | 872.1845
DEER-SFAM-CZ16-V2-eSA-10-ML-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-ML | 10.2569 | 2.5458 | 583.7347 | 0 | 3.1141 | 583.7347 | 879.9674
DEER-SFAM-CZ16-V2-eSA-10-MM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSA-10 | CZ16-V2-eSA-10-MM | 10.0875 | 2.4848 | 569.4785 | 0 | 3.1141 | 569.4785 | 865.7266
DEER-SFAM-CZ16-V2-eSA-13-HH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-HH | 13.3864 | 1.9676 | 442.565 | 0 | 3.1141 | 442.565 | 709.5831
DEER-SFAM-CZ16-V2-eSA-13-HL-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-HL | 12.7813 | 2.0001 | 444.6627 | 0 | 3.1141 | 444.6627 | 678.3701
DEER-SFAM-CZ16-V2-eSA-13-HM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-HM | 13.8013 | 1.9339 | 431.9282 | 0 | 3.1141 | 431.9282 | 698.889
DEER-SFAM-CZ16-V2-eSA-13-LH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-LH | 13.2734 | 1.8344 | 433.6661 | 0 | 3.1141 | 433.6661 | 729.9414
DEER-SFAM-CZ16-V2-eSA-13-LL-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-LL | 13.1365 | 1.9495 | 444.4496 | 0 | 3.1141 | 444.4496 | 740.3848
DEER-SFAM-CZ16-V2-eSA-13-LM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-LM | 12.7373 | 1.964 | 454.1313 | 0 | 3.1141 | 454.1313 | 750.2753
DEER-SFAM-CZ16-V2-eSA-13-MH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-MH | 13.9201 | 1.8645 | 429.084 | 0 | 3.1141 | 429.084 | 725.2845
DEER-SFAM-CZ16-V2-eSA-13-ML-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-ML | 12.486 | 1.9448 | 439.9743 | 0 | 3.1141 | 439.9743 | 735.3222
DEER-SFAM-CZ16-V2-eSA-13-MM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSA-13 | CZ16-V2-eSA-13-MM | 14.2514 | 1.803 | 415.3673 | 0 | 3.1141 | 415.3673 | 711.5438
DEER-SFAM-CZ16-V2-eSA-14-HH-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-HH | 12.7796 | 1.8734 | 429.1 | 0 | 3.1141 | 429.1 | 677.3709
DEER-SFAM-CZ16-V2-eSA-14-HL-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-HL | 14.434 | 1.8041 | 407.9318 | 0 | 3.1141 | 407.9318 | 590.4887
DEER-SFAM-CZ16-V2-eSA-14-HM-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-HM | 13.5186 | 1.9319 | 427.257 | 0 | 3.1141 | 427.257 | 707.291
DEER-SFAM-CZ16-V2-eSA-14-MH-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-MH | 13.7111 | 1.8452 | 431.0795 | 0 | 3.1141 | 431.0795 | 625.7566
DEER-SFAM-CZ16-V2-eSA-14-ML-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-ML | 13.3364 | 1.8601 | 418.9158 | 0 | 3.1141 | 418.9158 | 729.7332
DEER-SFAM-CZ16-V2-eSA-14-MM-s1 | 14 | CZ16 | V2 | CZ16-V2-eSA-14 | CZ16-V2-eSA-14-MM | 13.6735 | 1.8333 | 420.8924 | 0 | 3.1141 | 420.8924 | 634.2766
DEER-SFAM-CZ16-V2-eSA-15-HH-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-HH | 15.7504 | 1.6807 | 378.2503 | 0 | 3.1141 | 378.2503 | 585.1916
DEER-SFAM-CZ16-V2-eSA-15-HL-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-HL | 15.7152 | 1.6773 | 371.1575 | 0 | 3.1141 | 371.1575 | 629.1504
DEER-SFAM-CZ16-V2-eSA-15-HM-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-HM | 15.6224 | 1.664 | 378.3369 | 0 | 3.1141 | 378.3369 | 586.0597
DEER-SFAM-CZ16-V2-eSA-15-MH-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-MH | 13.8992 | 1.7652 | 400.3349 | 0 | 3.1141 | 400.3349 | 554.5298
DEER-SFAM-CZ16-V2-eSA-15-ML-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-ML | 15.2386 | 1.7072 | 385.1961 | 0 | 3.1141 | 385.1961 | 592.7223
DEER-SFAM-CZ16-V2-eSA-15-MM-s1 | 15 | CZ16 | V2 | CZ16-V2-eSA-15 | CZ16-V2-eSA-15-MM | 14.5749 | 1.7243 | 387.4086 | 0 | 3.1141 | 387.4086 | 576.4897
DEER-SFAM-CZ16-V2-eSA-16-CH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-CH | 14.8549 | 1.9546 | 462.218 | 0 | 3.1141 | 462.218 | 580.075
DEER-SFAM-CZ16-V2-eSA-16-CL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-CL | 15.3143 | 1.8456 | 441.4281 | 0 | 3.1141 | 441.4281 | 590.8222
DEER-SFAM-CZ16-V2-eSA-16-CM-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-CM | 15.0192 | 1.8953 | 453.1301 | 0 | 3.1141 | 453.1301 | 610.9585
DEER-SFAM-CZ16-V2-eSA-16-LH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-LH | 14.5904 | 1.5761 | 403.714 | 0 | 3.1141 | 403.714 | 607.6998
DEER-SFAM-CZ16-V2-eSA-16-LL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-LL | 14.1449 | 1.7066 | 424.5718 | 0 | 3.1141 | 424.5718 | 559.1517
DEER-SFAM-CZ16-V2-eSA-16-LM-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-LM | 14.0783 | 1.7063 | 424.705 | 0 | 3.1141 | 424.705 | 546.7064
DEER-SFAM-CZ16-V2-eSA-16-NM-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-NM | 15.4513 | 1.5322 | 395.0208 | 0 | 3.1141 | 395.0208 | 514.7832
DEER-SFAM-CZ16-V2-eSA-16-TH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-TH | 14.1872 | 1.9693 | 491.3218 | 0 | 3.1141 | 491.3218 | 567.7892
DEER-SFAM-CZ16-V2-eSA-16-TL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSA-16 | CZ16-V2-eSA-16-TL | 15.5815 | 1.7433 | 432.1764 | 0 | 3.1141 | 432.1764 | 514.9455
DEER-SFAM-CZ16-V2-eSA-17-CH-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-CH | 15.8103 | 1.8163 | 426.0171 | 0 | 3.1141 | 426.0171 | 575.3336
DEER-SFAM-CZ16-V2-eSA-17-CL-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-CL | 15.7976 | 1.8215 | 426.4947 | 0 | 3.1141 | 426.4947 | 575.778
DEER-SFAM-CZ16-V2-eSA-17-CM-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-CM | 15.9324 | 1.833 | 430.5052 | 0 | 3.1141 | 430.5052 | 548.0048
DEER-SFAM-CZ16-V2-eSA-17-LH-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-LH | 14.9422 | 1.5726 | 392.6928 | 0 | 3.1141 | 392.6928 | 552.8554
DEER-SFAM-CZ16-V2-eSA-17-LL-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-LL | 14.8981 | 1.6553 | 406.1743 | 0 | 3.1141 | 406.1743 | 493.5167
DEER-SFAM-CZ16-V2-eSA-17-LM-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-LM | 14.6455 | 1.6532 | 410.8871 | 0 | 3.1141 | 410.8871 | 486.4024
DEER-SFAM-CZ16-V2-eSA-17-TH-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-TH | 16.3411 | 1.6826 | 414.5147 | 0 | 3.1141 | 414.5147 | 536.964
DEER-SFAM-CZ16-V2-eSA-17-TL-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-TL | 17.4794 | 1.5451 | 366.0376 | 0 | 3.1141 | 366.0376 | 555.596
DEER-SFAM-CZ16-V2-eSA-17-TM-s2 | 17 | CZ16 | V2 | CZ16-V2-eSA-17 | CZ16-V2-eSA-17-TM | 16.7279 | 1.7566 | 434.0143 | 0 | 3.1141 | 434.0143 | 497.8328
DEER-SFAM-CZ16-V2-eSA-18-LH-s2 | 18 | CZ16 | V2 | CZ16-V2-eSA-18 | CZ16-V2-eSA-18-LH | 15.6512 | 1.5234 | 381.6407 | 0 | 3.1141 | 381.6407 | 486.8586
DEER-SFAM-CZ16-V2-eSA-18-LL-s2 | 18 | CZ16 | V2 | CZ16-V2-eSA-18 | CZ16-V2-eSA-18-LL | 16.1229 | 1.5096 | 367.2849 | 0 | 3.1141 | 367.2849 | 504.6413
DEER-SFAM-CZ16-V2-eSA-18-TH-s2 | 18 | CZ16 | V2 | CZ16-V2-eSA-18 | CZ16-V2-eSA-18-TH | 16.9733 | 1.5889 | 402.2572 | 0 | 3.1141 | 402.2572 | 485.588
DEER-SFAM-CZ16-V2-eSA-18-TL-s2 | 18 | CZ16 | V2 | CZ16-V2-eSA-18 | CZ16-V2-eSA-18-TL | 16.5445 | 1.7762 | 416.4223 | 0 | 3.1141 | 416.4223 | 507.0926
DEER-SFAM-CZ16-V2-eSA-18-TM-s2 | 18 | CZ16 | V2 | CZ16-V2-eSA-18 | CZ16-V2-eSA-18-TM | 16.187 | 1.651 | 414.5625 | 0 | 3.1141 | 414.5625 | 499.6611
DEER-SFAM-CZ16-V2-eSH-10-HH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-HH | 10.3548 | 2.3675 | 560.8159 | 8448.7332 | 3.1141 | 9009.5491 | 1367.1824
DEER-SFAM-CZ16-V2-eSH-10-HL-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-HL | 10.1402 | 2.466 | 574.1137 | 8310.2686 | 3.1141 | 8884.3823 | 1346.9126
DEER-SFAM-CZ16-V2-eSH-10-HM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-HM | 10.5251 | 2.4123 | 568.2461 | 8177.5477 | 3.1141 | 8745.7938 | 1316.269
DEER-SFAM-CZ16-V2-eSH-10-LH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-LH | 10.3991 | 2.3536 | 567.7254 | 8888.842 | 3.1141 | 9456.5674 | 1389.0089
DEER-SFAM-CZ16-V2-eSH-10-LL-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-LL | 10.5405 | 2.3975 | 563.3753 | 9192.7299 | 3.1141 | 9756.1052 | 1432.9396
DEER-SFAM-CZ16-V2-eSH-10-LM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-LM | 10.6636 | 2.321 | 557.9255 | 8799.8582 | 3.1141 | 9357.7837 | 1354.4167
DEER-SFAM-CZ16-V2-eSH-10-MH-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-MH | 10.5473 | 2.3925 | 563.5157 | 8996.8963 | 3.1141 | 9560.412 | 1440.0029
DEER-SFAM-CZ16-V2-eSH-10-ML-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-ML | 10.5785 | 2.4683 | 566.1556 | 8944.3394 | 3.1141 | 9510.4951 | 1395.6491
DEER-SFAM-CZ16-V2-eSH-10-MM-s1 | 10 | CZ16 | V2 | CZ16-V2-eSH-10 | CZ16-V2-eSH-10-MM | 10.4599 | 2.4508 | 569.9492 | 8456.5006 | 3.1141 | 9026.4498 | 1309.6111
DEER-SFAM-CZ16-V2-eSH-13-HH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-HH | 13.0396 | 1.9693 | 453.9841 | 8647.0506 | 3.1141 | 9101.0347 | 1175.2369
DEER-SFAM-CZ16-V2-eSH-13-HL-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-HL | 13.8175 | 1.9643 | 429.8304 | 7617.1123 | 3.1141 | 8046.9426 | 1162.4557
DEER-SFAM-CZ16-V2-eSH-13-HM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-HM | 13.3898 | 1.9211 | 442.7174 | 7742.8766 | 3.1141 | 8185.594 | 1106.5068
DEER-SFAM-CZ16-V2-eSH-13-LH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-LH | 12.9713 | 1.902 | 445.0723 | 9773.2186 | 3.1141 | 10218.2909 | 1500.9682
DEER-SFAM-CZ16-V2-eSH-13-LL-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-LL | 14.347 | 1.8196 | 414.605 | 8083.1752 | 3.1141 | 8497.7802 | 1083.1156
DEER-SFAM-CZ16-V2-eSH-13-LM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-LM | 12.4887 | 2.0038 | 459.1836 | 6539.6188 | 3.1141 | 6998.8024 | 1211.9812
DEER-SFAM-CZ16-V2-eSH-13-MH-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-MH | 13.7728 | 1.8527 | 427.0307 | 8721.4856 | 3.1141 | 9148.5163 | 1137.3525
DEER-SFAM-CZ16-V2-eSH-13-ML-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-ML | 12.5446 | 2.0695 | 459.199 | 8159.5146 | 3.1141 | 8618.7135 | 1197.2082
DEER-SFAM-CZ16-V2-eSH-13-MM-s1 | 13 | CZ16 | V2 | CZ16-V2-eSH-13 | CZ16-V2-eSH-13-MM | 13.604 | 1.919 | 436.4441 | 7861.5772 | 3.1141 | 8298.0213 | 1006.9943
DEER-SFAM-CZ16-V2-eSH-14-HH-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-HH | 13.9135 | 1.8743 | 425.9042 | 8057.9317 | 3.1141 | 8483.8359 | 978.2357
DEER-SFAM-CZ16-V2-eSH-14-HL-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-HL | 14.4505 | 1.8377 | 410.1761 | 8240.2927 | 3.1141 | 8650.4688 | 1070.052
DEER-SFAM-CZ16-V2-eSH-14-HM-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-HM | 14.1998 | 1.8138 | 415.3229 | 8237.9224 | 3.1141 | 8653.2453 | 891.786
DEER-SFAM-CZ16-V2-eSH-14-MH-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-MH | 13.8599 | 1.764 | 414.5546 | 9208.1401 | 3.1141 | 9622.6946 | 1128.3494
DEER-SFAM-CZ16-V2-eSH-14-ML-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-ML | 14.1728 | 1.7831 | 403.7865 | 9653.3046 | 3.1141 | 10057.091 | 1295.5547
DEER-SFAM-CZ16-V2-eSH-14-MM-s1 | 14 | CZ16 | V2 | CZ16-V2-eSH-14 | CZ16-V2-eSH-14-MM | 13.8792 | 1.7947 | 409.3387 | 8094.1102 | 3.1141 | 8503.4489 | 1027.3732
DEER-SFAM-CZ16-V2-eSH-15-HH-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-HH | 15.2373 | 1.6805 | 385.5338 | 9769.5128 | 3.1141 | 10155.0466 | 876.7148
DEER-SFAM-CZ16-V2-eSH-15-HL-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-HL | 15.5228 | 1.7026 | 383.6472 | 6925.668 | 3.1141 | 7309.3152 | 892.9075
DEER-SFAM-CZ16-V2-eSH-15-HM-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-HM | 15.5271 | 1.6761 | 375.7529 | 7330.8212 | 3.1141 | 7706.5741 | 875.3759
DEER-SFAM-CZ16-V2-eSH-15-MH-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-MH | 14.6478 | 1.7516 | 392.3304 | 8585.9414 | 3.1141 | 8978.2718 | 873.4189
DEER-SFAM-CZ16-V2-eSH-15-ML-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-ML | 15.2439 | 1.6642 | 375.4711 | 8504.3919 | 3.1141 | 8879.8631 | 886.4538
DEER-SFAM-CZ16-V2-eSH-15-MM-s1 | 15 | CZ16 | V2 | CZ16-V2-eSH-15 | CZ16-V2-eSH-15-MM | 15.8774 | 1.6696 | 371.4832 | 8873.1894 | 3.1141 | 9244.6726 | 909.092
DEER-SFAM-CZ16-V2-eSH-16-CH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-CH | 15.1288 | 1.873 | 453.6229 | 9556.2564 | 3.1141 | 10009.8793 | 1085.1463
DEER-SFAM-CZ16-V2-eSH-16-CL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-CL | 15.3394 | 1.913 | 447.479 | 8969.8052 | 3.1141 | 9417.2842 | 1103.8685
DEER-SFAM-CZ16-V2-eSH-16-LH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-LH | 14.1438 | 1.5938 | 412.5701 | 9511.8457 | 3.1141 | 9924.4158 | 1011.0679
DEER-SFAM-CZ16-V2-eSH-16-LL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-LL | 14.1363 | 1.7257 | 422.8001 | 9073.4773 | 3.1141 | 9496.2774 | 937.6269
DEER-SFAM-CZ16-V2-eSH-16-LM-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-LM | 13.718 | 1.6863 | 430.6906 | 9723.0679 | 3.1141 | 10153.7585 | 1105.7176
DEER-SFAM-CZ16-V2-eSH-16-TH-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-TH | 15.5949 | 1.7263 | 434.6877 | 11742.1712 | 3.1141 | 12176.8589 | 1189.8779
DEER-SFAM-CZ16-V2-eSH-16-TL-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-TL | 14.7976 | 2.0389 | 472.4407 | 11330.7449 | 3.1141 | 11803.1857 | 1163.0669
DEER-SFAM-CZ16-V2-eSH-16-TM-s2 | 16 | CZ16 | V2 | CZ16-V2-eSH-16 | CZ16-V2-eSH-16-TM | 15.0257 | 1.9955 | 465.3197 | 11387.2774 | 3.1141 | 11852.5972 | 1167.9205
DEER-SFAM-CZ16-V2-eSH-17-CM-s2 | 17 | CZ16 | V2 | CZ16-V2-eSH-17 | CZ16-V2-eSH-17-CM | 16.2357 | 1.8085 | 422.1536 | 8787.6232 | 3.1141 | 9209.7769 | 1070.1716
DEER-SFAM-CZ16-V2-eSH-17-LM-s2 | 17 | CZ16 | V2 | CZ16-V2-eSH-17 | CZ16-V2-eSH-17-LM | 14.8972 | 1.667 | 411.6715 | 8727.9333 | 3.1141 | 9139.6048 | 698.9686
DEER-SFAM-CZ16-V2-eSH-17-TH-s2 | 17 | CZ16 | V2 | CZ16-V2-eSH-17 | CZ16-V2-eSH-17-TH | 16.5322 | 1.6624 | 408.0341 | 11712.3462 | 3.1141 | 12120.3803 | 1192.1585
DEER-SFAM-CZ16-V2-eSH-17-TL-s2 | 17 | CZ16 | V2 | CZ16-V2-eSH-17 | CZ16-V2-eSH-17-TL | 16.4959 | 1.6877 | 411.0384 | 11723.708 | 3.1141 | 12134.7464 | 1193.2712
DEER-SFAM-CZ16-V2-eSH-18-LH-s2 | 18 | CZ16 | V2 | CZ16-V2-eSH-18 | CZ16-V2-eSH-18-LH | 15.7213 | 1.5739 | 378.0353 | 10340.8599 | 3.1141 | 10718.8952 | 895.996
DEER-SFAM-CZ16-V2-eSH-18-LL-s2 | 18 | CZ16 | V2 | CZ16-V2-eSH-18 | CZ16-V2-eSH-18-LL | 14.9957 | 1.6434 | 394.3312 | 9264.6113 | 3.1141 | 9658.9425 | 836.8215
DEER-SFAM-CZ16-V2-eSH-18-LM-s2 | 18 | CZ16 | V2 | CZ16-V2-eSH-18 | CZ16-V2-eSH-18-LM | 15.837 | 1.5648 | 381.1448 | 10892.6548 | 3.1141 | 11273.7996 | 974.5451
DEER-SFAM-CZ16-V2-eSH-18-TM-s2 | 18 | CZ16 | V2 | CZ16-V2-eSH-18 | CZ16-V2-eSH-18-TM | 16.9839 | 1.8163 | 405.0332 | 11895.5981 | 3.1141 | 12300.6313 | 1481.5718
DEER-SFAM-CZ16-V3-eSA-10-HH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-HH | 10.0938 | 3.3575 | 1256.8617 | 0 | 3.4 | 1256.8617 | 1571.3016
DEER-SFAM-CZ16-V3-eSA-10-HL-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-HL | 10.3794 | 3.6354 | 1258.5691 | 0 | 3.4 | 1258.5691 | 1573.1622
DEER-SFAM-CZ16-V3-eSA-10-HM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-HM | 10.1232 | 3.5161 | 1260.4607 | 0 | 3.4 | 1260.4607 | 1575.0294
DEER-SFAM-CZ16-V3-eSA-10-LH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-LH | 10.225 | 3.3819 | 1249.4581 | 0 | 3.4 | 1249.4581 | 1564.1387
DEER-SFAM-CZ16-V3-eSA-10-LL-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-LL | 10.4665 | 3.58 | 1254.4041 | 0 | 3.4 | 1254.4041 | 1569.0342
DEER-SFAM-CZ16-V3-eSA-10-LM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-LM | 10.2076 | 3.383 | 1246.6085 | 0 | 3.4 | 1246.6085 | 1561.2969
DEER-SFAM-CZ16-V3-eSA-10-MH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-MH | 10.1413 | 3.2915 | 1253.5228 | 0 | 3.4 | 1253.5228 | 1568.1752
DEER-SFAM-CZ16-V3-eSA-10-ML-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-ML | 10.1803 | 3.5915 | 1281.3662 | 0 | 3.4 | 1281.3662 | 1595.964
DEER-SFAM-CZ16-V3-eSA-10-MM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSA-10 | CZ16-V3-eSA-10-MM | 9.9326 | 3.3155 | 1260.3802 | 0 | 3.4 | 1260.3802 | 1574.9953
DEER-SFAM-CZ16-V3-eSA-13-HH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-HH | 13.4476 | 2.7231 | 964.2353 | 0 | 3.4 | 964.2353 | 1247.8123
DEER-SFAM-CZ16-V3-eSA-13-HL-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-HL | 12.5286 | 2.9021 | 991.7248 | 0 | 3.4 | 991.7248 | 1239.9366
DEER-SFAM-CZ16-V3-eSA-13-HM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-HM | 13.8888 | 2.795 | 941.8388 | 0 | 3.4 | 941.8388 | 1225.3594
DEER-SFAM-CZ16-V3-eSA-13-LH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-LH | 13.166 | 2.5721 | 950.4643 | 0 | 3.4 | 950.4643 | 1265.0845
DEER-SFAM-CZ16-V3-eSA-13-LL-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-LL | 12.8461 | 2.7626 | 989.3693 | 0 | 3.4 | 989.3693 | 1303.6506
DEER-SFAM-CZ16-V3-eSA-13-LM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-LM | 12.4877 | 2.7313 | 1005.2087 | 0 | 3.4 | 1005.2087 | 1319.6941
DEER-SFAM-CZ16-V3-eSA-13-MH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-MH | 14.0969 | 2.6444 | 920.3343 | 0 | 3.4 | 920.3343 | 1234.9042
DEER-SFAM-CZ16-V3-eSA-13-ML-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-ML | 12.3919 | 2.7965 | 976.6126 | 0 | 3.4 | 976.6126 | 1290.2477
DEER-SFAM-CZ16-V3-eSA-13-MM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSA-13 | CZ16-V3-eSA-13-MM | 14.496 | 2.575 | 891.9896 | 0 | 3.4 | 891.9896 | 1206.5298
DEER-SFAM-CZ16-V3-eSA-14-HH-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-HH | 12.8531 | 2.6627 | 941.6902 | 0 | 3.4 | 941.6902 | 1205.3637
DEER-SFAM-CZ16-V3-eSA-14-HL-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-HL | 14.2879 | 2.6404 | 895.8685 | 0 | 3.4 | 895.8685 | 1089.7601
DEER-SFAM-CZ16-V3-eSA-14-HM-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-HM | 13.278 | 2.7733 | 950.0374 | 0 | 3.4 | 950.0374 | 1247.4147
DEER-SFAM-CZ16-V3-eSA-14-MH-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-MH | 13.4261 | 2.5436 | 950.4295 | 0 | 3.4 | 950.4295 | 1157.1823
DEER-SFAM-CZ16-V3-eSA-14-ML-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-ML | 13.1664 | 2.6595 | 928.638 | 0 | 3.4 | 928.638 | 1258.7283
DEER-SFAM-CZ16-V3-eSA-14-MM-s1 | 14 | CZ16 | V3 | CZ16-V3-eSA-14 | CZ16-V3-eSA-14-MM | 13.4914 | 2.5398 | 926.7099 | 0 | 3.4 | 926.7099 | 1153.3401
DEER-SFAM-CZ16-V3-eSA-15-HH-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-HH | 16.0908 | 2.3637 | 812.6217 | 0 | 3.4 | 812.6217 | 1032.3926
DEER-SFAM-CZ16-V3-eSA-15-HL-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-HL | 15.632 | 2.4002 | 813.0159 | 0 | 3.4 | 813.0159 | 1086.995
DEER-SFAM-CZ16-V3-eSA-15-HM-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-HM | 15.7946 | 2.3921 | 822.5435 | 0 | 3.4 | 822.5435 | 1043.1607
DEER-SFAM-CZ16-V3-eSA-15-MH-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-MH | 13.9596 | 2.5057 | 874.6792 | 0 | 3.4 | 874.6792 | 1038.4336
DEER-SFAM-CZ16-V3-eSA-15-ML-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-ML | 14.9555 | 2.4503 | 855.2681 | 0 | 3.4 | 855.2681 | 1075.6638
DEER-SFAM-CZ16-V3-eSA-15-MM-s1 | 15 | CZ16 | V3 | CZ16-V3-eSA-15 | CZ16-V3-eSA-15-MM | 14.3853 | 2.4765 | 858.1497 | 0 | 3.4 | 858.1497 | 1058.9553
DEER-SFAM-CZ16-V3-eSA-16-CH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-CH | 15.2051 | 2.5293 | 930.5788 | 0 | 3.4 | 930.5788 | 1055.8367
DEER-SFAM-CZ16-V3-eSA-16-CL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-CL | 15.8572 | 2.4348 | 885.0667 | 0 | 3.4 | 885.0667 | 1043.5294
DEER-SFAM-CZ16-V3-eSA-16-CM-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-CM | 15.5382 | 2.432 | 907.2213 | 0 | 3.4 | 907.2213 | 1074.2777
DEER-SFAM-CZ16-V3-eSA-16-LH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-LH | 15.5521 | 2.2611 | 810.5784 | 0 | 3.4 | 810.5784 | 1027.2603
DEER-SFAM-CZ16-V3-eSA-16-LL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-LL | 14.8092 | 2.4411 | 860.6255 | 0 | 3.4 | 860.6255 | 1003.3048
DEER-SFAM-CZ16-V3-eSA-16-LM-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-LM | 14.6157 | 2.413 | 869.0815 | 0 | 3.4 | 869.0815 | 998.413
DEER-SFAM-CZ16-V3-eSA-16-NM-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-NM | 15.9427 | 2.3014 | 817.3572 | 0 | 3.4 | 817.3572 | 944.3647
DEER-SFAM-CZ16-V3-eSA-16-TH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-TH | 15.2423 | 2.6707 | 920.6558 | 0 | 3.4 | 920.6558 | 1001.7171
DEER-SFAM-CZ16-V3-eSA-16-TL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSA-16 | CZ16-V3-eSA-16-TL | 16.6229 | 2.4983 | 824.885 | 0 | 3.4 | 824.885 | 912.5334
DEER-SFAM-CZ16-V3-eSA-17-CH-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-CH | 16.1927 | 2.4 | 864.1807 | 0 | 3.4 | 864.1807 | 1022.5597
DEER-SFAM-CZ16-V3-eSA-17-CL-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-CL | 16.145 | 2.4409 | 866.7663 | 0 | 3.4 | 866.7663 | 1025.1082
DEER-SFAM-CZ16-V3-eSA-17-CM-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-CM | 16.3126 | 2.4282 | 867.3351 | 0 | 3.4 | 867.3351 | 992.2206
DEER-SFAM-CZ16-V3-eSA-17-LH-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-LH | 15.7638 | 2.2362 | 794.8832 | 0 | 3.4 | 794.8832 | 964.9042
DEER-SFAM-CZ16-V3-eSA-17-LL-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-LL | 15.5097 | 2.3506 | 824.7656 | 0 | 3.4 | 824.7656 | 917.254
DEER-SFAM-CZ16-V3-eSA-17-LM-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-LM | 15.2832 | 2.3466 | 836.5503 | 0 | 3.4 | 836.5503 | 916.5874
DEER-SFAM-CZ16-V3-eSA-17-TH-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-TH | 17.6067 | 2.2795 | 788.2494 | 0 | 3.4 | 788.2494 | 918.0589
DEER-SFAM-CZ16-V3-eSA-17-TL-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-TL | 18.5057 | 2.2596 | 714.264 | 0 | 3.4 | 714.264 | 915.1999
DEER-SFAM-CZ16-V3-eSA-17-TM-s2 | 17 | CZ16 | V3 | CZ16-V3-eSA-17 | CZ16-V3-eSA-17-TM | 18.0676 | 2.3066 | 801.187 | 0 | 3.4 | 801.187 | 868.6625
DEER-SFAM-CZ16-V3-eSA-18-LH-s2 | 18 | CZ16 | V3 | CZ16-V3-eSA-18 | CZ16-V3-eSA-18-LH | 16.4695 | 2.1726 | 770.3532 | 0 | 3.4 | 770.3532 | 881.8881
DEER-SFAM-CZ16-V3-eSA-18-LL-s2 | 18 | CZ16 | V3 | CZ16-V3-eSA-18 | CZ16-V3-eSA-18-LL | 16.7773 | 2.1731 | 751.5628 | 0 | 3.4 | 751.5628 | 897.1952
DEER-SFAM-CZ16-V3-eSA-18-TH-s2 | 18 | CZ16 | V3 | CZ16-V3-eSA-18 | CZ16-V3-eSA-18-TH | 18.5329 | 2.1387 | 752.7876 | 0 | 3.4 | 752.7876 | 841.0635
DEER-SFAM-CZ16-V3-eSA-18-TL-s2 | 18 | CZ16 | V3 | CZ16-V3-eSA-18 | CZ16-V3-eSA-18-TL | 17.8311 | 2.3117 | 785.7686 | 0 | 3.4 | 785.7686 | 882.0996
DEER-SFAM-CZ16-V3-eSA-18-TM-s2 | 18 | CZ16 | V3 | CZ16-V3-eSA-18 | CZ16-V3-eSA-18-TM | 17.222 | 2.2533 | 799.5076 | 0 | 3.4 | 799.5076 | 889.6957
DEER-SFAM-CZ16-V3-eSH-10-HH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-HH | 10.3419 | 3.3382 | 1215.5204 | 8242.6083 | 3.4 | 9458.1287 | 2016.8787
DEER-SFAM-CZ16-V3-eSH-10-HL-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-HL | 10.0857 | 3.4986 | 1249.4425 | 8206.4214 | 3.4 | 9455.8639 | 2019.3139
DEER-SFAM-CZ16-V3-eSH-10-HM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-HM | 10.491 | 3.3853 | 1239.5005 | 8204.5083 | 3.4 | 9444.0088 | 1981.2088
DEER-SFAM-CZ16-V3-eSH-10-LH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-LH | 10.2877 | 3.2336 | 1239.7451 | 8634.1645 | 3.4 | 9873.9097 | 2057.7097
DEER-SFAM-CZ16-V3-eSH-10-LL-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-LL | 10.4312 | 3.4056 | 1234.6336 | 8893.8438 | 3.4 | 10128.4773 | 2097.1773
DEER-SFAM-CZ16-V3-eSH-10-LM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-LM | 10.6999 | 3.2736 | 1208.9247 | 8603.6738 | 3.4 | 9812.5986 | 2003.1986
DEER-SFAM-CZ16-V3-eSH-10-MH-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-MH | 10.3838 | 3.3136 | 1235.183 | 8697.0951 | 3.4 | 9932.2781 | 2106.0781
DEER-SFAM-CZ16-V3-eSH-10-ML-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-ML | 10.4985 | 3.5425 | 1239.7531 | 8721.4934 | 3.4 | 9961.2465 | 2065.3965
DEER-SFAM-CZ16-V3-eSH-10-MM-s1 | 10 | CZ16 | V3 | CZ16-V3-eSH-10 | CZ16-V3-eSH-10-MM | 10.3313 | 3.3596 | 1251.5929 | 8323.9132 | 3.4 | 9575.506 | 1991.306
DEER-SFAM-CZ16-V3-eSH-13-HH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-HH | 13.3379 | 2.7917 | 974.0664 | 8453.485 | 3.4 | 9427.5513 | 1693.0013
DEER-SFAM-CZ16-V3-eSH-13-HL-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-HL | 13.6603 | 2.7786 | 947.5653 | 7429.4006 | 3.4 | 8376.9659 | 1676.8659
DEER-SFAM-CZ16-V3-eSH-13-HM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-HM | 13.5691 | 2.7479 | 957.418 | 7598.7204 | 3.4 | 8556.1385 | 1620.2385
DEER-SFAM-CZ16-V3-eSH-13-LH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-LH | 12.8414 | 2.6465 | 975.7295 | 9073.8125 | 3.4 | 10049.542 | 2016.1419
DEER-SFAM-CZ16-V3-eSH-13-LL-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-LL | 14.5228 | 2.5899 | 890.7232 | 7782.0094 | 3.4 | 8672.7326 | 1556.1327
DEER-SFAM-CZ16-V3-eSH-13-LM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-LM | 12.2493 | 2.7973 | 1017.7581 | 6370.4073 | 3.4 | 7388.1654 | 1770.3654
DEER-SFAM-CZ16-V3-eSH-13-MH-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-MH | 13.9185 | 2.5324 | 918.158 | 8415.0626 | 3.4 | 9333.2206 | 1624.1706
DEER-SFAM-CZ16-V3-eSH-13-ML-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-ML | 12.2254 | 2.94 | 1027.9397 | 7810.5504 | 3.4 | 8838.4901 | 1760.94
DEER-SFAM-CZ16-V3-eSH-13-MM-s1 | 13 | CZ16 | V3 | CZ16-V3-eSH-13 | CZ16-V3-eSH-13-MM | 13.5937 | 2.7513 | 951.0255 | 7805.2034 | 3.4 | 8756.229 | 1523.929
DEER-SFAM-CZ16-V3-eSH-14-HH-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-HH | 14.1667 | 2.6773 | 917.7998 | 7897.5468 | 3.4 | 8815.3466 | 1468.9966
DEER-SFAM-CZ16-V3-eSH-14-HL-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-HL | 14.5248 | 2.6673 | 896.5501 | 7972.9327 | 3.4 | 8869.4827 | 1551.3827
DEER-SFAM-CZ16-V3-eSH-14-HM-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-HM | 14.464 | 2.5905 | 896.8732 | 7971.2113 | 3.4 | 8868.0845 | 1371.5845
DEER-SFAM-CZ16-V3-eSH-14-MH-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-MH | 13.7244 | 2.462 | 909.8514 | 8625.3101 | 3.4 | 9535.1616 | 1617.5615
DEER-SFAM-CZ16-V3-eSH-14-ML-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-ML | 13.9653 | 2.5589 | 891.4195 | 8781.7854 | 3.4 | 9673.2049 | 1763.6049
DEER-SFAM-CZ16-V3-eSH-14-MM-s1 | 14 | CZ16 | V3 | CZ16-V3-eSH-14 | CZ16-V3-eSH-14-MM | 13.6353 | 2.5692 | 907.5556 | 7739.8113 | 3.4 | 8647.3669 | 1521.7669
DEER-SFAM-CZ16-V3-eSH-15-HH-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-HH | 15.5956 | 2.3935 | 829.883 | 9145.1528 | 3.4 | 9975.0358 | 1314.3858
DEER-SFAM-CZ16-V3-eSH-15-HL-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-HL | 15.5965 | 2.4716 | 836.2636 | 6808.2715 | 3.4 | 7644.535 | 1344.485
DEER-SFAM-CZ16-V3-eSH-15-HM-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-HM | 15.3922 | 2.3356 | 824.9773 | 7248.8926 | 3.4 | 8073.8699 | 1320.2699
DEER-SFAM-CZ16-V3-eSH-15-MH-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-MH | 14.4908 | 2.5119 | 864.8516 | 7898.5385 | 3.4 | 8763.39 | 1337.2401
DEER-SFAM-CZ16-V3-eSH-15-ML-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-ML | 15.0163 | 2.4089 | 830.3022 | 7822.1836 | 3.4 | 8652.4858 | 1331.8858
DEER-SFAM-CZ16-V3-eSH-15-MM-s1 | 15 | CZ16 | V3 | CZ16-V3-eSH-15 | CZ16-V3-eSH-15-MM | 15.8216 | 2.3512 | 812.4288 | 8474.0782 | 3.4 | 9286.507 | 1346.957
DEER-SFAM-CZ16-V3-eSH-16-CH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-CH | 15.6753 | 2.4777 | 902.4941 | 8684.9588 | 3.4 | 9587.453 | 1512.203
DEER-SFAM-CZ16-V3-eSH-16-CL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-CL | 15.7665 | 2.5076 | 897.6836 | 8201.2687 | 3.4 | 9098.9523 | 1533.8523
DEER-SFAM-CZ16-V3-eSH-16-LH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-LH | 15.2177 | 2.2525 | 823.1443 | 8456.3736 | 3.4 | 9279.5179 | 1397.8679
DEER-SFAM-CZ16-V3-eSH-16-LL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-LL | 14.6522 | 2.4518 | 868.1443 | 8036.216 | 3.4 | 8904.3603 | 1359.1603
DEER-SFAM-CZ16-V3-eSH-16-LM-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-LM | 14.6298 | 2.3772 | 863.7641 | 8605.6056 | 3.4 | 9469.3697 | 1509.3698
DEER-SFAM-CZ16-V3-eSH-16-TH-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-TH | 17.1541 | 2.3897 | 810.5645 | 10410.5582 | 3.4 | 11221.1226 | 1523.8727
DEER-SFAM-CZ16-V3-eSH-16-TL-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-TL | 15.3652 | 2.7106 | 914.3331 | 10123.1943 | 3.4 | 11037.5274 | 1570.8774
DEER-SFAM-CZ16-V3-eSH-16-TM-s2 | 16 | CZ16 | V3 | CZ16-V3-eSH-16 | CZ16-V3-eSH-16-TM | 15.6339 | 2.6382 | 898.7974 | 10183.0613 | 3.4 | 11081.8587 | 1567.3086
DEER-SFAM-CZ16-V3-eSH-17-CM-s2 | 17 | CZ16 | V3 | CZ16-V3-eSH-17 | CZ16-V3-eSH-17-CM | 16.6841 | 2.3686 | 847.3709 | 7814.4384 | 3.4 | 8661.8094 | 1459.4094
DEER-SFAM-CZ16-V3-eSH-17-LM-s2 | 17 | CZ16 | V3 | CZ16-V3-eSH-17 | CZ16-V3-eSH-17-LM | 15.6198 | 2.3087 | 828.2809 | 7737.6974 | 3.4 | 8565.9783 | 1102.8283
DEER-SFAM-CZ16-V3-eSH-17-TH-s2 | 17 | CZ16 | V3 | CZ16-V3-eSH-17 | CZ16-V3-eSH-17-TH | 17.7692 | 2.2888 | 777.7609 | 10404.8301 | 3.4 | 11182.5911 | 1522.191
DEER-SFAM-CZ16-V3-eSH-17-TL-s2 | 17 | CZ16 | V3 | CZ16-V3-eSH-17 | CZ16-V3-eSH-17-TL | 17.7312 | 2.3317 | 784.0956 | 10374.1856 | 3.4 | 11158.2812 | 1524.3812
DEER-SFAM-CZ16-V3-eSH-18-LH-s2 | 18 | CZ16 | V3 | CZ16-V3-eSH-18 | CZ16-V3-eSH-18-LH | 16.3338 | 2.2138 | 772.6889 | 9016.6315 | 3.4 | 9789.3204 | 1258.7704
DEER-SFAM-CZ16-V3-eSH-18-LL-s2 | 18 | CZ16 | V3 | CZ16-V3-eSH-18 | CZ16-V3-eSH-18-LL | 15.531 | 2.3178 | 812.2684 | 8161.584 | 3.4 | 8973.8523 | 1233.4524
DEER-SFAM-CZ16-V3-eSH-18-LM-s2 | 18 | CZ16 | V3 | CZ16-V3-eSH-18 | CZ16-V3-eSH-18-LM | 16.5701 | 2.2214 | 771.4855 | 9463.9351 | 3.4 | 10235.4207 | 1326.5207
DEER-SFAM-CZ16-V3-eSH-18-TM-s2 | 18 | CZ16 | V3 | CZ16-V3-eSH-18 | CZ16-V3-eSH-18-TM | 17.9358 | 2.3169 | 778.171 | 10462.4955 | 3.4 | 11240.6665 | 1800.6165
DEER-SFAM-CZ16-V4-eSA-10-HH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-HH | 10.1159 | 3.3524 | 1224.5932 | 0 | 3.4 | 1224.5932 | 1513.0212
DEER-SFAM-CZ16-V4-eSA-10-HL-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-HL | 10.4026 | 3.6297 | 1225.9953 | 0 | 3.4 | 1225.9953 | 1514.5638
DEER-SFAM-CZ16-V4-eSA-10-HM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-HM | 10.1417 | 3.509 | 1228.5486 | 0 | 3.4 | 1228.5486 | 1517.0883
DEER-SFAM-CZ16-V4-eSA-10-LH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-LH | 10.2464 | 3.3772 | 1214.4973 | 0 | 3.4 | 1214.4973 | 1503.1903
DEER-SFAM-CZ16-V4-eSA-10-LL-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-LL | 10.488 | 3.572 | 1218.4751 | 0 | 3.4 | 1218.4751 | 1507.0733
DEER-SFAM-CZ16-V4-eSA-10-LM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-LM | 10.2243 | 3.3786 | 1211.6202 | 0 | 3.4 | 1211.6202 | 1500.3202
DEER-SFAM-CZ16-V4-eSA-10-MH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-MH | 10.1487 | 3.2872 | 1220.0738 | 0 | 3.4 | 1220.0738 | 1508.7298
DEER-SFAM-CZ16-V4-eSA-10-ML-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-ML | 10.2047 | 3.5852 | 1248.3892 | 0 | 3.4 | 1248.3892 | 1536.9608
DEER-SFAM-CZ16-V4-eSA-10-MM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSA-10 | CZ16-V4-eSA-10-MM | 9.9486 | 3.3101 | 1226.8676 | 0 | 3.4 | 1226.8676 | 1515.4494
DEER-SFAM-CZ16-V4-eSA-13-HH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-HH | 13.3031 | 2.8738 | 955.3622 | 0 | 3.9 | 955.3622 | 1215.6245
DEER-SFAM-CZ16-V4-eSA-13-HL-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-HL | 12.5508 | 2.8973 | 961.1406 | 0 | 3.4 | 961.1406 | 1188.8154
DEER-SFAM-CZ16-V4-eSA-13-HM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-HM | 13.8064 | 2.8786 | 925.242 | 0 | 3.9 | 925.242 | 1185.4554
DEER-SFAM-CZ16-V4-eSA-13-LH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-LH | 13.1812 | 2.5684 | 924.4775 | 0 | 3.4 | 924.4775 | 1213.084
DEER-SFAM-CZ16-V4-eSA-13-LL-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-LL | 12.8773 | 2.7576 | 963.3823 | 0 | 3.4 | 963.3823 | 1251.6799
DEER-SFAM-CZ16-V4-eSA-13-LM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-LM | 12.5103 | 2.727 | 977.9515 | 0 | 3.4 | 977.9515 | 1266.424
DEER-SFAM-CZ16-V4-eSA-13-MH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-MH | 14.1078 | 2.6403 | 894.6635 | 0 | 3.4 | 894.6635 | 1183.2041
DEER-SFAM-CZ16-V4-eSA-13-ML-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-ML | 12.4011 | 2.7927 | 946.9317 | 0 | 3.4 | 946.9317 | 1234.6269
DEER-SFAM-CZ16-V4-eSA-13-MM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSA-13 | CZ16-V4-eSA-13-MM | 14.4979 | 2.5565 | 866.4644 | 0 | 3.4 | 866.4644 | 1154.9797
DEER-SFAM-CZ16-V4-eSA-14-HH-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-HH | 12.8599 | 2.6601 | 913.0674 | 0 | 3.4 | 913.0674 | 1154.9278
DEER-SFAM-CZ16-V4-eSA-14-HL-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-HL | 14.3068 | 2.6269 | 868.7823 | 0 | 3.4 | 868.7823 | 1046.634
DEER-SFAM-CZ16-V4-eSA-14-HM-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-HM | 13.3015 | 2.7694 | 921.2749 | 0 | 3.4 | 921.2749 | 1194.0638
DEER-SFAM-CZ16-V4-eSA-14-MH-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-MH | 13.4523 | 2.5419 | 925.6457 | 0 | 3.4 | 925.6457 | 1115.2971
DEER-SFAM-CZ16-V4-eSA-14-ML-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-ML | 13.188 | 2.6555 | 900.4938 | 0 | 3.4 | 900.4938 | 1203.2706
DEER-SFAM-CZ16-V4-eSA-14-MM-s1 | 14 | CZ16 | V4 | CZ16-V4-eSA-14 | CZ16-V4-eSA-14-MM | 13.5127 | 2.5358 | 901.4526 | 0 | 3.4 | 901.4526 | 1109.3343
DEER-SFAM-CZ16-V4-eSA-15-HH-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-HH | 15.9109 | 2.4569 | 801.7304 | 0 | 3.9 | 801.7304 | 1003.4461
DEER-SFAM-CZ16-V4-eSA-15-HL-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-HL | 15.5705 | 2.4615 | 801.471 | 0 | 3.9 | 801.471 | 1052.9498
DEER-SFAM-CZ16-V4-eSA-15-HM-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-HM | 15.6392 | 2.4713 | 810.0399 | 0 | 3.9 | 810.0399 | 1012.5214
DEER-SFAM-CZ16-V4-eSA-15-MH-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-MH | 13.9629 | 2.5024 | 848.5816 | 0 | 3.4 | 848.5816 | 998.8001
DEER-SFAM-CZ16-V4-eSA-15-ML-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-ML | 14.9867 | 2.4451 | 829.7695 | 0 | 3.4 | 829.7695 | 1031.9491
DEER-SFAM-CZ16-V4-eSA-15-MM-s1 | 15 | CZ16 | V4 | CZ16-V4-eSA-15 | CZ16-V4-eSA-15-MM | 14.4037 | 2.4724 | 831.8516 | 0 | 3.4 | 831.8516 | 1016.0558
DEER-SFAM-CZ16-V4-eSA-16-CH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-CH | 15.2001 | 2.5293 | 904.5223 | 0 | 3.4 | 904.5223 | 1019.5865
DEER-SFAM-CZ16-V4-eSA-16-CL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-CL | 15.9284 | 2.5181 | 864.5022 | 0 | 3.9 | 864.5022 | 1010.293
DEER-SFAM-CZ16-V4-eSA-16-CM-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-CM | 15.5667 | 2.5379 | 888.8457 | 0 | 3.9 | 888.8457 | 1042.559
DEER-SFAM-CZ16-V4-eSA-16-LH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-LH | 15.5256 | 2.2597 | 788.1563 | 0 | 3.4 | 788.1563 | 987.0638
DEER-SFAM-CZ16-V4-eSA-16-LL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-LL | 14.7945 | 2.4401 | 836.3502 | 0 | 3.4 | 836.3502 | 967.2962
DEER-SFAM-CZ16-V4-eSA-16-LM-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-LM | 14.6018 | 2.4127 | 844.3599 | 0 | 3.4 | 844.3599 | 963.0489
DEER-SFAM-CZ16-V4-eSA-16-NM-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-NM | 15.9343 | 2.2978 | 793.9291 | 0 | 3.4 | 793.9291 | 910.5033
DEER-SFAM-CZ16-V4-eSA-16-TH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-TH | 15.2217 | 2.6688 | 897.3217 | 0 | 3.4 | 897.3217 | 971.7606
DEER-SFAM-CZ16-V4-eSA-16-TL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSA-16 | CZ16-V4-eSA-16-TL | 16.7032 | 2.4527 | 808.5733 | 0 | 3.9 | 808.5733 | 889.1484
DEER-SFAM-CZ16-V4-eSA-17-CH-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-CH | 16.2612 | 2.4798 | 843.3872 | 0 | 3.9 | 843.3872 | 989.1207
DEER-SFAM-CZ16-V4-eSA-17-CL-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-CL | 16.2504 | 2.5095 | 844.0823 | 0 | 3.9 | 844.0823 | 989.7808
DEER-SFAM-CZ16-V4-eSA-17-CM-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-CM | 16.4084 | 2.5025 | 845.4532 | 0 | 3.9 | 845.4532 | 960.3825
DEER-SFAM-CZ16-V4-eSA-17-LH-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-LH | 15.734 | 2.2338 | 773.8235 | 0 | 3.4 | 773.8235 | 929.8871
DEER-SFAM-CZ16-V4-eSA-17-LL-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-LL | 15.5028 | 2.3497 | 801.3038 | 0 | 3.4 | 801.3038 | 886.2126
DEER-SFAM-CZ16-V4-eSA-17-LM-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-LM | 15.267 | 2.3445 | 813.615 | 0 | 3.4 | 813.615 | 887.0601
DEER-SFAM-CZ16-V4-eSA-17-TH-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-TH | 17.5707 | 2.2773 | 767.9601 | 0 | 3.4 | 767.9601 | 887.1428
DEER-SFAM-CZ16-V4-eSA-17-TL-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-TL | 18.4941 | 2.2536 | 694.1591 | 0 | 3.4 | 694.1591 | 878.7396
DEER-SFAM-CZ16-V4-eSA-17-TM-s2 | 17 | CZ16 | V4 | CZ16-V4-eSA-17 | CZ16-V4-eSA-17-TM | 18.0586 | 2.3443 | 790.5746 | 0 | 3.9 | 790.5746 | 852.6474
DEER-SFAM-CZ16-V4-eSA-18-LH-s2 | 18 | CZ16 | V4 | CZ16-V4-eSA-18 | CZ16-V4-eSA-18-LH | 16.447 | 2.1713 | 748.7772 | 0 | 3.4 | 748.7772 | 851.1339
DEER-SFAM-CZ16-V4-eSA-18-LL-s2 | 18 | CZ16 | V4 | CZ16-V4-eSA-18 | CZ16-V4-eSA-18-LL | 16.7663 | 2.1716 | 729.9543 | 0 | 3.4 | 729.9543 | 863.6146
DEER-SFAM-CZ16-V4-eSA-18-TH-s2 | 18 | CZ16 | V4 | CZ16-V4-eSA-18 | CZ16-V4-eSA-18-TH | 18.4848 | 2.1351 | 734.2255 | 0 | 3.4 | 734.2255 | 815.2473
DEER-SFAM-CZ16-V4-eSA-18-TL-s2 | 18 | CZ16 | V4 | CZ16-V4-eSA-18 | CZ16-V4-eSA-18-TL | 17.8057 | 2.306 | 765.8131 | 0 | 3.4 | 765.8131 | 854.3
DEER-SFAM-CZ16-V4-eSA-18-TM-s2 | 18 | CZ16 | V4 | CZ16-V4-eSA-18 | CZ16-V4-eSA-18-TM | 17.2033 | 2.2508 | 777.8334 | 0 | 3.4 | 777.8334 | 860.6301
DEER-SFAM-CZ16-V4-eSH-10-HH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-HH | 10.2233 | 3.4657 | 1206.326 | 7430.4122 | 3.9 | 8636.7383 | 1954.2383
DEER-SFAM-CZ16-V4-eSH-10-HL-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-HL | 10.1068 | 3.495 | 1214.9474 | 7532.3212 | 3.4 | 8747.2686 | 1925.3186
DEER-SFAM-CZ16-V4-eSH-10-HM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-HM | 10.5074 | 3.3809 | 1207.7308 | 7533.848 | 3.4 | 8741.5789 | 1892.1289
DEER-SFAM-CZ16-V4-eSH-10-LH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-LH | 10.3014 | 3.229 | 1208.0567 | 7895.797 | 3.4 | 9103.8537 | 1965.8537
DEER-SFAM-CZ16-V4-eSH-10-LL-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-LL | 10.45 | 3.4026 | 1202.4058 | 8145.5838 | 3.4 | 9347.9896 | 2000.0896
DEER-SFAM-CZ16-V4-eSH-10-LM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-LM | 10.7083 | 3.2702 | 1175.5173 | 7888.0525 | 3.4 | 9063.5698 | 1909.9198
DEER-SFAM-CZ16-V4-eSH-10-MH-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-MH | 10.3993 | 3.3081 | 1201.9985 | 7963.3166 | 3.4 | 9165.3151 | 2008.2151
DEER-SFAM-CZ16-V4-eSH-10-ML-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-ML | 10.51 | 3.5377 | 1203.8303 | 8002.1095 | 3.4 | 9205.9398 | 1967.9398
DEER-SFAM-CZ16-V4-eSH-10-MM-s1 | 10 | CZ16 | V4 | CZ16-V4-eSH-10 | CZ16-V4-eSH-10-MM | 10.3528 | 3.3592 | 1220.4832 | 7625.2697 | 3.4 | 8845.7529 | 1903.7028
DEER-SFAM-CZ16-V4-eSH-13-HH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-HH | 13.3381 | 2.7862 | 946.5664 | 7704.9873 | 3.4 | 8651.5536 | 1613.6536
DEER-SFAM-CZ16-V4-eSH-13-HL-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-HL | 13.5813 | 2.8762 | 929.0666 | 6553.4533 | 3.9 | 7482.5199 | 1611.7199
DEER-SFAM-CZ16-V4-eSH-13-HM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-HM | 13.5798 | 2.7391 | 929.3504 | 6928.5937 | 3.4 | 7857.9441 | 1543.094
DEER-SFAM-CZ16-V4-eSH-13-LH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-LH | 12.8533 | 2.6414 | 949.7094 | 8248.9379 | 3.4 | 9198.6473 | 1917.9473
DEER-SFAM-CZ16-V4-eSH-13-LL-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-LL | 14.5296 | 2.5862 | 865.1839 | 7071.9931 | 3.4 | 7937.177 | 1481.777
DEER-SFAM-CZ16-V4-eSH-13-LM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-LM | 12.2612 | 2.7927 | 990.8059 | 5808.2838 | 3.4 | 6799.0898 | 1686.2897
DEER-SFAM-CZ16-V4-eSH-13-MH-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-MH | 13.7201 | 2.6593 | 908.8124 | 7419.1562 | 3.9 | 8327.9687 | 1573.4687
DEER-SFAM-CZ16-V4-eSH-13-ML-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-ML | 12.2517 | 2.9348 | 999.5493 | 7105.9518 | 3.4 | 8105.501 | 1677.8011
DEER-SFAM-CZ16-V4-eSH-13-MM-s1 | 13 | CZ16 | V4 | CZ16-V4-eSH-13 | CZ16-V4-eSH-13-MM | 13.6069 | 2.7424 | 923.5593 | 7124.0868 | 3.4 | 8047.6461 | 1453.1961
DEER-SFAM-CZ16-V4-eSH-14-HH-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-HH | 14.1717 | 2.6713 | 891.2046 | 7188.4216 | 3.4 | 8079.6262 | 1402.2261
DEER-SFAM-CZ16-V4-eSH-14-HL-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-HL | 14.476 | 2.7261 | 881.6876 | 6941.0687 | 3.9 | 7822.7563 | 1499.3063
DEER-SFAM-CZ16-V4-eSH-14-HM-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-HM | 14.4684 | 2.585 | 870.317 | 7257.0724 | 3.4 | 8127.3893 | 1310.7893
DEER-SFAM-CZ16-V4-eSH-14-MH-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-MH | 13.7409 | 2.4575 | 885.2655 | 7843.6667 | 3.4 | 8728.9322 | 1544.2822
DEER-SFAM-CZ16-V4-eSH-14-ML-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-ML | 13.9906 | 2.5526 | 864.0272 | 7974.7642 | 3.4 | 8838.7914 | 1674.6414
DEER-SFAM-CZ16-V4-eSH-14-MM-s1 | 14 | CZ16 | V4 | CZ16-V4-eSH-14 | CZ16-V4-eSH-14-MM | 13.6517 | 2.5662 | 881.2899 | 7032.5207 | 3.4 | 7913.8106 | 1450.7106
DEER-SFAM-CZ16-V4-eSH-15-HH-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-HH | 15.4074 | 2.4829 | 820.2281 | 7891.3875 | 3.9 | 8711.6155 | 1287.7155
DEER-SFAM-CZ16-V4-eSH-15-HL-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-HL | 15.5209 | 2.5313 | 823.0498 | 5955.9821 | 3.9 | 6779.032 | 1298.882
DEER-SFAM-CZ16-V4-eSH-15-HM-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-HM | 15.3125 | 2.4127 | 813.0775 | 6305.0404 | 3.9 | 7118.1179 | 1278.4679
DEER-SFAM-CZ16-V4-eSH-15-MH-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-MH | 14.5074 | 2.5074 | 839.04 | 7157.575 | 3.4 | 7996.615 | 1277.2649
DEER-SFAM-CZ16-V4-eSH-15-ML-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-ML | 15.0407 | 2.3969 | 804.7804 | 7096.9409 | 3.4 | 7901.7213 | 1269.9213
DEER-SFAM-CZ16-V4-eSH-15-MM-s1 | 15 | CZ16 | V4 | CZ16-V4-eSH-15 | CZ16-V4-eSH-15-MM | 15.7451 | 2.4221 | 799.7888 | 7374.2117 | 3.9 | 8174.0004 | 1309.2505
DEER-SFAM-CZ16-V4-eSH-16-CH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-CH | 15.6858 | 2.5673 | 884.6812 | 7663.6604 | 3.9 | 8548.3415 | 1441.0915
DEER-SFAM-CZ16-V4-eSH-16-CL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-CL | 15.8383 | 2.5971 | 876.1878 | 7207.6718 | 3.9 | 8083.8596 | 1452.2596
DEER-SFAM-CZ16-V4-eSH-16-LH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-LH | 15.1999 | 2.2424 | 804.1653 | 7691.8164 | 3.4 | 8495.9816 | 1329.8817
DEER-SFAM-CZ16-V4-eSH-16-LL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-LL | 14.638 | 2.451 | 843.4968 | 7308.6232 | 3.4 | 8152.1201 | 1289.3201
DEER-SFAM-CZ16-V4-eSH-16-LM-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-LM | 14.5967 | 2.3745 | 841.1811 | 7823.1736 | 3.4 | 8664.3547 | 1431.2547
DEER-SFAM-CZ16-V4-eSH-16-TH-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-TH | 17.1014 | 2.4386 | 805.8515 | 9389.8368 | 3.9 | 10195.6884 | 1445.7384
DEER-SFAM-CZ16-V4-eSH-16-TL-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-TL | 15.3707 | 2.7086 | 889.8672 | 9278.1519 | 3.4 | 10168.0191 | 1491.3691
DEER-SFAM-CZ16-V4-eSH-16-TM-s2 | 16 | CZ16 | V4 | CZ16-V4-eSH-16 | CZ16-V4-eSH-16-TM | 15.636 | 2.6353 | 874.9779 | 9334.9227 | 3.4 | 10209.9006 | 1488.2506
DEER-SFAM-CZ16-V4-eSH-17-CM-s2 | 17 | CZ16 | V4 | CZ16-V4-eSH-17 | CZ16-V4-eSH-17-CM | 16.7596 | 2.4573 | 827.12 | 6821.2736 | 3.9 | 7648.3936 | 1364.0937
DEER-SFAM-CZ16-V4-eSH-17-LM-s2 | 17 | CZ16 | V4 | CZ16-V4-eSH-17 | CZ16-V4-eSH-17-LM | 15.6207 | 2.2995 | 809.5155 | 7035.4126 | 3.4 | 7844.9281 | 1058.7281
DEER-SFAM-CZ16-V4-eSH-17-TH-s2 | 17 | CZ16 | V4 | CZ16-V4-eSH-17 | CZ16-V4-eSH-17-TH | 17.74 | 2.2847 | 757.5104 | 9550.4993 | 3.4 | 10308.0097 | 1442.5097
DEER-SFAM-CZ16-V4-eSH-17-TL-s2 | 17 | CZ16 | V4 | CZ16-V4-eSH-17 | CZ16-V4-eSH-17-TL | 17.7143 | 2.3269 | 763.2742 | 9521.7175 | 3.4 | 10284.9917 | 1443.5417
DEER-SFAM-CZ16-V4-eSH-18-LH-s2 | 18 | CZ16 | V4 | CZ16-V4-eSH-18 | CZ16-V4-eSH-18-LH | 16.3145 | 2.2095 | 751.0869 | 8203.8343 | 3.4 | 8954.9212 | 1192.8211
DEER-SFAM-CZ16-V4-eSH-18-LL-s2 | 18 | CZ16 | V4 | CZ16-V4-eSH-18 | CZ16-V4-eSH-18-LL | 15.5131 | 2.3131 | 788.9849 | 7412.1355 | 3.4 | 8201.1204 | 1172.2204
DEER-SFAM-CZ16-V4-eSH-18-LM-s2 | 18 | CZ16 | V4 | CZ16-V4-eSH-18 | CZ16-V4-eSH-18-LM | 16.5524 | 2.2198 | 750.2358 | 8616.5338 | 3.4 | 9366.7697 | 1254.9197
DEER-SFAM-CZ16-V4-eSH-18-TM-s2 | 18 | CZ16 | V4 | CZ16-V4-eSH-18 | CZ16-V4-eSH-18-TM | 17.922 | 2.3155 | 758.2356 | 9604.0526 | 3.4 | 10362.2882 | 1705.3882

## WtdRes (hidden)
| DEER-SFAM-CZ |  | StandardCalc |  |  |  |  | Alternative |  |  |  |  | Alternative
|  |  | AC:cool+coolfan |  |  |  |  | AC:cool+coolfan |  |  |  |  | Peak Demand
| CZ |  | HP:cool+coolfan+heat+heatsup+heatfan |  |  |  |  | HP:cool+coolfan+heat+heatsup+heatfan
Climate | Equipment | Key | -V1- | -V2- | -V3- | -V4- | -V5- | -V1- | -V2- | -V3- | -V4- | -V5- | -V1- | -V2- | -V3- | -V4- | -V5-
1 | SA-10-HH | 01-SA-10-HH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-HL | 01-SA-10-HL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-HM | 01-SA-10-HM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-LH | 01-SA-10-LH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-LL | 01-SA-10-LL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-LM | 01-SA-10-LM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-MH | 01-SA-10-MH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-ML | 01-SA-10-ML | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-10-MM | 01-SA-10-MM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-HH | 01-SA-13-HH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-HL | 01-SA-13-HL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-HM | 01-SA-13-HM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-LH | 01-SA-13-LH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-LL | 01-SA-13-LL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-LM | 01-SA-13-LM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-MH | 01-SA-13-MH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-ML | 01-SA-13-ML | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-13-MM | 01-SA-13-MM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-HH | 01-SA-14-HH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-HL | 01-SA-14-HL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-HM | 01-SA-14-HM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-MH | 01-SA-14-MH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-ML | 01-SA-14-ML | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-14-MM | 01-SA-14-MM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-HH | 01-SA-15-HH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-HL | 01-SA-15-HL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-HM | 01-SA-15-HM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-MH | 01-SA-15-MH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-ML | 01-SA-15-ML | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-15-MM | 01-SA-15-MM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-CH | 01-SA-16-CH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-CL | 01-SA-16-CL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-CM | 01-SA-16-CM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-LH | 01-SA-16-LH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-LL | 01-SA-16-LL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-LM | 01-SA-16-LM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-NM | 01-SA-16-NM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-TH | 01-SA-16-TH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-16-TL | 01-SA-16-TL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-CH | 01-SA-17-CH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-CL | 01-SA-17-CL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-CM | 01-SA-17-CM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-LH | 01-SA-17-LH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-LL | 01-SA-17-LL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-LM | 01-SA-17-LM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-TH | 01-SA-17-TH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-TL | 01-SA-17-TL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-17-TM | 01-SA-17-TM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-18-LH | 01-SA-18-LH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-18-LL | 01-SA-18-LL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-18-TH | 01-SA-18-TH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-18-TL | 01-SA-18-TL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SA-18-TM | 01-SA-18-TM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-HH | 01-SH-10-HH | 5446.978 | 3173.8313 | 3201.412 | 2888.7731 | 4280.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-HL | 01-SH-10-HL | 5521.8982 | 3210.2946 | 3236.1454 | 2917.0786 | 4334.9846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-HM | 01-SH-10-HM | 5284.2405 | 3100.0329 | 3154.2499 | 2865.8446 | 4174.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-LH | 01-SH-10-LH | 5786.0083 | 3340.547 | 3335.079 | 3044.4636 | 4530.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-LL | 01-SH-10-LL | 5530.3086 | 3176.6172 | 3173.3888 | 2876.2958 | 4318.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-LM | 01-SH-10-LM | 5425.7 | 3159.1329 | 3157.6555 | 2874.5861 | 4259.9683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-MH | 01-SH-10-MH | 5703.4572 | 3287.5036 | 3276.9052 | 2982.8087 | 4459.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-ML | 01-SH-10-ML | 5144.8253 | 2976.4225 | 3001.0561 | 2704.5368 | 4032.1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-10-MM | 01-SH-10-MM | 5523.5062 | 3197.5534 | 3207.9546 | 2909.4419 | 4329.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-HH | 01-SH-13-HH | 5301.0367 | 3039.7769 | 3079.5604 | 2778.3374 | 4146.4207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-HL | 01-SH-13-HL | 4601.183 | 2626.034 | 2650.5389 | 2386.6167 | 3589.4778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-HM | 01-SH-13-HM | 4707.1569 | 2711.1101 | 2753.7248 | 2482.7519 | 3689.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-LH | 01-SH-13-LH | 5754.6455 | 3155.3796 | 3095.0943 | 2792.497 | 4404.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-LL | 01-SH-13-LL | 4884.8519 | 2765.8535 | 2773.6382 | 2500.1435 | 3795.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-LM | 01-SH-13-LM | 4256.9184 | 2447.2384 | 2451.0351 | 2222.744 | 3327.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-MH | 01-SH-13-MH | 5365.6612 | 3069.1682 | 3077.1649 | 2780.8544 | 4185.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-ML | 01-SH-13-ML | 5087.4522 | 2854.0266 | 2824.4569 | 2547.5233 | 3930.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-13-MM | 01-SH-13-MM | 4960.154 | 2850.9777 | 2875.2897 | 2604.9243 | 3881.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-HH | 01-SH-14-HH | 4847.4784 | 2771.2882 | 2812.4151 | 2535.6964 | 3788.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-HL | 01-SH-14-HL | 4840.3748 | 2716.5881 | 2734.6651 | 2461.9004 | 3752.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-HM | 01-SH-14-HM | 4753.5819 | 2693.5458 | 2705.5759 | 2448.1103 | 3697.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-MH | 01-SH-14-MH | 5200.8211 | 2852.2968 | 2817.3187 | 2537.3967 | 3985.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-ML | 01-SH-14-ML | 5485.4508 | 2977.8839 | 2891.5466 | 2590.921 | 4173.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-14-MM | 01-SH-14-MM | 4762.76 | 2639.7173 | 2632.3924 | 2376.3352 | 3670.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-HH | 01-SH-15-HH | 5775.7629 | 3192.7788 | 3122.6701 | 2812.6991 | 4429.6661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-HL | 01-SH-15-HL | 4113.4366 | 2345.611 | 2381.7761 | 2145.8162 | 3212.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-HM | 01-SH-15-HM | 4285.6309 | 2436.0513 | 2504.2124 | 2255.819 | 3351.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-MH | 01-SH-15-MH | 5140.4346 | 2816.8794 | 2748.5478 | 2476.3331 | 3929.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-ML | 01-SH-15-ML | 4774.0627 | 2612.4243 | 2556.7519 | 2298.5338 | 3648.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-15-MM | 01-SH-15-MM | 4989.6837 | 2775.7613 | 2763.9029 | 2490.423 | 3848.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-CH | 01-SH-16-CH | 5218.3156 | 2895.5642 | 2651.3888 | 2384.1521 | 3956.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-CL | 01-SH-16-CL | 4859.5842 | 2685.0078 | 2478.6555 | 2224.6631 | 3684.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-LH | 01-SH-16-LH | 5587.78 | 3112.1906 | 2907.4375 | 2625.8306 | 4260.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-LL | 01-SH-16-LL | 5164.8512 | 2807.0539 | 2622.8427 | 2361.6712 | 3905.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-LM | 01-SH-16-LM | 5626.0222 | 3112.6935 | 2897.8079 | 2614.7069 | 4276.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-TH | 01-SH-16-TH | 6401.3799 | 3647.6219 | 3277.6149 | 2954.4557 | 4880.7964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-TL | 01-SH-16-TL | 6436.6132 | 3595.4171 | 3195.5475 | 2871.5395 | 4864.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-16-TM | 01-SH-16-TM | 6514.2148 | 3657.3553 | 3255.4436 | 2926.2001 | 4932.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-17-CM | 01-SH-17-CM | 5477.6866 | 2987.3423 | 2673.0024 | 2395.5711 | 4111.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-17-LM | 01-SH-17-LM | 5008.3679 | 2725.1183 | 2553.2656 | 2300.4963 | 3790.3638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-17-TH | 01-SH-17-TH | 6375.0368 | 3640.7174 | 3260.9246 | 2937.303 | 4860.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-17-TL | 01-SH-17-TL | 6351.1474 | 3603.5423 | 3213.8958 | 2893.5121 | 4828.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-18-LH | 01-SH-18-LH | 5770.9451 | 3155.245 | 2842.2396 | 2553.1993 | 4341.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-18-LL | 01-SH-18-LL | 5204.2586 | 2813.4556 | 2603.0883 | 2341.2922 | 3920.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-18-LM | 01-SH-18-LM | 6064.853 | 3329.5405 | 2978.6669 | 2673.4259 | 4562.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | SH-18-TM | 01-SH-18-TM | 6310.8655 | 3589.7861 | 3173.7557 | 2840.4749 | 4790.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | SA-10-HH | 02-SA-10-HH | 1440.0708 | 920.6979 | 1762.5204 | 1715.1076 | 1277.7628 | 1440.0708 | 920.6979 | 1762.5204 | 1715.1076 | 1277.7628 | 3.8336 | 3.1775 | 3.7681 | 3.7421 | 3.5409
2 | SA-10-HL | 02-SA-10-HL | 1495.9053 | 953.5008 | 1830.851 | 1778.8441 | 1325.8178 | 1495.9053 | 953.5008 | 1830.851 | 1778.8441 | 1325.8178 | 4.2897 | 3.536 | 4.1384 | 4.0979 | 3.9378
2 | SA-10-HM | 02-SA-10-HM | 1466.1015 | 931.9703 | 1797.52 | 1747.8215 | 1299.0555 | 1466.1015 | 931.9703 | 1797.52 | 1747.8215 | 1299.0555 | 4.0178 | 3.3062 | 3.8479 | 3.8127 | 3.6807
2 | SA-10-LH | 02-SA-10-LH | 1413.2931 | 898.0173 | 1741.7542 | 1695.2341 | 1253.9586 | 1413.2931 | 898.0173 | 1741.7542 | 1695.2341 | 1253.9586 | 3.74 | 3.1142 | 3.7033 | 3.6761 | 3.4655
2 | SA-10-LL | 02-SA-10-LL | 1456.2053 | 924.3391 | 1796.4183 | 1745.106 | 1291.6556 | 1456.2053 | 924.3391 | 1796.4183 | 1745.106 | 1291.6556 | 4.0582 | 3.3539 | 3.9481 | 3.9086 | 3.7352
2 | SA-10-LM | 02-SA-10-LM | 1416.134 | 898.1345 | 1742.0408 | 1695.3357 | 1255.1385 | 1416.134 | 898.1345 | 1742.0408 | 1695.3357 | 1255.1385 | 3.781 | 3.1405 | 3.7288 | 3.7012 | 3.4973
2 | SA-10-MH | 02-SA-10-MH | 1419.6224 | 911.6204 | 1744.2046 | 1698.6261 | 1262.7097 | 1419.6224 | 911.6204 | 1744.2046 | 1698.6261 | 1262.7097 | 3.6406 | 3.0418 | 3.6049 | 3.5793 | 3.3779
2 | SA-10-ML | 02-SA-10-ML | 1494.2169 | 949.5251 | 1835.6898 | 1785.3949 | 1324.5777 | 1494.2169 | 949.5251 | 1835.6898 | 1785.3949 | 1324.5777 | 4.1275 | 3.4227 | 3.9956 | 3.9653 | 3.801
2 | SA-10-MM | 02-SA-10-MM | 1421.2738 | 901.6303 | 1730.5324 | 1706.2384 | 1258.5006 | 1421.2738 | 901.6303 | 1730.5324 | 1706.2384 | 1258.5006 | 3.8071 | 3.154 | 3.426 | 3.6989 | 3.4833
2 | SA-13-HH | 02-SA-13-HH | 1122.3155 | 719.8882 | 1386.8501 | 1346.2272 | 999.0099 | 1122.3155 | 719.8882 | 1386.8501 | 1346.2272 | 999.0099 | 3.195 | 2.6544 | 3.1663 | 3.1397 | 2.9582
2 | SA-13-HL | 02-SA-13-HL | 1135.869 | 716.9091 | 1401.5669 | 1360.395 | 1005.7385 | 1135.869 | 716.9091 | 1401.5669 | 1360.395 | 1005.7385 | 3.3136 | 2.713 | 3.3458 | 3.3155 | 3.0628
2 | SA-13-HM | 02-SA-13-HM | 1119.1747 | 713.7414 | 1378.3504 | 1337.7803 | 993.5721 | 1119.1747 | 713.7414 | 1378.3504 | 1337.7803 | 993.5721 | 3.2866 | 2.6913 | 3.2186 | 3.1879 | 3.0187
2 | SA-13-LH | 02-SA-13-LH | 1082.2966 | 690.8669 | 1331.9625 | 1296.4808 | 961.2734 | 1082.2966 | 690.8669 | 1331.9625 | 1296.4808 | 961.2734 | 2.8955 | 2.3977 | 2.8878 | 2.863 | 2.681
2 | SA-13-LL | 02-SA-13-LL | 1126.8318 | 714.1627 | 1393.8607 | 1354.7753 | 999.8165 | 1126.8318 | 714.1627 | 1393.8607 | 1354.7753 | 999.8165 | 3.1258 | 2.5727 | 3.1175 | 3.0942 | 2.8879
2 | SA-13-LM | 02-SA-13-LM | 1128.904 | 719.2637 | 1396.8316 | 1358.3371 | 1003.3991 | 1128.904 | 719.2637 | 1396.8316 | 1358.3371 | 1003.3991 | 3.0151 | 2.5072 | 3.0136 | 2.9915 | 2.7978
2 | SA-13-MH | 02-SA-13-MH | 1095.3513 | 701.0148 | 1336.1631 | 1296.88 | 971.0372 | 1095.3513 | 701.0148 | 1336.1631 | 1296.88 | 971.0372 | 3.0868 | 2.5604 | 3.0671 | 3.041 | 2.8578
2 | SA-13-ML | 02-SA-13-ML | 1117.3118 | 706.2963 | 1376.6536 | 1335.9335 | 989.3646 | 1117.3118 | 706.2963 | 1376.6536 | 1335.9335 | 989.3646 | 3.208 | 2.6165 | 3.1969 | 3.1706 | 2.9531
2 | SA-13-MM | 02-SA-13-MM | 1075.995 | 684.8952 | 1306.9814 | 1270.0179 | 951.3815 | 1075.995 | 684.8952 | 1306.9814 | 1270.0179 | 951.3815 | 3.1062 | 2.5387 | 3.0838 | 3.0589 | 2.8594
2 | SA-14-HH | 02-SA-14-HH | 1086.2867 | 692.3089 | 1333.2631 | 1294.8879 | 963.3949 | 1086.2867 | 692.3089 | 1333.2631 | 1294.8879 | 963.3949 | 3.082 | 2.5319 | 3.0653 | 3.0396 | 2.8435
2 | SA-14-HL | 02-SA-14-HL | 1047.4135 | 662.213 | 1287.6324 | 1250.1684 | 927.0237 | 1047.4135 | 662.213 | 1287.6324 | 1250.1684 | 927.0237 | 3.069 | 2.4974 | 3.0878 | 3.0568 | 2.8278
2 | SA-14-HM | 02-SA-14-HM | 1088.3426 | 688.4698 | 1343.3234 | 1305.4473 | 964.5415 | 1088.3426 | 688.4698 | 1343.3234 | 1305.4473 | 964.5415 | 3.1224 | 2.5749 | 3.1233 | 3.096 | 2.8883
2 | SA-14-MH | 02-SA-14-MH | 1068.6037 | 684.4259 | 1322.5724 | 1286.4825 | 951.419 | 1068.6037 | 684.4259 | 1322.5724 | 1286.4825 | 951.419 | 2.8037 | 2.3383 | 2.806 | 2.7849 | 2.6052
2 | SA-14-ML | 02-SA-14-ML | 1060.4671 | 670.9574 | 1309.0102 | 1269.9857 | 939.7059 | 1060.4671 | 670.9574 | 1309.0102 | 1269.9857 | 939.7059 | 3.0023 | 2.4715 | 3.0244 | 2.9972 | 2.7793
2 | SA-14-MM | 02-SA-14-MM | 1048.3182 | 669.967 | 1293.8942 | 1259.2352 | 932.1216 | 1048.3182 | 669.967 | 1293.8942 | 1259.2352 | 932.1216 | 2.8196 | 2.3468 | 2.8196 | 2.7992 | 2.6176
2 | SA-15-HH | 02-SA-15-HH | 974.4481 | 628.2313 | 1194.6983 | 1160.2449 | 867.0029 | 974.4481 | 628.2313 | 1194.6983 | 1160.2449 | 867.0029 | 2.8365 | 2.3241 | 2.7671 | 2.7401 | 2.6038
2 | SA-15-HL | 02-SA-15-HL | 954.3126 | 607.0736 | 1181.5648 | 1144.7982 | 847.5619 | 954.3126 | 607.0736 | 1181.5648 | 1144.7982 | 847.5619 | 2.8811 | 2.3534 | 2.8742 | 2.8454 | 2.6537
2 | SA-15-HM | 02-SA-15-HM | 967.457 | 618.801 | 1190.3845 | 1155.936 | 859.4946 | 967.457 | 618.801 | 1190.3845 | 1155.936 | 859.4946 | 2.7748 | 2.246 | 2.6946 | 2.6677 | 2.5331
2 | SA-15-MH | 02-SA-15-MH | 1008.5592 | 644.5438 | 1236.2718 | 1200.9118 | 894.9301 | 1008.5592 | 644.5438 | 1236.2718 | 1200.9118 | 894.9301 | 2.8592 | 2.3667 | 2.8891 | 2.8641 | 2.6541
2 | SA-15-ML | 02-SA-15-ML | 984.8069 | 624.3963 | 1215.6157 | 1181.4545 | 873.4117 | 984.8069 | 624.3963 | 1215.6157 | 1181.4545 | 873.4117 | 2.7981 | 2.2925 | 2.807 | 2.7813 | 2.5834
2 | SA-15-MM | 02-SA-15-MM | 987.3294 | 624.8445 | 1215.1061 | 1179.4168 | 874.3293 | 987.3294 | 624.8445 | 1215.1061 | 1179.4168 | 874.3293 | 2.8315 | 2.3275 | 2.8451 | 2.8205 | 2.6185
2 | SA-16-CH | 02-SA-16-CH | 1150.1338 | 727.6423 | 1307.4534 | 1272.1463 | 998.2341 | 1150.1338 | 727.6423 | 1307.4534 | 1272.1463 | 998.2341 | 3.0957 | 2.6082 | 3.0139 | 2.9861 | 2.8711
2 | SA-16-CL | 02-SA-16-CL | 1075.9734 | 677.9883 | 1228.4374 | 1194.7333 | 933.6631 | 1075.9734 | 677.9883 | 1228.4374 | 1194.7333 | 933.6631 | 3.0968 | 2.494 | 2.9083 | 2.8745 | 2.8023
2 | SA-16-CM | 02-SA-16-CM | 1111.8129 | 703.9277 | 1267.0733 | 1234.6195 | 965.9684 | 1111.8129 | 703.9277 | 1267.0733 | 1234.6195 | 965.9684 | 3.1072 | 2.55 | 2.9619 | 2.9313 | 2.8406
2 | SA-16-LH | 02-SA-16-LH | 972.5642 | 624.6099 | 1138.8465 | 1108.3799 | 854.3885 | 972.5642 | 624.6099 | 1138.8465 | 1108.3799 | 854.3885 | 2.8226 | 2.2687 | 2.7298 | 2.7012 | 2.5677
2 | SA-16-LL | 02-SA-16-LL | 1026.7964 | 652.768 | 1195.6855 | 1163.7781 | 897.951 | 1026.7964 | 652.768 | 1195.6855 | 1163.7781 | 897.951 | 3.044 | 2.4611 | 2.9457 | 2.9172 | 2.7757
2 | SA-16-LM | 02-SA-16-LM | 1026.4237 | 652.6074 | 1202.2299 | 1169.9767 | 898.9648 | 1026.4237 | 652.6074 | 1202.2299 | 1169.9767 | 898.9648 | 2.9375 | 2.3858 | 2.8437 | 2.815 | 2.6833
2 | SA-16-NM | 02-SA-16-NM | 942.277 | 590.3025 | 1103.7861 | 1071.8643 | 821.3451 | 942.277 | 590.3025 | 1103.7861 | 1071.8643 | 821.3451 | 2.7111 | 2.1643 | 2.6418 | 2.6089 | 2.4633
2 | SA-16-TH | 02-SA-16-TH | 1186.0475 | 774.6607 | 1307.2936 | 1273.3413 | 1032.0425 | 1186.0475 | 774.6607 | 1307.2936 | 1273.3413 | 1032.0425 | 3.2764 | 2.7024 | 3.1745 | 3.1432 | 3.0109
2 | SA-16-TL | 02-SA-16-TL | 1071.0053 | 682.014 | 1184.1082 | 1149.7811 | 924.8776 | 1071.0053 | 682.014 | 1184.1082 | 1149.7811 | 924.8776 | 3.1252 | 2.4987 | 2.9494 | 2.9183 | 2.8234
2 | SA-17-CH | 02-SA-17-CH | 1060.64 | 668.4744 | 1212.6525 | 1180.2625 | 920.8299 | 1060.64 | 668.4744 | 1212.6525 | 1180.2625 | 920.8299 | 2.9516 | 2.4736 | 2.8689 | 2.8398 | 2.7307
2 | SA-17-CL | 02-SA-17-CL | 1057.6932 | 664.4905 | 1209.5794 | 1175.97 | 917.3047 | 1057.6932 | 664.4905 | 1209.5794 | 1175.97 | 917.3047 | 2.9961 | 2.4803 | 2.8868 | 2.8547 | 2.7538
2 | SA-17-CM | 02-SA-17-CM | 1073.6393 | 677.0595 | 1216.7678 | 1184.7289 | 930.2869 | 1073.6393 | 677.0595 | 1216.7678 | 1184.7289 | 930.2869 | 2.983 | 2.4815 | 2.8899 | 2.8598 | 2.75
2 | SA-17-LH | 02-SA-17-LH | 943.5389 | 602.8197 | 1106.0426 | 1075.9179 | 827.7312 | 943.5389 | 602.8197 | 1106.0426 | 1075.9179 | 827.7312 | 2.7632 | 2.2231 | 2.6611 | 2.634 | 2.5124
2 | SA-17-LL | 02-SA-17-LL | 987.1489 | 625.6577 | 1145.3648 | 1114.0904 | 861.6178 | 987.1489 | 625.6577 | 1145.3648 | 1114.0904 | 861.6178 | 2.9201 | 2.3709 | 2.8223 | 2.7963 | 2.6664
2 | SA-17-LM | 02-SA-17-LM | 988.0059 | 626.8599 | 1153.3389 | 1122.4714 | 864.0271 | 988.0059 | 626.8599 | 1153.3389 | 1122.4714 | 864.0271 | 2.8514 | 2.3049 | 2.7716 | 2.7403 | 2.6018
2 | SA-17-TH | 02-SA-17-TH | 999.0907 | 655.432 | 1129.049 | 1100.311 | 875.9153 | 999.0907 | 655.432 | 1129.049 | 1100.311 | 875.9153 | 2.7814 | 2.2816 | 2.6925 | 2.667 | 2.5504
2 | SA-17-TL | 02-SA-17-TL | 917.0679 | 583.1475 | 1038.4796 | 1010.5085 | 796.4436 | 917.0679 | 583.1475 | 1038.4796 | 1010.5085 | 796.4436 | 2.8331 | 2.2745 | 2.6527 | 2.6262 | 2.5595
2 | SA-17-TM | 02-SA-17-TM | 1100.5541 | 707.5409 | 1173.9845 | 1141.0561 | 945.232 | 1100.5541 | 707.5409 | 1173.9845 | 1141.0561 | 945.232 | 2.9768 | 2.5189 | 2.8423 | 2.8241 | 2.7554
2 | SA-18-LH | 02-SA-18-LH | 925.1558 | 589.4332 | 1074.0095 | 1045.4902 | 808.991 | 925.1558 | 589.4332 | 1074.0095 | 1045.4902 | 808.991 | 2.695 | 2.1851 | 2.6111 | 2.5848 | 2.4606
2 | SA-18-LL | 02-SA-18-LL | 899.5818 | 569.7291 | 1053.24 | 1023.8255 | 786.7399 | 899.5818 | 569.7291 | 1053.24 | 1023.8255 | 786.7399 | 2.6835 | 2.1581 | 2.5985 | 2.5699 | 2.4421
2 | SA-18-TH | 02-SA-18-TH | 962.3383 | 632.715 | 1078.5645 | 1049.5573 | 842.4381 | 962.3383 | 632.715 | 1078.5645 | 1049.5573 | 842.4381 | 2.6412 | 2.1572 | 2.5404 | 2.5154 | 2.4146
2 | SA-18-TL | 02-SA-18-TL | 1040.8258 | 674.7549 | 1147.6146 | 1117.1027 | 903.545 | 1040.8258 | 674.7549 | 1147.6146 | 1117.1027 | 903.545 | 2.9538 | 2.4859 | 2.8689 | 2.842 | 2.737
2 | SA-18-TM | 02-SA-18-TM | 990.2814 | 645.7329 | 1120.0332 | 1091.5617 | 866.7149 | 990.2814 | 645.7329 | 1120.0332 | 1091.5617 | 866.7149 | 2.7138 | 2.2164 | 2.6089 | 2.5833 | 2.4807
2 | SH-10-HH | 02-SH-10-HH | 7132.2588 | 3892.4422 | 4515.0562 | 4209.3858 | 5847.5397 | 1402.3488 | 901.336 | 1732.3921 | 1682.1284 | 1260.3428 | 3.8558 | 3.2005 | 3.8035 | 3.7688 | 3.6337
2 | SH-10-HL | 02-SH-10-HL | 7177.6468 | 3944.9763 | 4602.6347 | 4287.6482 | 5898.2535 | 1449.8572 | 925.6927 | 1789.7642 | 1735.5767 | 1300.8214 | 4.0755 | 3.3609 | 3.9759 | 3.9415 | 3.8301
2 | SH-10-HM | 02-SH-10-HM | 6989.2991 | 3851.7436 | 4538.7738 | 4228.6687 | 5751.1722 | 1435.9989 | 914.7778 | 1761.9643 | 1709.1571 | 1286.9051 | 3.9118 | 3.2351 | 3.8941 | 3.8707 | 3.6856
2 | SH-10-LH | 02-SH-10-LH | 7493.1769 | 4034.284 | 4628.1047 | 4315.7439 | 6116.5578 | 1397.6142 | 897.6984 | 1723.8666 | 1677.8761 | 1255.8159 | 3.59 | 2.9866 | 3.5706 | 3.5455 | 3.3879
2 | SH-10-LL | 02-SH-10-LL | 7451.3027 | 4004.399 | 4613.5809 | 4296.5711 | 6080.6167 | 1425.4061 | 903.1388 | 1752.7767 | 1701.3681 | 1276.1194 | 3.9034 | 3.2422 | 3.8723 | 3.8377 | 3.681
2 | SH-10-LM | 02-SH-10-LM | 7215.7057 | 3931.4061 | 4538.8796 | 4231.5349 | 5911.5983 | 1398.4874 | 892.3657 | 1716.0546 | 1667.6485 | 1253.8857 | 3.7203 | 3.0834 | 3.6997 | 3.6709 | 3.5069
2 | SH-10-MH | 02-SH-10-MH | 7467.6068 | 4020.1997 | 4613.3281 | 4301.9127 | 6095.6549 | 1406.8983 | 898.3866 | 1729.9857 | 1684.402 | 1262.0225 | 3.7328 | 3.1021 | 3.6997 | 3.6741 | 3.5206
2 | SH-10-ML | 02-SH-10-ML | 7086.3697 | 3852.5785 | 4502.2117 | 4196.2186 | 5806.1879 | 1449.0505 | 915.7437 | 1776.1345 | 1723.8471 | 1296.0582 | 4.0655 | 3.3553 | 4.0457 | 4.0098 | 3.8277
2 | SH-10-MM | 02-SH-10-MM | 7231.4642 | 3949.4232 | 4591.0815 | 4280.7203 | 5930.8229 | 1439.3101 | 915.6205 | 1767.9793 | 1719.8083 | 1289.7569 | 3.8613 | 3.2022 | 3.7992 | 3.7713 | 3.6374
2 | SH-13-HH | 02-SH-13-HH | 6976.2907 | 3669.1369 | 4129.7787 | 3834.6637 | 5651.901 | 1159.6268 | 747.7913 | 1418.8053 | 1376.0395 | 1041.9142 | 3.279 | 2.6897 | 3.1788 | 3.1505 | 3.0752
2 | SH-13-HL | 02-SH-13-HL | 6158.8148 | 3238.6887 | 3731.6325 | 3468.9451 | 4996.007 | 1106.7575 | 702.3169 | 1370.0798 | 1328.9885 | 991.8673 | 3.2767 | 2.6956 | 3.3256 | 3.295 | 3.0871
2 | SH-13-HM | 02-SH-13-HM | 6278.0335 | 3331.7098 | 3825.8506 | 3556.6307 | 5104.4103 | 1137.4263 | 729.9274 | 1392.001 | 1349.8307 | 1020.8131 | 3.2575 | 2.6684 | 3.1641 | 3.1347 | 3.0543
2 | SH-13-LH | 02-SH-13-LH | 7618.5075 | 3863.1469 | 4149.4008 | 3848.9122 | 6097.4467 | 1102.5722 | 705.2284 | 1358.0845 | 1323.8403 | 989.6486 | 2.9264 | 2.4385 | 2.9249 | 2.903 | 2.764
2 | SH-13-LL | 02-SH-13-LL | 6501.0678 | 3359.2014 | 3765.8862 | 3496.3156 | 5240.8268 | 1065.1603 | 678.7687 | 1298.9642 | 1261.0813 | 954.069 | 3.0336 | 2.5043 | 3.0413 | 3.0154 | 2.8581
2 | SH-13-LM | 02-SH-13-LM | 5641.3564 | 3017.9275 | 3547.345 | 3309.3737 | 4603.3181 | 1143.129 | 727.2491 | 1414.667 | 1375.5934 | 1025.1508 | 3.0773 | 2.5595 | 3.0808 | 3.0574 | 2.9054
2 | SH-13-MH | 02-SH-13-MH | 6989.4679 | 3645.9864 | 4036.9812 | 3747.5683 | 5645.0467 | 1069.3812 | 691.3794 | 1320.0849 | 1281.1999 | 962.3411 | 3.0113 | 2.4895 | 3.005 | 2.9813 | 2.8373
2 | SH-13-ML | 02-SH-13-ML | 6709.1079 | 3474.1334 | 3944.9196 | 3667.8659 | 5415.5572 | 1157.7287 | 733.2036 | 1437.3828 | 1396.2101 | 1037.4476 | 3.2609 | 2.6993 | 3.2881 | 3.2617 | 3.0762
2 | SH-13-MM | 02-SH-13-MM | 6449.1045 | 3441.0168 | 3926.6581 | 3647.5242 | 5249.2844 | 1121.4858 | 713.6155 | 1374.3389 | 1333.4731 | 1004.6586 | 3.2108 | 2.6298 | 3.2153 | 3.1877 | 3.0179
2 | SH-14-HH | 02-SH-14-HH | 6467.2719 | 3382.8541 | 3834.6431 | 3563.3488 | 5233.9191 | 1095.2232 | 703.0567 | 1338.8775 | 1300.3166 | 982.959 | 3.1336 | 2.5597 | 3.0312 | 3.0036 | 2.9348
2 | SH-14-HL | 02-SH-14-HL | 6539.5699 | 3348.7932 | 3772.5588 | 3499.8108 | 5260.5736 | 1065.3184 | 676.5449 | 1307.802 | 1268.8179 | 954.0736 | 3.1208 | 2.5278 | 3.0105 | 2.9809 | 2.915
2 | SH-14-HM | 02-SH-14-HM | 6438.8172 | 3333.8999 | 3756.0993 | 3488.4868 | 5194.926 | 1065.7147 | 680.981 | 1307.1059 | 1269.2218 | 955.7584 | 2.9947 | 2.4335 | 2.8893 | 2.8613 | 2.7998
2 | SH-14-MH | 02-SH-14-MH | 6998.8869 | 3543.2192 | 3841.4526 | 3562.7558 | 5601.8327 | 1028.9408 | 657.1871 | 1268.3601 | 1235.1054 | 923.2788 | 2.743 | 2.2781 | 2.7418 | 2.7215 | 2.5883
2 | SH-14-ML | 02-SH-14-ML | 7419.1561 | 3679.7399 | 3909.8879 | 3619.113 | 5900.5844 | 1033.8101 | 651.6723 | 1267.5284 | 1231.2112 | 924.171 | 2.9781 | 2.4328 | 2.9661 | 2.9415 | 2.7959
2 | SH-14-MM | 02-SH-14-MM | 6384.2464 | 3253.056 | 3654.9753 | 3393.5404 | 5128.2584 | 1033.6914 | 654.7013 | 1277.9025 | 1240.2422 | 925.8619 | 2.8918 | 2.3781 | 2.9062 | 2.881 | 2.722
2 | SH-15-HH | 02-SH-15-HH | 7593.5767 | 3838.1799 | 4033.856 | 3721.4376 | 6065.1204 | 981.9079 | 630.0065 | 1204.8785 | 1170.1574 | 881.5012 | 2.7515 | 2.2346 | 2.6613 | 2.635 | 2.5726
2 | SH-15-HL | 02-SH-15-HL | 5570.3226 | 2906.0268 | 3347.964 | 3110.8328 | 4508.8653 | 989.2034 | 631.3704 | 1215.2882 | 1179.2404 | 887.0306 | 2.9009 | 2.3902 | 2.8741 | 2.8484 | 2.7289
2 | SH-15-HM | 02-SH-15-HM | 5828.1576 | 2985.4696 | 3426.4855 | 3179.6722 | 4693.4708 | 953.6233 | 609.1546 | 1186.0318 | 1149.8473 | 856.3595 | 2.8135 | 2.3076 | 2.7933 | 2.7682 | 2.6436
2 | SH-15-MH | 02-SH-15-MH | 6851.8563 | 3400.7777 | 3682.2801 | 3414.1812 | 5455.7244 | 995.5496 | 633.033 | 1224.6022 | 1189.322 | 892.08 | 2.8446 | 2.3395 | 2.8558 | 2.8264 | 2.6773
2 | SH-15-ML | 02-SH-15-ML | 6539.9003 | 3242.2614 | 3526.8896 | 3271.2722 | 5207.0688 | 965.66 | 608.4278 | 1184.2879 | 1151.133 | 863.2031 | 2.82 | 2.29 | 2.8203 | 2.7967 | 2.6438
2 | SH-15-MM | 02-SH-15-MM | 6711.8722 | 3402.7409 | 3710.2562 | 3432.2825 | 5375.3969 | 948.846 | 605.9426 | 1175.1731 | 1139.6623 | 851.6524 | 2.8019 | 2.308 | 2.7921 | 2.7665 | 2.6368
2 | SH-16-CH | 02-SH-16-CH | 7294.0469 | 3870.8176 | 3843.2202 | 3560.4805 | 5884.9382 | 1107.8103 | 705.1493 | 1260.366 | 1226.8804 | 985.1971 | 3.0352 | 2.4751 | 2.8838 | 2.8532 | 2.8371
2 | SH-16-CL | 02-SH-16-CL | 6939.1209 | 3645.944 | 3691.8376 | 3425.2364 | 5589.3157 | 1130.506 | 715.2846 | 1277.6879 | 1244.4577 | 1003.3271 | 3.115 | 2.6443 | 3.0282 | 3.0039 | 2.9517
2 | SH-16-LH | 02-SH-16-LH | 7449.8361 | 3838.9402 | 3815.716 | 3529.6744 | 5964.3249 | 985.9786 | 640.1657 | 1154.6305 | 1124.9714 | 883.5543 | 2.7883 | 2.2634 | 2.7125 | 2.6851 | 2.6078
2 | SH-16-LL | 02-SH-16-LL | 7125.4292 | 3594.0108 | 3653.8673 | 3381.4947 | 5679.2305 | 1024.9016 | 648.7659 | 1201.9588 | 1168.8845 | 912.9769 | 2.9978 | 2.424 | 2.9043 | 2.8733 | 2.7996
2 | SH-16-LM | 02-SH-16-LM | 7587.444 | 3887.3393 | 3870.7155 | 3578.2686 | 6065.808 | 1022.5328 | 658.497 | 1197.9134 | 1165.9908 | 914.5219 | 2.918 | 2.3527 | 2.8161 | 2.7864 | 2.722
2 | SH-16-TH | 02-SH-16-TH | 8539.8852 | 4697.986 | 4361.7521 | 4027.45 | 6934.3109 | 1045.5911 | 681.7644 | 1166.218 | 1133.2897 | 933.3873 | 3.0514 | 2.4648 | 2.9277 | 2.8972 | 2.8466
2 | SH-16-TL | 02-SH-16-TL | 8588.9876 | 4673.019 | 4433.6503 | 4097.0866 | 6960.5771 | 1182.426 | 755.3259 | 1308.3119 | 1270.9875 | 1049.5372 | 3.3372 | 2.7808 | 3.2349 | 3.2024 | 3.144
2 | SH-16-TM | 02-SH-16-TM | 8631.1555 | 4707.0596 | 4454.6409 | 4117.7271 | 6998.4069 | 1167.2007 | 746.8093 | 1290.6673 | 1255.0354 | 1036.4007 | 3.275 | 2.7313 | 3.1736 | 3.1435 | 3.0862
2 | SH-17-CM | 02-SH-17-CM | 7283.419 | 3787.2506 | 3704.3884 | 3431.3019 | 5840.5665 | 1068.6428 | 676.8038 | 1208.4931 | 1177.0093 | 948.6956 | 2.9599 | 2.5108 | 2.8775 | 2.854 | 2.8041
2 | SH-17-LM | 02-SH-17-LM | 6914.5569 | 3488.7576 | 3540.535 | 3276.8874 | 5511.1444 | 1006.7856 | 644.971 | 1165.0989 | 1131.7497 | 898.1458 | 2.8778 | 2.4108 | 2.7832 | 2.7618 | 2.7152
2 | SH-17-TH | 02-SH-17-TH | 8460.7104 | 4652.1904 | 4302.1041 | 3969.2995 | 6867.7447 | 990.1755 | 642.5725 | 1113.5173 | 1083.2285 | 883.638 | 2.8609 | 2.3302 | 2.7505 | 2.7221 | 2.6757
2 | SH-17-TL | 02-SH-17-TL | 8464.8325 | 4638.5394 | 4282.1704 | 3951.5817 | 6864.195 | 998.5001 | 645.3741 | 1121.3517 | 1090.5818 | 890.0806 | 2.9209 | 2.375 | 2.8119 | 2.7841 | 2.7308
2 | SH-18-LH | 02-SH-18-LH | 7754.4674 | 4005.3885 | 3814.6462 | 3512.6217 | 6199.0739 | 924.8004 | 587.8982 | 1079.3485 | 1049.675 | 824.2365 | 2.7134 | 2.2031 | 2.6256 | 2.5993 | 2.5368
2 | SH-18-LL | 02-SH-18-LL | 7161.6566 | 3596.1039 | 3586.1096 | 3311.3641 | 5696.0466 | 957.5451 | 607.1992 | 1124.7677 | 1093.4777 | 853.4571 | 2.8025 | 2.2721 | 2.7044 | 2.6776 | 2.6184
2 | SH-18-LM | 02-SH-18-LM | 8094.1697 | 4217.8728 | 3958.8016 | 3641.3556 | 6481.052 | 929.9326 | 591.194 | 1079.7538 | 1049.8701 | 828.3887 | 2.764 | 2.237 | 2.6644 | 2.6359 | 2.5809
2 | SH-18-TM | 02-SH-18-TM | 8468.5459 | 4666.9827 | 4259.3345 | 3928.543 | 6874.0391 | 964.0185 | 628.3656 | 1102.7048 | 1071.1571 | 862.5826 | 2.8227 | 2.3104 | 2.7529 | 2.7247 | 2.6468
3 | SA-10-HH | 03-SA-10-HH | 324.7956 | 154.0685 | 540.0302 | 528.7623 | 331.4935 | 324.7956 | 154.0685 | 540.0302 | 528.7623 | 331.4935 | 2.2029 | 1.5458 | 2.503 | 2.4815 | 2.0727
3 | SA-10-HL | 03-SA-10-HL | 322.6924 | 152.7769 | 537.6181 | 529.0653 | 329.76 | 322.6924 | 152.7769 | 537.6181 | 529.0653 | 329.76 | 2.2472 | 1.5586 | 2.5711 | 2.5751 | 2.1155
3 | SA-10-HM | 03-SA-10-HM | 323.451 | 152.2332 | 541.0932 | 532.2119 | 330.8729 | 323.451 | 152.2332 | 541.0932 | 532.2119 | 330.8729 | 2.2375 | 1.5511 | 2.5464 | 2.5584 | 2.1026
3 | SA-10-LH | 03-SA-10-LH | 309.947 | 146.6207 | 527.3923 | 519.3315 | 319.9879 | 309.947 | 146.6207 | 527.3923 | 519.3315 | 319.9879 | 2.1086 | 1.4934 | 2.4382 | 2.4514 | 2.0036
3 | SA-10-LL | 03-SA-10-LL | 327.6699 | 153.4098 | 550.6606 | 541.605 | 335.6641 | 327.6699 | 153.4098 | 550.6606 | 541.605 | 335.6641 | 2.2673 | 1.5782 | 2.6094 | 2.6055 | 2.1403
3 | SA-10-LM | 03-SA-10-LM | 312.6413 | 147.6838 | 531.3233 | 522.7546 | 322.4735 | 312.6413 | 147.6838 | 531.3233 | 522.7546 | 322.4735 | 2.1534 | 1.5168 | 2.4834 | 2.4916 | 2.041
3 | SA-10-MH | 03-SA-10-MH | 316.452 | 150.7245 | 532.9031 | 527.8066 | 325.6094 | 316.452 | 150.7245 | 532.9031 | 527.8066 | 325.6094 | 2.1079 | 1.5042 | 2.4139 | 2.4423 | 2.0007
3 | SA-10-ML | 03-SA-10-ML | 332.0421 | 155.9462 | 554.2584 | 545.3996 | 339.21 | 332.0421 | 155.9462 | 554.2584 | 545.3996 | 339.21 | 2.3136 | 1.6024 | 2.65 | 2.6486 | 2.1777
3 | SA-10-MM | 03-SA-10-MM | 305.7687 | 144.7638 | 517.0936 | 505.4427 | 314.5011 | 305.7687 | 144.7638 | 517.0936 | 505.4427 | 314.5011 | 2.0453 | 1.4491 | 2.3751 | 2.3588 | 1.9446
3 | SA-13-HH | 03-SA-13-HH | 245.768 | 116.0748 | 415.3983 | 409.049 | 252.8393 | 245.768 | 116.0748 | 415.3983 | 409.049 | 252.8393 | 1.6616 | 1.164 | 1.9168 | 1.9247 | 1.573
3 | SA-13-HL | 03-SA-13-HL | 240.932 | 112.8838 | 406.777 | 398.3611 | 247.2745 | 240.932 | 112.8838 | 406.777 | 398.3611 | 247.2745 | 1.6517 | 1.1553 | 1.9261 | 1.9207 | 1.5683
3 | SA-13-HM | 03-SA-13-HM | 243.5489 | 114.9955 | 410.5402 | 402.5368 | 250.0946 | 243.5489 | 114.9955 | 410.5402 | 402.5368 | 250.0946 | 1.6961 | 1.1852 | 1.9659 | 1.9626 | 1.6067
3 | SA-13-LH | 03-SA-13-LH | 238.7565 | 113.1843 | 405.4908 | 392.7939 | 245.8827 | 238.7565 | 113.1843 | 405.4908 | 392.7939 | 245.8827 | 1.614 | 1.1402 | 1.86 | 1.8386 | 1.5285
3 | SA-13-LL | 03-SA-13-LL | 246.9157 | 116.2344 | 416.5496 | 408.6587 | 253.5509 | 246.9157 | 116.2344 | 416.5496 | 408.6587 | 253.5509 | 1.698 | 1.191 | 1.9709 | 1.9524 | 1.6097
3 | SA-13-LM | 03-SA-13-LM | 249.5959 | 118.2152 | 423.1092 | 414.3897 | 257.0968 | 249.5959 | 118.2152 | 423.1092 | 414.3897 | 257.0968 | 1.6737 | 1.1923 | 1.9345 | 1.9181 | 1.5905
3 | SA-13-MH | 03-SA-13-MH | 233.0847 | 111.9741 | 388.1563 | 383.3582 | 238.7744 | 233.0847 | 111.9741 | 388.1563 | 383.3582 | 238.7744 | 1.6177 | 1.1361 | 1.8558 | 1.864 | 1.5294
3 | SA-13-ML | 03-SA-13-ML | 241.4878 | 113.7211 | 410.2867 | 402.2661 | 248.8323 | 241.4878 | 113.7211 | 410.2867 | 402.2661 | 248.8323 | 1.6689 | 1.175 | 1.9457 | 1.944 | 1.5874
3 | SA-13-MM | 03-SA-13-MM | 231.8099 | 110.0381 | 384.2898 | 377.3791 | 236.3578 | 231.8099 | 110.0381 | 384.2898 | 377.3791 | 236.3578 | 1.6403 | 1.1277 | 1.8817 | 1.8798 | 1.542
3 | SA-14-HH | 03-SA-14-HH | 232.7279 | 111.0748 | 394.3713 | 387.4921 | 240.0494 | 232.7279 | 111.0748 | 394.3713 | 387.4921 | 240.0494 | 1.5977 | 1.1291 | 1.8564 | 1.8614 | 1.5196
3 | SA-14-HL | 03-SA-14-HL | 223.086 | 105.0088 | 377.41 | 369.8089 | 229.3612 | 223.086 | 105.0088 | 377.41 | 369.8089 | 229.3612 | 1.5333 | 1.0752 | 1.7996 | 1.7951 | 1.4603
3 | SA-14-HM | 03-SA-14-HM | 223.4286 | 105.8691 | 379.9452 | 372.8901 | 230.568 | 223.4286 | 105.8691 | 379.9452 | 372.8901 | 230.568 | 1.5356 | 1.0841 | 1.8112 | 1.8099 | 1.4678
3 | SA-14-MH | 03-SA-14-MH | 237.883 | 112.9471 | 402.2694 | 392.7332 | 244.7443 | 237.883 | 112.9471 | 402.2694 | 392.7332 | 244.7443 | 1.5873 | 1.1319 | 1.8205 | 1.8067 | 1.5047
3 | SA-14-ML | 03-SA-14-ML | 225.5797 | 106.8179 | 385.6452 | 378.5166 | 233.3729 | 225.5797 | 106.8179 | 385.6452 | 378.5166 | 233.3729 | 1.5418 | 1.0868 | 1.8085 | 1.8086 | 1.4703
3 | SA-14-MM | 03-SA-14-MM | 229.8106 | 108.8541 | 389.5982 | 380.0383 | 236.6202 | 229.8106 | 108.8541 | 389.5982 | 380.0383 | 236.6202 | 1.5412 | 1.1021 | 1.7818 | 1.7679 | 1.4662
3 | SA-15-HH | 03-SA-15-HH | 208.284 | 99.5956 | 348.2199 | 343.2493 | 213.5726 | 208.284 | 99.5956 | 348.2199 | 343.2493 | 213.5726 | 1.4318 | 1.01 | 1.6453 | 1.6541 | 1.356
3 | SA-15-HL | 03-SA-15-HL | 203.7682 | 96.5511 | 341.9846 | 335.4404 | 208.921 | 203.7682 | 96.5511 | 341.9846 | 335.4404 | 208.921 | 1.4074 | 0.98375 | 1.6447 | 1.6404 | 1.3372
3 | SA-15-HM | 03-SA-15-HM | 210.6193 | 100.1689 | 358.8181 | 348.6601 | 217.419 | 210.6193 | 100.1689 | 358.8181 | 348.6601 | 217.419 | 1.4321 | 1.0117 | 1.6911 | 1.6608 | 1.3676
3 | SA-15-MH | 03-SA-15-MH | 210.7603 | 100.5478 | 354.3662 | 349.0136 | 216.61 | 210.7603 | 100.5478 | 354.3662 | 349.0136 | 216.61 | 1.4205 | 1.015 | 1.6558 | 1.6665 | 1.3568
3 | SA-15-ML | 03-SA-15-ML | 210.5132 | 99.8913 | 353.9939 | 345.3732 | 215.9582 | 210.5132 | 99.8913 | 353.9939 | 345.3732 | 215.9582 | 1.4629 | 1.0249 | 1.702 | 1.6845 | 1.3876
3 | SA-15-MM | 03-SA-15-MM | 209.7668 | 99.0054 | 355.5368 | 349.1488 | 216.0062 | 209.7668 | 99.0054 | 355.5368 | 349.1488 | 216.0062 | 1.4299 | 1.0064 | 1.6685 | 1.6689 | 1.3605
3 | SA-16-CH | 03-SA-16-CH | 241.8052 | 114.4019 | 385.4074 | 374.6289 | 241.563 | 241.8052 | 114.4019 | 385.4074 | 374.6289 | 241.563 | 1.6258 | 1.1493 | 1.8203 | 1.7971 | 1.524
3 | SA-16-CL | 03-SA-16-CL | 226.3551 | 107.9965 | 363.4819 | 353.8929 | 227.269 | 226.3551 | 107.9965 | 363.4819 | 353.8929 | 227.269 | 1.5469 | 1.0866 | 1.7275 | 1.7127 | 1.4469
3 | SA-16-CM | 03-SA-16-CM | 231.8871 | 110.6666 | 373.3856 | 363.7566 | 233.1515 | 231.8871 | 110.6666 | 373.3856 | 363.7566 | 233.1515 | 1.5852 | 1.1173 | 1.7682 | 1.7535 | 1.4834
3 | SA-16-LH | 03-SA-16-LH | 221.3748 | 105.2291 | 348.8009 | 344.0534 | 220.4741 | 221.3748 | 105.2291 | 348.8009 | 344.0534 | 220.4741 | 1.4507 | 1.0014 | 1.6151 | 1.5744 | 1.3477
3 | SA-16-LL | 03-SA-16-LL | 228.9353 | 108.4416 | 365.7013 | 357.0208 | 229.0973 | 228.9353 | 108.4416 | 365.7013 | 357.0208 | 229.0973 | 1.5054 | 1.0522 | 1.6846 | 1.6449 | 1.4056
3 | SA-16-LM | 03-SA-16-LM | 229.3351 | 108.5053 | 371.1069 | 361.9347 | 230.8431 | 229.3351 | 108.5053 | 371.1069 | 361.9347 | 230.8431 | 1.5023 | 1.0538 | 1.6917 | 1.6614 | 1.4077
3 | SA-16-NM | 03-SA-16-NM | 221.845 | 102.4087 | 357.4835 | 348.1538 | 221.9758 | 221.845 | 102.4087 | 357.4835 | 348.1538 | 221.9758 | 1.3945 | 0.98555 | 1.5951 | 1.5407 | 1.3147
3 | SA-16-TH | 03-SA-16-TH | 242.6476 | 120.1671 | 352.7656 | 354.2928 | 234.9284 | 242.6476 | 120.1671 | 352.7656 | 354.2928 | 234.9284 | 1.592 | 1.1321 | 1.7228 | 1.713 | 1.4776
3 | SA-16-TL | 03-SA-16-TL | 231.5093 | 110.3009 | 335.4271 | 334.2872 | 222.175 | 231.5093 | 110.3009 | 335.4271 | 334.2872 | 222.175 | 1.5925 | 1.0871 | 1.7051 | 1.6756 | 1.4562
3 | SA-17-CH | 03-SA-17-CH | 220.453 | 104.6601 | 354.7729 | 346.0638 | 221.4441 | 220.453 | 104.6601 | 354.7729 | 346.0638 | 221.4441 | 1.4949 | 1.0544 | 1.6742 | 1.6602 | 1.4011
3 | SA-17-CL | 03-SA-17-CL | 220.3921 | 104.5909 | 354.3911 | 345.166 | 221.2482 | 220.3921 | 104.5909 | 354.3911 | 345.166 | 221.2482 | 1.5014 | 1.056 | 1.6887 | 1.6675 | 1.4079
3 | SA-17-CM | 03-SA-17-CM | 224.4466 | 106.2527 | 351.6596 | 347.4032 | 222.8373 | 224.4466 | 106.2527 | 351.6596 | 347.4032 | 222.8373 | 1.5183 | 1.0692 | 1.6889 | 1.677 | 1.4192
3 | SA-17-LH | 03-SA-17-LH | 209.1327 | 100.1557 | 334.9311 | 329.8331 | 210.1015 | 209.1327 | 100.1557 | 334.9311 | 329.8331 | 210.1015 | 1.3666 | 0.95756 | 1.5497 | 1.5106 | 1.2827
3 | SA-17-LL | 03-SA-17-LL | 217.3853 | 102.9198 | 347.2689 | 338.5707 | 217.4951 | 217.3853 | 102.9198 | 347.2689 | 338.5707 | 217.4951 | 1.4351 | 0.99942 | 1.5993 | 1.5675 | 1.3372
3 | SA-17-LM | 03-SA-17-LM | 220.2868 | 104.2786 | 350.6371 | 344.8728 | 220.2316 | 220.2868 | 104.2786 | 350.6371 | 344.8728 | 220.2316 | 1.4439 | 1.0168 | 1.6105 | 1.5876 | 1.3502
3 | SA-17-TH | 03-SA-17-TH | 206.7424 | 102.1208 | 307.6755 | 303.6538 | 201.8201 | 206.7424 | 102.1208 | 307.6755 | 303.6538 | 201.8201 | 1.3983 | 0.98575 | 1.5313 | 1.5186 | 1.3001
3 | SA-17-TL | 03-SA-17-TL | 189.26 | 92.289 | 285.6852 | 278.2344 | 185.2904 | 189.26 | 92.289 | 285.6852 | 278.2344 | 185.2904 | 1.3919 | 0.93866 | 1.5401 | 1.4896 | 1.2821
3 | SA-17-TM | 03-SA-17-TM | 231.9266 | 109.9429 | 329.7991 | 326.0251 | 220.346 | 231.9266 | 109.9429 | 329.7991 | 326.0251 | 220.346 | 1.5551 | 1.0702 | 1.6262 | 1.6125 | 1.4144
3 | SA-18-LH | 03-SA-18-LH | 205.7398 | 97.7284 | 327.5199 | 320.257 | 205.6778 | 205.7398 | 97.7284 | 327.5199 | 320.257 | 205.6778 | 1.3456 | 0.93791 | 1.4959 | 1.467 | 1.253
3 | SA-18-LL | 03-SA-18-LL | 199.0995 | 94.2089 | 316.8277 | 310.425 | 198.9264 | 199.0995 | 94.2089 | 316.8277 | 310.425 | 198.9264 | 1.3359 | 0.9233 | 1.5046 | 1.4628 | 1.2463
3 | SA-18-TH | 03-SA-18-TH | 202.2465 | 99.4437 | 294.3547 | 296.9219 | 195.7637 | 202.2465 | 99.4437 | 294.3547 | 296.9219 | 195.7637 | 1.345 | 0.94689 | 1.4385 | 1.4439 | 1.2411
3 | SA-18-TL | 03-SA-18-TL | 207.114 | 101.2676 | 302.0074 | 301.4173 | 200.2276 | 207.114 | 101.2676 | 302.0074 | 301.4173 | 200.2276 | 1.4012 | 0.98052 | 1.5127 | 1.5033 | 1.2941
3 | SA-18-TM | 03-SA-18-TM | 206.4692 | 102.1214 | 313.6848 | 309.3349 | 203.4875 | 206.4692 | 102.1214 | 313.6848 | 309.3349 | 203.4875 | 1.3706 | 0.9851 | 1.5126 | 1.5021 | 1.2842
3 | SH-10-HH | 03-SH-10-HH | 3960.9424 | 1967.1935 | 2214.1552 | 1969.2695 | 3423.2629 | 315.0202 | 149.0451 | 528.1262 | 521.36 | 305.6504 | 2.1132 | 1.4831 | 2.4156 | 2.4323 | 2.029
3 | SH-10-HL | 03-SH-10-HL | 4023.9258 | 1988.5173 | 2247.7937 | 1991.0882 | 3475.5645 | 322.5228 | 151.6933 | 542.5097 | 533.3738 | 312.8947 | 2.1988 | 1.5357 | 2.5268 | 2.5299 | 2.1108
3 | SH-10-HM | 03-SH-10-HM | 3837.9154 | 1919.2653 | 2192.8038 | 1947.5233 | 3323.7893 | 317.7089 | 150.7807 | 529.4457 | 523.0113 | 308.0397 | 2.1759 | 1.5258 | 2.4792 | 2.4886 | 2.088
3 | SH-10-LH | 03-SH-10-LH | 4178.5629 | 2080.0265 | 2316.5363 | 2039.0255 | 3609.8966 | 316.8126 | 150.3017 | 533.3222 | 522.0136 | 307.5791 | 2.0869 | 1.49 | 2.3744 | 2.3544 | 2.0064
3 | SH-10-LL | 03-SH-10-LL | 3955.3433 | 1954.2111 | 2211.1521 | 1960.9741 | 3416.4636 | 320.9351 | 151.1135 | 540.5053 | 532.1543 | 311.4662 | 2.1906 | 1.5361 | 2.5209 | 2.5235 | 2.1044
3 | SH-10-LM | 03-SH-10-LM | 3902.9025 | 1948.2995 | 2203.631 | 1962.4184 | 3377.0489 | 319.5646 | 151.1809 | 535.1404 | 529.1753 | 310.0178 | 2.1425 | 1.5087 | 2.4457 | 2.4589 | 2.0576
3 | SH-10-MH | 03-SH-10-MH | 4106.9282 | 2037.1031 | 2271.1278 | 2017.1956 | 3546.5502 | 312.3384 | 148.1893 | 527.4498 | 521.3742 | 303.511 | 2.1082 | 1.4929 | 2.4102 | 2.4299 | 2.0267
3 | SH-10-ML | 03-SH-10-ML | 3709.5845 | 1832.3243 | 2102.9173 | 1864.9631 | 3206.8833 | 319.6075 | 150.273 | 536.2215 | 527.2461 | 309.9238 | 2.2087 | 1.5388 | 2.5493 | 2.5438 | 2.1205
3 | SH-10-MM | 03-SH-10-MM | 3995.8506 | 1980.1571 | 2231.2065 | 1964.2332 | 3451.9611 | 320.7996 | 152.1299 | 533.1771 | 522.0505 | 310.7745 | 2.2172 | 1.5421 | 2.5152 | 2.4905 | 2.1235
3 | SH-13-HH | 03-SH-13-HH | 3753.9707 | 1853.5021 | 2027.9878 | 1794.3202 | 3235.4791 | 246.3457 | 117.1223 | 409.1478 | 404.1936 | 238.7526 | 1.6876 | 1.1801 | 1.934 | 1.9466 | 1.62
3 | SH-13-HL | 03-SH-13-HL | 3275.9561 | 1608.0541 | 1810.3522 | 1584.4857 | 2825.2695 | 238.4936 | 112.815 | 413.4146 | 398.4133 | 232.5084 | 1.6411 | 1.1445 | 1.9517 | 1.913 | 1.5806
3 | SH-13-HM | 03-SH-13-HM | 3362.6862 | 1662.5761 | 1852.2918 | 1638.3482 | 2902.0404 | 244.2159 | 115.7831 | 406.8121 | 400.5278 | 236.7167 | 1.6872 | 1.1752 | 1.9369 | 1.9425 | 1.6189
3 | SH-13-LH | 03-SH-13-LH | 3958.0864 | 1903.224 | 2044.8887 | 1786.8238 | 3392.7538 | 241.0218 | 114.8309 | 409.4893 | 395.41 | 234.3324 | 1.617 | 1.1552 | 1.8687 | 1.8469 | 1.5575
3 | SH-13-LL | 03-SH-13-LL | 3443.1221 | 1684.3408 | 1846.6131 | 1627.6666 | 2963.3046 | 233.9393 | 110.6256 | 387.6922 | 380.1973 | 226.4757 | 1.6329 | 1.1376 | 1.8619 | 1.8641 | 1.5656
3 | SH-13-LM | 03-SH-13-LM | 3095.6095 | 1527.4887 | 1733.2709 | 1526.1169 | 2673.5247 | 251.2757 | 118.5858 | 427.0403 | 417.8041 | 244.229 | 1.6886 | 1.2047 | 1.9595 | 1.943 | 1.627
3 | SH-13-MH | 03-SH-13-MH | 3768.6543 | 1863.044 | 2004.4498 | 1775.8999 | 3245.6022 | 232.7909 | 111.2988 | 385.5643 | 381.7821 | 225.6431 | 1.5561 | 1.098 | 1.7814 | 1.7999 | 1.4955
3 | SH-13-ML | 03-SH-13-ML | 3612.1203 | 1748.8064 | 1917.7937 | 1680.8837 | 3103.3895 | 247.8393 | 117.1518 | 419.5516 | 410.4552 | 240.762 | 1.6883 | 1.194 | 1.9717 | 1.9545 | 1.6261
3 | SH-13-MM | 03-SH-13-MM | 3520.6047 | 1741.5304 | 1912.2649 | 1685.1653 | 3035.7724 | 235.74 | 112.7178 | 393.8766 | 387.0136 | 228.7722 | 1.6423 | 1.1495 | 1.9021 | 1.9039 | 1.5785
3 | SH-14-HH | 03-SH-14-HH | 3428.7239 | 1689.6351 | 1861.5998 | 1643.1933 | 2955.3633 | 231.2335 | 110.3008 | 385.735 | 378.9751 | 224.2908 | 1.5975 | 1.1141 | 1.8372 | 1.8444 | 1.5335
3 | SH-14-HL | 03-SH-14-HL | 3387.8369 | 1645.8513 | 1818.0357 | 1597.2131 | 2913.6362 | 227.3434 | 107.1865 | 383.9234 | 375.6336 | 220.7111 | 1.6008 | 1.1103 | 1.8586 | 1.8504 | 1.537
3 | SH-14-HM | 03-SH-14-HM | 3341.5444 | 1637.814 | 1810.1681 | 1598.6443 | 2878.2419 | 230.962 | 109.1597 | 387.4058 | 380.628 | 224.0514 | 1.5891 | 1.1076 | 1.8272 | 1.8328 | 1.5253
3 | SH-14-MH | 03-SH-14-MH | 3571.7315 | 1723.3476 | 1869.572 | 1638.2875 | 3065.0634 | 226.3327 | 107.4793 | 384.7905 | 375.3856 | 220.096 | 1.5157 | 1.0791 | 1.7484 | 1.7337 | 1.459
3 | SH-14-ML | 03-SH-14-ML | 3753.2492 | 1779.4993 | 1893.9684 | 1659.0539 | 3208.4024 | 219.4045 | 102.9465 | 373.1592 | 365.6886 | 213.184 | 1.5054 | 1.0471 | 1.7571 | 1.7537 | 1.4469
3 | SH-14-MM | 03-SH-14-MM | 3310.2503 | 1606.281 | 1769.8304 | 1552.1085 | 2845.8832 | 224.2299 | 105.8089 | 383.7846 | 374.6943 | 218.1858 | 1.5374 | 1.0836 | 1.7954 | 1.7786 | 1.4801
3 | SH-15-HH | 03-SH-15-HH | 3966.4953 | 1901.2791 | 2007.8417 | 1759.223 | 3395.0446 | 213.0939 | 101.5744 | 355.605 | 350.2982 | 206.7155 | 1.4435 | 1.0155 | 1.6586 | 1.6676 | 1.3872
3 | SH-15-HL | 03-SH-15-HL | 2918.3846 | 1434.2699 | 1606.5717 | 1417.045 | 2516.8569 | 213.3465 | 100.9028 | 358.9038 | 351.8075 | 207.0595 | 1.4866 | 1.0335 | 1.7225 | 1.7182 | 1.4275
3 | SH-15-HM | 03-SH-15-HM | 3014.0345 | 1481.7295 | 1652.4293 | 1457.1643 | 2598.7736 | 205.1143 | 97.5405 | 345.2985 | 339.1574 | 199.2049 | 1.393 | 0.9761 | 1.6254 | 1.6275 | 1.3402
3 | SH-15-MH | 03-SH-15-MH | 3571.6706 | 1700.7505 | 1804.4414 | 1584.3422 | 3054.795 | 204.4902 | 97.2183 | 346.1555 | 339.9203 | 198.7784 | 1.3915 | 0.98594 | 1.632 | 1.6402 | 1.3417
3 | SH-15-ML | 03-SH-15-ML | 3284.8237 | 1571.2253 | 1692.9367 | 1485.8688 | 2813.908 | 204.748 | 96.152 | 348.2588 | 340.5804 | 198.9452 | 1.4132 | 0.98163 | 1.6516 | 1.6484 | 1.3583
3 | SH-15-MM | 03-SH-15-MM | 3435.6866 | 1666.1604 | 1790.4361 | 1572.0042 | 2949.1623 | 203.0179 | 96.9605 | 340.3168 | 334.1892 | 197.1012 | 1.4049 | 0.98693 | 1.6334 | 1.6309 | 1.3515
3 | SH-16-CH | 03-SH-16-CH | 3552.6093 | 1700.5972 | 1751.259 | 1536.0108 | 3035.9272 | 236.5691 | 112.9147 | 375.6335 | 365.2556 | 227.5428 | 1.5858 | 1.12 | 1.7611 | 1.7466 | 1.5182
3 | SH-16-CL | 03-SH-16-CL | 3324.4515 | 1583.3176 | 1654.9193 | 1453.7816 | 2841.076 | 234.0589 | 110.7643 | 371.7033 | 361.9092 | 224.9716 | 1.5809 | 1.1114 | 1.7656 | 1.7507 | 1.5136
3 | SH-16-LH | 03-SH-16-LH | 3837.4307 | 1858.5912 | 1891.5372 | 1673.6019 | 3283.557 | 222.2047 | 106.4701 | 347.813 | 345.1339 | 213.4657 | 1.4261 | 1.0007 | 1.5662 | 1.5525 | 1.3624
3 | SH-16-LL | 03-SH-16-LL | 3557.3363 | 1676.5396 | 1756.1693 | 1541.1297 | 3035.4601 | 229.4562 | 108.4987 | 370.6988 | 361.6123 | 221.1601 | 1.5084 | 1.0582 | 1.7018 | 1.6666 | 1.445
3 | SH-16-LM | 03-SH-16-LM | 3865.825 | 1858.3587 | 1904.9123 | 1682.2185 | 3305.1886 | 229.5334 | 110.279 | 366.9735 | 362.9726 | 221.2855 | 1.4608 | 1.0403 | 1.6462 | 1.6164 | 1.4021
3 | SH-16-TH | 03-SH-16-TH | 4315.6589 | 2115.1925 | 2022.1522 | 1778.8152 | 3687.0378 | 219.965 | 109.1709 | 324.3076 | 321.384 | 210.0345 | 1.4839 | 1.0436 | 1.6225 | 1.5946 | 1.417
3 | SH-16-TL | 03-SH-16-TL | 4358.5471 | 2078.6496 | 2003.0954 | 1746.6507 | 3709.1797 | 239.1269 | 114.7164 | 352.7114 | 348.9298 | 227.6145 | 1.639 | 1.1441 | 1.7808 | 1.7606 | 1.5627
3 | SH-16-TM | 03-SH-16-TM | 4417.6422 | 2114.6949 | 2031.0596 | 1772.2574 | 3760.9987 | 236.3922 | 113.6019 | 348.611 | 345.4798 | 225.054 | 1.6261 | 1.1333 | 1.7569 | 1.7428 | 1.5492
3 | SH-17-CM | 03-SH-17-CM | 3750.4846 | 1755.0076 | 1749.0567 | 1527.7729 | 3188.0864 | 220.2901 | 104.6744 | 350.4271 | 340.841 | 211.8642 | 1.4922 | 1.0488 | 1.6669 | 1.6534 | 1.4287
3 | SH-17-LM | 03-SH-17-LM | 3427.7709 | 1628.3676 | 1691.2517 | 1487.3393 | 2927.2177 | 216.5108 | 102.9123 | 342.1614 | 337.1101 | 208.1109 | 1.4271 | 1.0046 | 1.5727 | 1.5593 | 1.3645
3 | SH-17-TH | 03-SH-17-TH | 4286.8611 | 2094.1335 | 1993.0573 | 1745.3046 | 3659.5164 | 205.8406 | 100.7222 | 308.0888 | 303.3494 | 196.6938 | 1.4125 | 0.99167 | 1.5475 | 1.5284 | 1.349
3 | SH-17-TL | 03-SH-17-TL | 4258.9634 | 2069.5467 | 1969.8187 | 1722.592 | 3632.6863 | 206.1576 | 101.255 | 309.733 | 305.0122 | 197.1802 | 1.4224 | 0.9977 | 1.5675 | 1.5425 | 1.3591
3 | SH-18-LH | 03-SH-18-LH | 3872.3244 | 1834.5329 | 1817.399 | 1580.3411 | 3296.6748 | 201.5033 | 95.3689 | 321.6449 | 314.3524 | 193.8677 | 1.3299 | 0.92869 | 1.4868 | 1.4631 | 1.272
3 | SH-18-LL | 03-SH-18-LL | 3544.9481 | 1661.9939 | 1710.9354 | 1495.5636 | 3019.4587 | 207.6771 | 98.5783 | 337.046 | 328.7187 | 200.3847 | 1.3657 | 0.9639 | 1.5501 | 1.5251 | 1.3104
3 | SH-18-LM | 03-SH-18-LM | 4064.1437 | 1929.3636 | 1888.0962 | 1638.5918 | 3458.7882 | 202.2675 | 96.3541 | 322.214 | 315.1884 | 194.6587 | 1.3418 | 0.93311 | 1.5008 | 1.4667 | 1.2826
3 | SH-18-TM | 03-SH-18-TM | 4200.289 | 2048.5402 | 1906.6391 | 1672.0875 | 3580.676 | 191.6808 | 96.306 | 283.3566 | 284.5591 | 183.3956 | 1.3004 | 0.93139 | 1.4541 | 1.4426 | 1.2483
4 | SA-10-HH | 04-SA-10-HH | 1272.0892 | 773.7622 | 1627.4604 | 1603.0849 | 1230.0201 | 1272.0892 | 773.7622 | 1627.4604 | 1603.0849 | 1230.0201 | 3.5663 | 2.9523 | 3.3988 | 3.4013 | 3.3997
4 | SA-10-HL | 04-SA-10-HL | 1263.7457 | 765.6707 | 1640.0695 | 1610.677 | 1225.2052 | 1263.7457 | 765.6707 | 1640.0695 | 1610.677 | 1225.2052 | 3.7878 | 3.0995 | 3.6526 | 3.6463 | 3.6102
4 | SA-10-HM | 04-SA-10-HM | 1257.9797 | 761.2871 | 1634.678 | 1605.0106 | 1219.7793 | 1257.9797 | 761.2871 | 1634.678 | 1605.0106 | 1219.7793 | 3.6413 | 2.9522 | 3.455 | 3.4487 | 3.4535
4 | SA-10-LH | 04-SA-10-LH | 1185.7231 | 724.0435 | 1552.7451 | 1521.5563 | 1153.0686 | 1185.7231 | 724.0435 | 1552.7451 | 1521.5563 | 1153.0686 | 3.332 | 2.683 | 3.2374 | 3.2377 | 3.1718
4 | SA-10-LL | 04-SA-10-LL | 1267.5235 | 766.0518 | 1653.5043 | 1639.0789 | 1232.0562 | 1267.5235 | 766.0518 | 1653.5043 | 1639.0789 | 1232.0562 | 3.734 | 3.0493 | 3.6054 | 3.8874 | 3.5954
4 | SA-10-LM | 04-SA-10-LM | 1205.4988 | 735.6033 | 1573.2416 | 1542.3611 | 1171.2323 | 1205.4988 | 735.6033 | 1573.2416 | 1542.3611 | 1171.2323 | 3.4273 | 2.7804 | 3.3123 | 3.3133 | 3.2636
4 | SA-10-MH | 04-SA-10-MH | 1205.3722 | 737.1403 | 1568.8915 | 1538.5384 | 1170.7066 | 1205.3722 | 737.1403 | 1568.8915 | 1538.5384 | 1170.7066 | 3.2732 | 2.6668 | 3.1803 | 3.1806 | 3.1226
4 | SA-10-ML | 04-SA-10-ML | 1289.824 | 780.0485 | 1671.4684 | 1640.1655 | 1249.5304 | 1289.824 | 780.0485 | 1671.4684 | 1640.1655 | 1249.5304 | 3.7934 | 3.102 | 3.6488 | 3.6429 | 3.6133
4 | SA-10-MM | 04-SA-10-MM | 1183.3537 | 722.3772 | 1523.5617 | 1494.902 | 1145.9088 | 1183.3537 | 722.3772 | 1523.5617 | 1494.902 | 1145.9088 | 3.4274 | 2.7314 | 3.2862 | 3.2858 | 3.2477
4 | SA-13-HH | 04-SA-13-HH | 955.5201 | 580.8691 | 1253.6262 | 1246.5406 | 931.4085 | 955.5201 | 580.8691 | 1253.6262 | 1246.5406 | 931.4085 | 2.8083 | 2.279 | 2.7439 | 2.9579 | 2.7075
4 | SA-13-HL | 04-SA-13-HL | 931.6006 | 565.4975 | 1210.0518 | 1197.4971 | 904.7927 | 931.6006 | 565.4975 | 1210.0518 | 1197.4971 | 904.7927 | 2.8466 | 2.2524 | 2.7763 | 2.8855 | 2.7171
4 | SA-13-HM | 04-SA-13-HM | 948.374 | 570.9816 | 1242.0958 | 1230.1267 | 922.1772 | 948.374 | 570.9816 | 1242.0958 | 1230.1267 | 922.1772 | 2.915 | 2.3044 | 2.819 | 3.0184 | 2.7884
4 | SA-13-LH | 04-SA-13-LH | 915.146 | 555.9542 | 1199.9969 | 1173.6934 | 889.3426 | 915.146 | 555.9542 | 1199.9969 | 1173.6934 | 889.3426 | 2.5426 | 2.0708 | 2.4816 | 2.4819 | 2.4277
4 | SA-13-LL | 04-SA-13-LL | 957.2877 | 578.2252 | 1246.0791 | 1225.5435 | 928.6604 | 957.2877 | 578.2252 | 1246.0791 | 1225.5435 | 928.6604 | 2.7611 | 2.2452 | 2.6883 | 2.6889 | 2.6343
4 | SA-13-LM | 04-SA-13-LM | 950.4046 | 577.0226 | 1243.138 | 1216.6028 | 923.023 | 950.4046 | 577.0226 | 1243.138 | 1216.6028 | 923.023 | 2.647 | 2.1571 | 2.5842 | 2.5852 | 2.5279
4 | SA-13-MH | 04-SA-13-MH | 915.393 | 558.0529 | 1182.013 | 1158.4604 | 886.7645 | 915.393 | 558.0529 | 1182.013 | 1158.4604 | 886.7645 | 2.6319 | 2.1287 | 2.5852 | 2.5819 | 2.5125
4 | SA-13-ML | 04-SA-13-ML | 936.0188 | 565.8204 | 1223.6301 | 1199.5023 | 908.6342 | 936.0188 | 565.8204 | 1223.6301 | 1199.5023 | 908.6342 | 2.8352 | 2.2914 | 2.7628 | 2.7636 | 2.7024
4 | SA-13-MM | 04-SA-13-MM | 916.7407 | 555.3243 | 1183.5506 | 1174.1594 | 889.0739 | 916.7407 | 555.3243 | 1183.5506 | 1174.1594 | 889.0739 | 2.7351 | 2.2147 | 2.6641 | 2.864 | 2.6332
4 | SA-14-HH | 04-SA-14-HH | 904.2586 | 548.0899 | 1186.1135 | 1162.115 | 878.8217 | 904.2586 | 548.0899 | 1186.1135 | 1162.115 | 878.8217 | 2.6957 | 2.1908 | 2.6449 | 2.6431 | 2.5753
4 | SA-14-HL | 04-SA-14-HL | 862.3188 | 520.9881 | 1129.1526 | 1119.6539 | 839.0267 | 862.3188 | 520.9881 | 1129.1526 | 1119.6539 | 839.0267 | 2.5808 | 2.0293 | 2.5539 | 2.6573 | 2.4684
4 | SA-14-HM | 04-SA-14-HM | 860.7241 | 522.8522 | 1128.6186 | 1104.9159 | 836.5758 | 860.7241 | 522.8522 | 1128.6186 | 1104.9159 | 836.5758 | 2.5981 | 2.0532 | 2.572 | 2.5657 | 2.4733
4 | SA-14-MH | 04-SA-14-MH | 905.9831 | 551.6955 | 1183.5521 | 1162.9122 | 880.545 | 905.9831 | 551.6955 | 1183.5521 | 1162.9122 | 880.545 | 2.4715 | 2.0371 | 2.4072 | 2.4078 | 2.3641
4 | SA-14-ML | 04-SA-14-ML | 866.9362 | 523.6826 | 1140.2222 | 1117.0824 | 842.7446 | 866.9362 | 523.6826 | 1140.2222 | 1117.0824 | 842.7446 | 2.5721 | 2.043 | 2.5255 | 2.525 | 2.4474
4 | SA-14-MM | 04-SA-14-MM | 878.8867 | 534.3182 | 1152.0378 | 1126.8665 | 854.1214 | 878.8867 | 534.3182 | 1152.0378 | 1126.8665 | 854.1214 | 2.4554 | 2.0023 | 2.4051 | 2.4053 | 2.3466
4 | SA-15-HH | 04-SA-15-HH | 814.2392 | 496.0372 | 1061.5683 | 1055.9887 | 792.6652 | 814.2392 | 496.0372 | 1061.5683 | 1055.9887 | 792.6652 | 2.4792 | 1.9639 | 2.3965 | 2.5675 | 2.3724
4 | SA-15-HL | 04-SA-15-HL | 798.7655 | 482.4135 | 1038.1916 | 1029.8382 | 775.6873 | 798.7655 | 482.4135 | 1038.1916 | 1029.8382 | 775.6873 | 2.3846 | 1.878 | 2.3678 | 2.475 | 2.2844
4 | SA-15-HM | 04-SA-15-HM | 823.2427 | 497.1813 | 1072.6555 | 1065.472 | 800.1573 | 823.2427 | 497.1813 | 1072.6555 | 1065.472 | 800.1573 | 2.5006 | 1.9642 | 2.3822 | 2.5378 | 2.3802
4 | SA-15-MH | 04-SA-15-MH | 808.519 | 494.2936 | 1054.7876 | 1033.6321 | 785.6094 | 808.519 | 494.2936 | 1054.7876 | 1033.6321 | 785.6094 | 2.376 | 1.8778 | 2.3573 | 2.351 | 2.2628
4 | SA-15-ML | 04-SA-15-ML | 824.1268 | 497.9154 | 1070.1463 | 1048.6185 | 798.5045 | 824.1268 | 497.9154 | 1070.1463 | 1048.6185 | 798.5045 | 2.4339 | 1.9548 | 2.3789 | 2.379 | 2.3185
4 | SA-15-MM | 04-SA-15-MM | 808.6897 | 491.1224 | 1056.3576 | 1036.9497 | 785.5494 | 808.6897 | 491.1224 | 1056.3576 | 1036.9497 | 785.5494 | 2.3826 | 1.8806 | 2.3519 | 2.3451 | 2.2661
4 | SA-16-CH | 04-SA-16-CH | 978.652 | 589.4319 | 1205.2739 | 1192.3933 | 936.5744 | 978.652 | 589.4319 | 1205.2739 | 1192.3933 | 936.5744 | 2.837 | 2.3125 | 2.6724 | 2.8918 | 2.7183
4 | SA-16-CL | 04-SA-16-CL | 934.3329 | 561.8605 | 1149.6336 | 1136.1472 | 893.6088 | 934.3329 | 561.8605 | 1149.6336 | 1136.1472 | 893.6088 | 2.9446 | 2.2952 | 2.6759 | 2.8538 | 2.7729
4 | SA-16-CM | 04-SA-16-CM | 955.7653 | 575.3564 | 1177.3371 | 1166.467 | 914.8762 | 955.7653 | 575.3564 | 1177.3371 | 1166.467 | 914.8762 | 2.9428 | 2.3078 | 2.6828 | 2.8818 | 2.7786
4 | SA-16-LH | 04-SA-16-LH | 911.0192 | 560.0892 | 1110.7916 | 1093.1627 | 871.4156 | 911.0192 | 560.0892 | 1110.7916 | 1093.1627 | 871.4156 | 2.6547 | 2.1216 | 2.4556 | 2.4575 | 2.4995
4 | SA-16-LL | 04-SA-16-LL | 939.9212 | 574.1384 | 1158.7102 | 1141.6185 | 900.8807 | 939.9212 | 574.1384 | 1158.7102 | 1141.6185 | 900.8807 | 2.7957 | 2.2371 | 2.6004 | 2.601 | 2.6355
4 | SA-16-LM | 04-SA-16-LM | 933.4547 | 568.7123 | 1155.3218 | 1136.8318 | 895.0669 | 933.4547 | 568.7123 | 1155.3218 | 1136.8318 | 895.0669 | 2.7167 | 2.185 | 2.5354 | 2.5364 | 2.5652
4 | SA-16-NM | 04-SA-16-NM | 874.8883 | 523.2499 | 1087.9595 | 1064.4822 | 836.9936 | 874.8883 | 523.2499 | 1087.9595 | 1064.4822 | 836.9936 | 2.5865 | 2.0268 | 2.3361 | 2.3335 | 2.4148
4 | SA-16-TH | 04-SA-16-TH | 1027.4474 | 630.4081 | 1191.1112 | 1172.7263 | 970.5893 | 1027.4474 | 630.4081 | 1191.1112 | 1172.7263 | 970.5893 | 2.9114 | 2.3842 | 2.7224 | 2.7241 | 2.7594
4 | SA-16-TL | 04-SA-16-TL | 992.3203 | 598.5718 | 1148.9321 | 1138.1968 | 935.7749 | 992.3203 | 598.5718 | 1148.9321 | 1138.1968 | 935.7749 | 2.925 | 2.3724 | 2.686 | 2.8733 | 2.7814
4 | SA-17-CH | 04-SA-17-CH | 898.6175 | 539.3505 | 1112.3514 | 1099.0247 | 860.4883 | 898.6175 | 539.3505 | 1112.3514 | 1099.0247 | 860.4883 | 2.7575 | 2.1666 | 2.5143 | 2.7138 | 2.6063
4 | SA-17-CL | 04-SA-17-CL | 900.1245 | 539.9439 | 1114.512 | 1098.9374 | 861.6363 | 900.1245 | 539.9439 | 1114.512 | 1098.9374 | 861.6363 | 2.804 | 2.1975 | 2.5542 | 2.751 | 2.6477
4 | SA-17-CM | 04-SA-17-CM | 917.3616 | 549.2754 | 1121.159 | 1108.8095 | 875.4805 | 917.3616 | 549.2754 | 1121.159 | 1108.8095 | 875.4805 | 2.7997 | 2.1974 | 2.5492 | 2.7493 | 2.6446
4 | SA-17-LH | 04-SA-17-LH | 865.0094 | 530.1489 | 1064.2874 | 1047.5133 | 828.9254 | 865.0094 | 530.1489 | 1064.2874 | 1047.5133 | 828.9254 | 2.559 | 2.0454 | 2.3773 | 2.3788 | 2.4114
4 | SA-17-LL | 04-SA-17-LL | 894.8049 | 544.6371 | 1102.162 | 1083.715 | 856.7529 | 894.8049 | 544.6371 | 1102.162 | 1083.715 | 856.7529 | 2.6767 | 2.1424 | 2.485 | 2.4851 | 2.5224
4 | SA-17-LM | 04-SA-17-LM | 895.153 | 544.684 | 1110.4221 | 1093.018 | 858.7233 | 895.153 | 544.684 | 1110.4221 | 1093.018 | 858.7233 | 2.6267 | 2.0869 | 2.4507 | 2.4505 | 2.4742
4 | SA-17-TH | 04-SA-17-TH | 865.5442 | 535.1208 | 1026.998 | 1008.1207 | 822.7283 | 865.5442 | 535.1208 | 1026.998 | 1008.1207 | 822.7283 | 2.4629 | 2.0134 | 2.3376 | 2.3371 | 2.3401
4 | SA-17-TL | 04-SA-17-TL | 842.3943 | 510.514 | 993.4177 | 972.0875 | 796.897 | 842.3943 | 510.514 | 993.4177 | 972.0875 | 796.897 | 2.5126 | 2.0343 | 2.3385 | 2.3325 | 2.3732
4 | SA-17-TM | 04-SA-17-TM | 979.6081 | 586.4781 | 1111.3567 | 1103.0238 | 918.6208 | 979.6081 | 586.4781 | 1111.3567 | 1103.0238 | 918.6208 | 2.7443 | 2.2562 | 2.5307 | 2.7329 | 2.6217
4 | SA-18-LH | 04-SA-18-LH | 843.1489 | 515.4491 | 1033.849 | 1017.8454 | 807.0413 | 843.1489 | 515.4491 | 1033.849 | 1017.8454 | 807.0413 | 2.4775 | 1.9856 | 2.3022 | 2.3037 | 2.3359
4 | SA-18-LL | 04-SA-18-LL | 824.8274 | 500.2544 | 1010.9942 | 993.8029 | 788.3594 | 824.8274 | 500.2544 | 1010.9942 | 993.8029 | 788.3594 | 2.4891 | 1.9818 | 2.3047 | 2.3064 | 2.3424
4 | SA-18-TH | 04-SA-18-TH | 845.7543 | 523.2467 | 997.2829 | 1001.3423 | 805.6542 | 845.7543 | 523.2467 | 997.2829 | 1001.3423 | 805.6542 | 2.3546 | 1.929 | 2.2254 | 2.4017 | 2.2589
4 | SA-18-TL | 04-SA-18-TL | 880.0641 | 538.3629 | 1033.3326 | 1015.6475 | 833.3313 | 880.0641 | 538.3629 | 1033.3326 | 1015.6475 | 833.3313 | 2.5926 | 2.123 | 2.4275 | 2.4282 | 2.4578
4 | SA-18-TM | 04-SA-18-TM | 864.2993 | 531.5886 | 1028.5211 | 1009.6341 | 821.5267 | 864.2993 | 531.5886 | 1028.5211 | 1009.6341 | 821.5267 | 2.4045 | 1.959 | 2.2785 | 2.2786 | 2.2825
4 | SH-10-HH | 04-SH-10-HH | 5215.5703 | 2746.7259 | 3383.6332 | 3158.9138 | 4603.5464 | 1211.1346 | 739.6929 | 1574.6736 | 1574.61 | 1154.542 | 3.3564 | 2.7072 | 3.2814 | 3.4926 | 3.2424
4 | SH-10-HL | 04-SH-10-HL | 5293.4256 | 2783.7485 | 3451.6609 | 3209.4947 | 4672.2442 | 1248.6915 | 758.5896 | 1625.4672 | 1616.159 | 1189.2926 | 3.5583 | 2.8694 | 3.429 | 3.6671 | 3.434
4 | SH-10-HM | 04-SH-10-HM | 5131.4001 | 2721.4149 | 3388.9776 | 3120.6894 | 4535.1985 | 1240.8783 | 754.3485 | 1591.9845 | 1561.8138 | 1178.9756 | 3.5069 | 2.8452 | 3.388 | 3.3851 | 3.3761
4 | SH-10-LH | 04-SH-10-LH | 5454.7796 | 2845.6049 | 3460.055 | 3181.8676 | 4801.1109 | 1206.8823 | 737.4486 | 1567.147 | 1539.5273 | 1148.9813 | 3.2139 | 2.6379 | 3.1173 | 3.1181 | 3.1008
4 | SH-10-LL | 04-SH-10-LL | 5368.6597 | 2796.9347 | 3442.3475 | 3171.1361 | 4727.765 | 1245.9139 | 755.6506 | 1608.7659 | 1579.1124 | 1184.3115 | 3.4782 | 2.8137 | 3.3479 | 3.3558 | 3.3465
4 | SH-10-LM | 04-SH-10-LM | 5256.8019 | 2771.4654 | 3413.7607 | 3141.1193 | 4638.4085 | 1235.4464 | 752.4256 | 1592.6967 | 1559.2729 | 1174.5192 | 3.3665 | 2.7201 | 3.2635 | 3.2675 | 3.2401
4 | SH-10-MH | 04-SH-10-MH | 5406.8637 | 2816.009 | 3429.5225 | 3148.7515 | 4757.8278 | 1200.2398 | 731.1357 | 1560.335 | 1527.394 | 1142.1132 | 3.3178 | 2.7124 | 3.2119 | 3.2142 | 3.1986
4 | SH-10-ML | 04-SH-10-ML | 5085.9085 | 2669.9795 | 3343.0841 | 3082.5456 | 4488.9837 | 1237.9244 | 749.4497 | 1608.0745 | 1576.502 | 1177.1451 | 3.5842 | 2.8618 | 3.5023 | 3.5046 | 3.4456
4 | SH-10-MM | 04-SH-10-MM | 5323.2945 | 2794.4979 | 3439.0986 | 3171.4048 | 4693.8574 | 1262.4776 | 766.338 | 1609.8196 | 1585.4571 | 1198.8084 | 3.5819 | 2.9369 | 3.3872 | 3.393 | 3.4484
4 | SH-13-HH | 04-SH-13-HH | 4906.2066 | 2510.8275 | 2992.7564 | 2766.4806 | 4300.897 | 954.7179 | 581.9528 | 1247.7678 | 1241.289 | 910.0981 | 2.805 | 2.2973 | 2.754 | 2.9765 | 2.7194
4 | SH-13-HL | 04-SH-13-HL | 4342.9215 | 2237.2265 | 2740.7903 | 2531.7333 | 3816.8034 | 935.8018 | 563.7462 | 1228.452 | 1217.3599 | 891.0434 | 2.8499 | 2.2398 | 2.8005 | 2.9625 | 2.7426
4 | SH-13-HM | 04-SH-13-HM | 4447.2029 | 2304.0424 | 2806.278 | 2597.903 | 3911.1112 | 953.0307 | 578.9307 | 1240.8582 | 1231.5131 | 907.5951 | 2.8284 | 2.3129 | 2.7654 | 2.9846 | 2.7403
4 | SH-13-LH | 04-SH-13-LH | 5256.9891 | 2580.8198 | 2984.6431 | 2721.5481 | 4569.2379 | 918.7547 | 560.0456 | 1205.7671 | 1179.5298 | 875.2029 | 2.5428 | 2.0643 | 2.4926 | 2.4915 | 2.4512
4 | SH-13-LL | 04-SH-13-LL | 4569.0762 | 2319.7123 | 2762.2716 | 2530.3052 | 3998.8547 | 918.4445 | 557.6044 | 1179.6956 | 1158.6498 | 872.6709 | 2.6746 | 2.1327 | 2.6164 | 2.6109 | 2.5705
4 | SH-13-LM | 04-SH-13-LM | 4074.2378 | 2122.1497 | 2641.2696 | 2429.4801 | 3589.8375 | 956.2356 | 580.0944 | 1253.882 | 1227.2901 | 910.3445 | 2.6859 | 2.1789 | 2.6298 | 2.6295 | 2.5886
4 | SH-13-MH | 04-SH-13-MH | 4904.5656 | 2502.3842 | 2915.9839 | 2701.9039 | 4292.5182 | 897.2268 | 549.6025 | 1164.0856 | 1165.0539 | 855.4515 | 2.5379 | 2.0258 | 2.5312 | 2.694 | 2.452
4 | SH-13-ML | 04-SH-13-ML | 4724.8742 | 2383.503 | 2855.7388 | 2613.8286 | 4132.2476 | 954.3347 | 576.464 | 1246.2264 | 1220.9702 | 907.7271 | 2.8088 | 2.2562 | 2.7433 | 2.742 | 2.7024
4 | SH-13-MM | 04-SH-13-MM | 4589.3465 | 2374.2823 | 2843.0173 | 2600.3195 | 4029.7715 | 926.7575 | 561.6264 | 1200.9071 | 1176.4712 | 881.0764 | 2.7446 | 2.1991 | 2.6917 | 2.6921 | 2.6406
4 | SH-14-HH | 04-SH-14-HH | 4517.8233 | 2312.0085 | 2778.0554 | 2566.789 | 3962.0805 | 900.1031 | 547.2919 | 1178.6641 | 1171.738 | 857.9287 | 2.6935 | 2.1949 | 2.636 | 2.8413 | 2.6082
4 | SH-14-HL | 04-SH-14-HL | 4534.5466 | 2276.1061 | 2738.5303 | 2516.6313 | 3964.0589 | 893.0089 | 538.8489 | 1171.6076 | 1158.8633 | 850.2935 | 2.74 | 2.2192 | 2.6656 | 2.8617 | 2.6488
4 | SH-14-HM | 04-SH-14-HM | 4469.7059 | 2270.0063 | 2734.1355 | 2525.9433 | 3915.5801 | 896.71 | 543.5667 | 1175.9911 | 1168.0715 | 854.4828 | 2.6469 | 2.1457 | 2.572 | 2.7602 | 2.5588
4 | SH-14-MH | 04-SH-14-MH | 4786.5953 | 2362.687 | 2762.2657 | 2521.1984 | 4166.2851 | 863.2607 | 525.2009 | 1134.1753 | 1109.2266 | 822.2392 | 2.3854 | 1.9387 | 2.3346 | 2.3347 | 2.2996
4 | SH-14-ML | 04-SH-14-ML | 5043.3207 | 2427.0632 | 2772.7349 | 2532.3497 | 4367.8273 | 844.2456 | 511.6116 | 1104.1811 | 1094.039 | 804.0791 | 2.5127 | 1.9734 | 2.4718 | 2.5559 | 2.4151
4 | SH-14-MM | 04-SH-14-MM | 4409.6107 | 2212.7008 | 2654.2331 | 2427.3733 | 3853.4277 | 863.1783 | 521.5685 | 1141.4137 | 1115.8869 | 822.0743 | 2.5005 | 2.0042 | 2.4644 | 2.4634 | 2.4067
4 | SH-15-HH | 04-SH-15-HH | 5238.846 | 2536.4376 | 2871.3111 | 2617.9918 | 4539.0465 | 829.6198 | 504.949 | 1083.8155 | 1078.4241 | 790.6847 | 2.4382 | 1.9673 | 2.3607 | 2.5285 | 2.3544
4 | SH-15-HL | 04-SH-15-HL | 3897.7405 | 2001.8572 | 2453.3634 | 2266.3362 | 3423.9529 | 833.9878 | 504.1853 | 1092.2989 | 1082.1834 | 794.208 | 2.5129 | 2.0395 | 2.4754 | 2.6612 | 2.4328
4 | SH-15-HM | 04-SH-15-HM | 4016.3549 | 2040.4741 | 2470.1852 | 2278.1804 | 3519.3987 | 796.6848 | 483.8234 | 1043.9035 | 1036.6083 | 759.2433 | 2.3563 | 1.8655 | 2.3409 | 2.4623 | 2.2715
4 | SH-15-MH | 04-SH-15-MH | 4665.494 | 2267.0667 | 2600.6043 | 2368.2441 | 4046.9848 | 788.3997 | 480.3595 | 1032.0999 | 1010.5755 | 750.8256 | 2.3792 | 1.877 | 2.3426 | 2.3356 | 2.284
4 | SH-15-ML | 04-SH-15-ML | 4422.8523 | 2160.9837 | 2518.7341 | 2307.5359 | 3843.4825 | 791.5397 | 479.176 | 1039.4078 | 1027.7909 | 754.0211 | 2.3779 | 1.8657 | 2.3533 | 2.4291 | 2.2861
4 | SH-15-MM | 04-SH-15-MM | 4588.5984 | 2270.7629 | 2634.952 | 2413.9913 | 3994.4644 | 796.1108 | 483.5214 | 1036.3968 | 1029.0848 | 758.1536 | 2.3708 | 1.8793 | 2.3588 | 2.4661 | 2.2855
4 | SH-16-CH | 04-SH-16-CH | 4942.3333 | 2489.6322 | 2743.7654 | 2518.2902 | 4303.3685 | 964.8365 | 581.0391 | 1175.7916 | 1166.5015 | 911.3713 | 2.8831 | 2.2635 | 2.6257 | 2.8257 | 2.7591
4 | SH-16-CL | 04-SH-16-CL | 4660.3188 | 2343.5411 | 2637.7617 | 2421.137 | 4060.9887 | 956.2044 | 573.8633 | 1170.1166 | 1157.7437 | 903.0886 | 2.9079 | 2.2897 | 2.6574 | 2.8714 | 2.7854
4 | SH-16-LH | 04-SH-16-LH | 5158.5 | 2557.8699 | 2777.9567 | 2538.5818 | 4476.9618 | 904.1212 | 559.7537 | 1105.3058 | 1087.8613 | 856.6523 | 2.5627 | 2.0473 | 2.3929 | 2.3918 | 2.4546
4 | SH-16-LL | 04-SH-16-LL | 4890.7092 | 2385.3222 | 2684.7901 | 2462.5811 | 4241.6806 | 932.9883 | 568.1144 | 1158.6842 | 1140.6859 | 883.7379 | 2.762 | 2.1943 | 2.5827 | 2.5824 | 2.6436
4 | SH-16-LM | 04-SH-16-LM | 5237.4181 | 2578.7295 | 2825.1727 | 2584.7148 | 4542.6286 | 932.9409 | 575.1682 | 1153.8936 | 1136.1665 | 884.6164 | 2.667 | 2.1304 | 2.4918 | 2.4921 | 2.5546
4 | SH-16-TH | 04-SH-16-TH | 5884.9428 | 3001.7604 | 3028.9639 | 2774.5285 | 5112.2638 | 945.9714 | 576.0484 | 1096.2994 | 1097.182 | 890.6262 | 2.7601 | 2.1541 | 2.5321 | 2.6984 | 2.6392
4 | SH-16-TL | 04-SH-16-TL | 5946.7516 | 2990.4404 | 3083.0453 | 2812.6548 | 5159.2579 | 1016.1556 | 611.513 | 1192.2722 | 1171.0403 | 955.432 | 3.0036 | 2.4588 | 2.8035 | 2.806 | 2.8878
4 | SH-16-TM | 04-SH-16-TM | 5990.0164 | 3019.5167 | 3100.7978 | 2827.2111 | 5197.6879 | 1005.4787 | 606.0873 | 1180.5206 | 1159.7885 | 945.6532 | 2.9544 | 2.4235 | 2.7597 | 2.7616 | 2.8416
4 | SH-17-CM | 04-SH-17-CM | 4991.4668 | 2458.4811 | 2653.5588 | 2420.6408 | 4326.0975 | 902.1646 | 541.0541 | 1104.1337 | 1092.2171 | 851.9811 | 2.7493 | 2.1648 | 2.516 | 2.7166 | 2.6337
4 | SH-17-LM | 04-SH-17-LM | 4712.4705 | 2300.1086 | 2575.7834 | 2365.5781 | 4086.7002 | 884.9143 | 539.5865 | 1093.389 | 1088.065 | 838.4831 | 2.5916 | 2.104 | 2.4249 | 2.6079 | 2.4982
4 | SH-17-TH | 04-SH-17-TH | 5803.14 | 2956.4475 | 2959.5656 | 2700.2462 | 5037.8926 | 872.3668 | 535.3088 | 1034.2135 | 1031.4568 | 823.782 | 2.5042 | 2.0325 | 2.3697 | 2.5383 | 2.4156
4 | SH-17-TL | 04-SH-17-TL | 5794.5973 | 2939.9294 | 2944.1791 | 2683.9669 | 5027.2889 | 878.149 | 537.3756 | 1040.8658 | 1037.1316 | 828.9058 | 2.5626 | 2.0692 | 2.427 | 2.5918 | 2.4698
4 | SH-18-LH | 04-SH-18-LH | 5276.1816 | 2572.6584 | 2683.6526 | 2443.8918 | 4558.5509 | 824.9329 | 503.4251 | 1014.6698 | 1000.3932 | 780.8731 | 2.4651 | 1.9637 | 2.2997 | 2.2992 | 2.36
4 | SH-18-LL | 04-SH-18-LL | 4851.3058 | 2342.6455 | 2575.9163 | 2354.6806 | 4196.0717 | 845.0914 | 515.0376 | 1055.0191 | 1038.2333 | 800.985 | 2.5348 | 2.0191 | 2.3733 | 2.3738 | 2.4274
4 | SH-18-LM | 04-SH-18-LM | 5526.1219 | 2700.851 | 2774.277 | 2522.3969 | 4772.6405 | 834.4643 | 509.3188 | 1024.2617 | 1009.9238 | 789.7412 | 2.5157 | 2.0147 | 2.3456 | 2.3461 | 2.4103
4 | SH-18-TM | 04-SH-18-TM | 5741.4291 | 2919.9535 | 2855.0291 | 2591.8149 | 4977.1057 | 818.0775 | 504.2377 | 969.6635 | 952.2046 | 772.1504 | 2.4624 | 1.972 | 2.3304 | 2.3289 | 2.3619
5 | SA-10-HH | 05-SA-10-HH | 275.7985 | 121.5227 | 511.329 | 494.6119 | 230.2779 | 275.7985 | 121.5227 | 511.329 | 494.6119 | 230.2779 | 2.3881 | 1.8409 | 2.7418 | 2.7173 | 2.1944
5 | SA-10-HL | 05-SA-10-HL | 270.9298 | 118.9136 | 505.1596 | 493.0122 | 226.3698 | 270.9298 | 118.9136 | 505.1596 | 493.0122 | 226.3698 | 2.4878 | 1.9031 | 2.872 | 2.8815 | 2.2825
5 | SA-10-HM | 05-SA-10-HM | 272.9857 | 119.782 | 511.3675 | 499.5818 | 228.2539 | 272.9857 | 119.782 | 511.3675 | 499.5818 | 228.2539 | 2.4596 | 1.8834 | 2.8264 | 2.8424 | 2.2566
5 | SA-10-LH | 05-SA-10-LH | 264.4612 | 116.8835 | 502.7976 | 492.0494 | 221.9961 | 264.4612 | 116.8835 | 502.7976 | 492.0494 | 221.9961 | 2.3393 | 1.809 | 2.7176 | 2.7397 | 2.1556
5 | SA-10-LL | 05-SA-10-LL | 277.796 | 121.2991 | 521.3937 | 508.0125 | 232.0641 | 277.796 | 121.2991 | 521.3937 | 508.0125 | 232.0641 | 2.5116 | 1.9223 | 2.918 | 2.9209 | 2.3057
5 | SA-10-LM | 05-SA-10-LM | 266.5307 | 117.8685 | 505.8893 | 494.9449 | 223.6991 | 266.5307 | 117.8685 | 505.8893 | 494.9449 | 223.6991 | 2.3662 | 1.8259 | 2.7427 | 2.7616 | 2.1783
5 | SA-10-MH | 05-SA-10-MH | 270.6153 | 120.4291 | 510.0804 | 501.6127 | 227.2685 | 270.6153 | 120.4291 | 510.0804 | 501.6127 | 227.2685 | 2.323 | 1.8092 | 2.6692 | 2.7098 | 2.1442
5 | SA-10-ML | 05-SA-10-ML | 280.4493 | 122.5477 | 523.2156 | 510.3954 | 234.1204 | 280.4493 | 122.5477 | 523.2156 | 510.3954 | 234.1204 | 2.5383 | 1.9405 | 2.9337 | 2.9394 | 2.3284
5 | SA-10-MM | 05-SA-10-MM | 261.3752 | 115.7438 | 495.0785 | 477.7445 | 219.1417 | 261.3752 | 115.7438 | 495.0785 | 477.7445 | 219.1417 | 2.3225 | 1.7863 | 2.7041 | 2.6782 | 2.1351
5 | SA-13-HH | 05-SA-13-HH | 207.3156 | 91.4754 | 394.1833 | 384.7306 | 173.9341 | 207.3156 | 91.4754 | 394.1833 | 384.7306 | 173.9341 | 1.8653 | 1.4317 | 2.1439 | 2.1644 | 1.713
5 | SA-13-HL | 05-SA-13-HL | 204.2712 | 89.4603 | 386.7599 | 376.6497 | 170.973 | 204.2712 | 89.4603 | 386.7599 | 376.6497 | 170.973 | 1.8625 | 1.4234 | 2.1831 | 2.1797 | 1.7102
5 | SA-13-HM | 05-SA-13-HM | 204.9691 | 90.297 | 388.0318 | 377.6418 | 171.7565 | 204.9691 | 90.297 | 388.0318 | 377.6418 | 171.7565 | 1.8876 | 1.453 | 2.1898 | 2.1928 | 1.736
5 | SA-13-LH | 05-SA-13-LH | 204.0946 | 90.0207 | 386.92 | 373.5227 | 171.0025 | 204.0946 | 90.0207 | 386.92 | 373.5227 | 171.0025 | 1.7796 | 1.378 | 2.0595 | 2.0413 | 1.6388
5 | SA-13-LL | 05-SA-13-LL | 209.7602 | 91.7789 | 394.7801 | 381.0632 | 175.2572 | 209.7602 | 91.7789 | 394.7801 | 381.0632 | 175.2572 | 1.8883 | 1.4515 | 2.206 | 2.1853 | 1.7361
5 | SA-13-LM | 05-SA-13-LM | 214.1354 | 94.3746 | 404.3646 | 390.6614 | 179.2871 | 214.1354 | 94.3746 | 404.3646 | 390.6614 | 179.2871 | 1.8678 | 1.4441 | 2.162 | 2.1423 | 1.7192
5 | SA-13-MH | 05-SA-13-MH | 196.1431 | 87.1285 | 366.4355 | 358.4525 | 164.3732 | 196.1431 | 87.1285 | 366.4355 | 358.4525 | 164.3732 | 1.7918 | 1.3902 | 2.0751 | 2.0939 | 1.6525
5 | SA-13-ML | 05-SA-13-ML | 204.3437 | 90.157 | 388.7552 | 379.0027 | 171.4388 | 204.3437 | 90.157 | 388.7552 | 379.0027 | 171.4388 | 1.8578 | 1.4251 | 2.1749 | 2.1744 | 1.7078
5 | SA-13-MM | 05-SA-13-MM | 194.3674 | 85.0812 | 361.3317 | 353.1116 | 162.2509 | 194.3674 | 85.0812 | 361.3317 | 353.1116 | 162.2509 | 1.7908 | 1.3687 | 2.0657 | 2.0709 | 1.6424
5 | SA-14-HH | 05-SA-14-HH | 196.5376 | 86.95 | 372.508 | 363.687 | 164.9057 | 196.5376 | 86.95 | 372.508 | 363.687 | 164.9057 | 1.7863 | 1.3748 | 2.0772 | 2.0859 | 1.6432
5 | SA-14-HL | 05-SA-14-HL | 187.761 | 82.719 | 356.8184 | 347.3003 | 157.4324 | 187.761 | 82.719 | 356.8184 | 347.3003 | 157.4324 | 1.7542 | 1.346 | 2.0433 | 2.0446 | 1.6121
5 | SA-14-HM | 05-SA-14-HM | 189.2031 | 83.7014 | 360.4434 | 351.0537 | 158.8476 | 189.2031 | 83.7014 | 360.4434 | 351.0537 | 158.8476 | 1.7651 | 1.3546 | 2.0767 | 2.0799 | 1.6237
5 | SA-14-MH | 05-SA-14-MH | 203.388 | 90.0729 | 383.5925 | 370.5369 | 170.4271 | 203.388 | 90.0729 | 383.5925 | 370.5369 | 170.4271 | 1.7673 | 1.3733 | 2.0346 | 2.0177 | 1.6287
5 | SA-14-ML | 05-SA-14-ML | 192.3687 | 84.6375 | 366.7531 | 357.3565 | 161.3452 | 192.3687 | 84.6375 | 366.7531 | 357.3565 | 161.3452 | 1.7357 | 1.3342 | 2.037 | 2.0404 | 1.5972
5 | SA-14-MM | 05-SA-14-MM | 195.9186 | 86.8852 | 370.2704 | 357.5605 | 164.2645 | 195.9186 | 86.8852 | 370.2704 | 357.5605 | 164.2645 | 1.721 | 1.3319 | 1.9901 | 1.9728 | 1.5845
5 | SA-15-HH | 05-SA-15-HH | 174.3688 | 77.4704 | 327.8225 | 320.5648 | 146.2693 | 174.3688 | 77.4704 | 327.8225 | 320.5648 | 146.2693 | 1.5921 | 1.2314 | 1.8216 | 1.8361 | 1.4652
5 | SA-15-HL | 05-SA-15-HL | 170.1077 | 75.2432 | 320.8761 | 312.795 | 142.6025 | 170.1077 | 75.2432 | 320.8761 | 312.795 | 142.6025 | 1.5843 | 1.215 | 1.8262 | 1.8316 | 1.4546
5 | SA-15-HM | 05-SA-15-HM | 177.0136 | 78.5761 | 334.1941 | 327.3758 | 148.5758 | 177.0136 | 78.5761 | 334.1941 | 327.3758 | 148.5758 | 1.6015 | 1.2386 | 1.8827 | 1.8637 | 1.4762
5 | SA-15-MH | 05-SA-15-MH | 178.389 | 79.5909 | 335.7415 | 328.5189 | 149.8063 | 178.389 | 79.5909 | 335.7415 | 328.5189 | 149.8063 | 1.6162 | 1.2495 | 1.8789 | 1.8929 | 1.4892
5 | SA-15-ML | 05-SA-15-ML | 177.2719 | 77.9964 | 333.0553 | 321.8761 | 148.2583 | 177.2719 | 77.9964 | 333.0553 | 321.8761 | 148.2583 | 1.6366 | 1.2576 | 1.9129 | 1.8938 | 1.5045
5 | SA-15-MM | 05-SA-15-MM | 178.2737 | 78.6226 | 337.7676 | 329.6315 | 149.47 | 178.2737 | 78.6226 | 337.7676 | 329.6315 | 149.47 | 1.6063 | 1.2364 | 1.8792 | 1.8825 | 1.4784
5 | SA-16-CH | 05-SA-16-CH | 198.4206 | 88.9493 | 350.3537 | 346.6457 | 165.3394 | 198.4206 | 88.9493 | 350.3537 | 346.6457 | 165.3394 | 1.7353 | 1.3013 | 1.9587 | 1.9308 | 1.5774
5 | SA-16-CL | 05-SA-16-CL | 185.5417 | 83.9417 | 334.9925 | 328.1755 | 155.3115 | 185.5417 | 83.9417 | 334.9925 | 328.1755 | 155.3115 | 1.6276 | 1.2177 | 1.843 | 1.8205 | 1.4789
5 | SA-16-CM | 05-SA-16-CM | 189.9504 | 86.2286 | 343.7603 | 336.769 | 159.1736 | 189.9504 | 86.2286 | 343.7603 | 336.769 | 159.1736 | 1.6756 | 1.259 | 1.8901 | 1.8687 | 1.5242
5 | SA-16-LH | 05-SA-16-LH | 181.9781 | 82.3808 | 321.5716 | 321.802 | 152.0959 | 181.9781 | 82.3808 | 321.5716 | 321.802 | 152.0959 | 1.4705 | 1.1232 | 1.6809 | 1.6491 | 1.3461
5 | SA-16-LL | 05-SA-16-LL | 187.8564 | 84.6217 | 334.7072 | 332.2539 | 156.9425 | 187.8564 | 84.6217 | 334.7072 | 332.2539 | 156.9425 | 1.5617 | 1.1839 | 1.7853 | 1.7436 | 1.4257
5 | SA-16-LM | 05-SA-16-LM | 189.9486 | 85.6096 | 340.9103 | 338.4646 | 158.8813 | 189.9486 | 85.6096 | 340.9103 | 338.4646 | 158.8813 | 1.5831 | 1.2062 | 1.8094 | 1.7784 | 1.448
5 | SA-16-NM | 05-SA-16-NM | 186.7001 | 82.9879 | 332.127 | 328.2553 | 155.4503 | 186.7001 | 82.9879 | 332.127 | 328.2553 | 155.4503 | 1.4894 | 1.1207 | 1.7259 | 1.652 | 1.3569
5 | SA-16-TH | 05-SA-16-TH | 195.3423 | 88.6962 | 322.8823 | 322.5113 | 161.8037 | 195.3423 | 88.6962 | 322.8823 | 322.5113 | 161.8037 | 1.6228 | 1.2267 | 1.8353 | 1.7919 | 1.4787
5 | SA-16-TL | 05-SA-16-TL | 186.0584 | 82.2646 | 306.1813 | 304.4797 | 153.0942 | 186.0584 | 82.2646 | 306.1813 | 304.4797 | 153.0942 | 1.5639 | 1.1679 | 1.7572 | 1.7041 | 1.4182
5 | SA-17-CH | 05-SA-17-CH | 181.5715 | 81.8536 | 324.2837 | 320.6375 | 151.7279 | 181.5715 | 81.8536 | 324.2837 | 320.6375 | 151.7279 | 1.5969 | 1.1962 | 1.8219 | 1.7855 | 1.4521
5 | SA-17-CL | 05-SA-17-CL | 181.465 | 81.576 | 323.7203 | 320.4162 | 151.5332 | 181.465 | 81.576 | 323.7203 | 320.4162 | 151.5332 | 1.5979 | 1.1933 | 1.8352 | 1.7894 | 1.4521
5 | SA-17-CM | 05-SA-17-CM | 184.0176 | 82.2458 | 325.4023 | 321.5935 | 153.2605 | 184.0176 | 82.2458 | 325.4023 | 321.5935 | 153.2605 | 1.6146 | 1.2067 | 1.8389 | 1.797 | 1.4667
5 | SA-17-LH | 05-SA-17-LH | 172.2424 | 78.3827 | 309.2919 | 308.2903 | 144.4221 | 172.2424 | 78.3827 | 309.2919 | 308.2903 | 144.4221 | 1.4343 | 1.0938 | 1.6534 | 1.6202 | 1.3131
5 | SA-17-LL | 05-SA-17-LL | 179.0419 | 79.5114 | 317.7495 | 314.3302 | 149.0026 | 179.0419 | 79.5114 | 317.7495 | 314.3302 | 149.0026 | 1.5076 | 1.1366 | 1.7057 | 1.6744 | 1.3729
5 | SA-17-LM | 05-SA-17-LM | 182.4923 | 80.5479 | 324.0712 | 321.3106 | 151.7152 | 182.4923 | 80.5479 | 324.0712 | 321.3106 | 151.7152 | 1.5239 | 1.1519 | 1.7147 | 1.6914 | 1.3886
5 | SA-17-TH | 05-SA-17-TH | 165.4602 | 74.8758 | 276.007 | 275.2144 | 137.1104 | 165.4602 | 74.8758 | 276.007 | 275.2144 | 137.1104 | 1.4372 | 1.089 | 1.6288 | 1.6039 | 1.3113
5 | SA-17-TL | 05-SA-17-TL | 148.5531 | 68.0444 | 252.123 | 250.4178 | 123.692 | 148.5531 | 68.0444 | 252.123 | 250.4178 | 123.692 | 1.3458 | 1.0032 | 1.585 | 1.5173 | 1.224
5 | SA-17-TM | 05-SA-17-TM | 186.3257 | 81.8299 | 298.1938 | 294.1346 | 152.4313 | 186.3257 | 81.8299 | 298.1938 | 294.1346 | 152.4313 | 1.5377 | 1.1537 | 1.6788 | 1.649 | 1.3939
5 | SA-18-LH | 05-SA-18-LH | 169.8832 | 76.4882 | 300.2676 | 297.7332 | 141.734 | 169.8832 | 76.4882 | 300.2676 | 297.7332 | 141.734 | 1.4033 | 1.0656 | 1.5866 | 1.5606 | 1.281
5 | SA-18-LL | 05-SA-18-LL | 163.5691 | 73.2998 | 290.6758 | 288.5546 | 136.4484 | 163.5691 | 73.2998 | 290.6758 | 288.5546 | 136.4484 | 1.382 | 1.0461 | 1.5942 | 1.553 | 1.2619
5 | SA-18-TH | 05-SA-18-TH | 163.0096 | 73.5173 | 269.888 | 270.2062 | 134.8765 | 163.0096 | 73.5173 | 269.888 | 270.2062 | 134.8765 | 1.3627 | 1.0342 | 1.516 | 1.5015 | 1.2424
5 | SA-18-TL | 05-SA-18-TL | 164.7647 | 73.9454 | 273.7903 | 272.2231 | 136.1902 | 164.7647 | 73.9454 | 273.7903 | 272.2231 | 136.1902 | 1.4213 | 1.0698 | 1.6046 | 1.571 | 1.2932
5 | SA-18-TM | 05-SA-18-TM | 167.1957 | 76.0247 | 283.2282 | 281.9745 | 138.9778 | 167.1957 | 76.0247 | 283.2282 | 281.9745 | 138.9778 | 1.4204 | 1.0835 | 1.6056 | 1.5884 | 1.2988
5 | SH-10-HH | 05-SH-10-HH | 3687.9698 | 1667.2914 | 1831.3238 | 1595.6396 | 2903.2257 | 266.4205 | 117.3693 | 502.637 | 492.7583 | 279.3062 | 2.3445 | 1.8076 | 2.6692 | 2.6977 | 2.2947
5 | SH-10-HL | 05-SH-10-HL | 3733.7239 | 1683.2127 | 1856.426 | 1611.7017 | 2938.4028 | 272.8591 | 119.8045 | 515.4209 | 503.8444 | 286.0224 | 2.4452 | 1.8769 | 2.7977 | 2.8122 | 2.3934
5 | SH-10-HM | 05-SH-10-HM | 3582.1583 | 1634.4523 | 1819.5601 | 1582.3619 | 2830.3672 | 269.0926 | 118.7749 | 502.8116 | 491.9934 | 281.1968 | 2.3957 | 1.8491 | 2.7568 | 2.7783 | 2.3504
5 | SH-10-LH | 05-SH-10-LH | 3898.7858 | 1751.8457 | 1896.991 | 1638.9278 | 3059.1426 | 272.1276 | 120.5592 | 502.7926 | 493.1696 | 283.451 | 2.2919 | 1.7875 | 2.6326 | 2.604 | 2.2492
5 | SH-10-LL | 05-SH-10-LL | 3757.6657 | 1685.2347 | 1853.7848 | 1610.9785 | 2952.8308 | 273.4812 | 120.0109 | 515.477 | 504.321 | 286.4708 | 2.4306 | 1.8777 | 2.8133 | 2.8257 | 2.3876
5 | SH-10-LM | 05-SH-10-LM | 3680.5598 | 1672.4569 | 1844.844 | 1608.6691 | 2902.3747 | 273.1099 | 120.0591 | 512.1559 | 502.7127 | 285.7129 | 2.3621 | 1.836 | 2.7205 | 2.746 | 2.3208
5 | SH-10-MH | 05-SH-10-MH | 3846.3529 | 1726.6774 | 1876.2965 | 1633.0584 | 3019.1181 | 266.3648 | 117.7757 | 503.179 | 493.9645 | 279.4919 | 2.318 | 1.798 | 2.6684 | 2.6995 | 2.2768
5 | SH-10-ML | 05-SH-10-ML | 3523.9858 | 1589.7833 | 1774.9174 | 1541.8128 | 2777.7714 | 270.1816 | 118.3971 | 509.3447 | 496.4586 | 282.9067 | 2.4746 | 1.898 | 2.8632 | 2.8658 | 2.4273
5 | SH-10-MM | 05-SH-10-MM | 3726.9711 | 1681.931 | 1844.8153 | 1587.6757 | 2931.2838 | 271.2317 | 119.5337 | 504.66 | 487.7283 | 282.6989 | 2.4125 | 1.8551 | 2.7744 | 2.7499 | 2.3629
5 | SH-13-HH | 05-SH-13-HH | 3548.9317 | 1575.5898 | 1665.1967 | 1439.3209 | 2769.4587 | 206.6272 | 91.4847 | 386.3526 | 378.0052 | 216.0277 | 1.8919 | 1.4577 | 2.1754 | 2.1976 | 1.8556
5 | SH-13-HL | 05-SH-13-HL | 3092.9895 | 1375.7733 | 1491.4934 | 1284.3878 | 2421.3025 | 200.7774 | 88.5244 | 380.6529 | 373.2008 | 210.8542 | 1.854 | 1.4238 | 2.1827 | 2.1598 | 1.8248
5 | SH-13-HM | 05-SH-13-HM | 3166.3955 | 1418.2668 | 1530.2235 | 1324.2647 | 2481.7477 | 205.0204 | 90.0172 | 383.6635 | 375.3417 | 214.2471 | 1.8767 | 1.4423 | 2.1667 | 2.1806 | 1.8411
5 | SH-13-LH | 05-SH-13-LH | 3879.3727 | 1630.0656 | 1688.4376 | 1443.262 | 2983.2242 | 206.4899 | 91.8304 | 390.8085 | 377.2704 | 216.6094 | 1.8029 | 1.3982 | 2.0833 | 2.0657 | 1.7702
5 | SH-13-LL | 05-SH-13-LL | 3268.4903 | 1438.8135 | 1522.6207 | 1313.1445 | 2545.8997 | 196.2388 | 86.3377 | 366.2434 | 357.3087 | 204.8746 | 1.7881 | 1.3724 | 2.0487 | 2.0585 | 1.7507
5 | SH-13-LM | 05-SH-13-LM | 2872.9662 | 1286.8965 | 1429.0796 | 1230.8202 | 2258.9035 | 215.52 | 94.7112 | 408.0739 | 393.6939 | 225.8654 | 1.894 | 1.463 | 2.198 | 2.1774 | 1.8601
5 | SH-13-MH | 05-SH-13-MH | 3577.8653 | 1588.8597 | 1647.022 | 1425.7567 | 2786.4448 | 194.8346 | 86.8334 | 363.2949 | 356.3718 | 203.6733 | 1.7463 | 1.346 | 1.959 | 2.0004 | 1.7046
5 | SH-13-ML | 05-SH-13-ML | 3414.0799 | 1483.5922 | 1578.4349 | 1352.0819 | 2652.6314 | 210.8846 | 92.862 | 398.4174 | 385.197 | 220.9215 | 1.9112 | 1.4698 | 2.237 | 2.2159 | 1.8792
5 | SH-13-MM | 05-SH-13-MM | 3309.1939 | 1483.3929 | 1573.3075 | 1355.893 | 2588.918 | 197.5028 | 87.5347 | 370.904 | 362.1332 | 206.7733 | 1.8316 | 1.4154 | 2.1362 | 2.1478 | 1.8025
5 | SH-14-HH | 05-SH-14-HH | 3248.3643 | 1441.7462 | 1533.4934 | 1323.6787 | 2536.4349 | 193.4333 | 85.4132 | 362.8845 | 354.7082 | 202.3949 | 1.793 | 1.379 | 2.0713 | 2.0864 | 1.7595
5 | SH-14-HL | 05-SH-14-HL | 3242.5125 | 1413.4 | 1503.6385 | 1291.6309 | 2521.2387 | 190.6861 | 83.9148 | 361.4155 | 351.4817 | 200.0661 | 1.7856 | 1.3679 | 2.0878 | 2.0855 | 1.7551
5 | SH-14-HM | 05-SH-14-HM | 3195.7229 | 1408.5056 | 1504.0248 | 1298.979 | 2492.4569 | 194.1659 | 85.437 | 365.8774 | 357.1583 | 203.3795 | 1.767 | 1.3593 | 2.0414 | 2.053 | 1.734
5 | SH-14-MH | 05-SH-14-MH | 3507.5697 | 1484.6952 | 1554.2797 | 1330.9272 | 2704.7218 | 193.5364 | 85.5618 | 367.3791 | 355.0422 | 203.1366 | 1.6833 | 1.304 | 1.9458 | 1.9292 | 1.6526
5 | SH-14-ML | 05-SH-14-ML | 3670.6041 | 1535.2175 | 1567.9427 | 1341.9357 | 2815.8852 | 186.0003 | 81.6794 | 354.0048 | 345.3709 | 195.4416 | 1.6855 | 1.2861 | 1.9708 | 1.9708 | 1.6557
5 | SH-14-MM | 05-SH-14-MM | 3186.8772 | 1379.4932 | 1469.5798 | 1259.2193 | 2474.3034 | 190.7293 | 83.9086 | 364.4776 | 351.9284 | 200.5432 | 1.7085 | 1.314 | 1.997 | 1.9789 | 1.6795
5 | SH-15-HH | 05-SH-15-HH | 3868.248 | 1620.5431 | 1638.7313 | 1397.5606 | 2965.3473 | 178.1506 | 79.055 | 335.7414 | 328.0115 | 186.7645 | 1.6039 | 1.236 | 1.8432 | 1.8577 | 1.5727
5 | SH-15-HL | 05-SH-15-HL | 2765.4716 | 1230.0811 | 1333.8758 | 1150.7866 | 2165.0674 | 179.3554 | 78.687 | 338.2554 | 329.6015 | 187.8427 | 1.6616 | 1.2741 | 1.9379 | 1.9416 | 1.6328
5 | SH-15-HM | 05-SH-15-HM | 2877.9716 | 1271.4139 | 1365.9699 | 1177.7116 | 2247.246 | 171.7307 | 76.2494 | 323.997 | 316.2827 | 180.0975 | 1.5776 | 1.2109 | 1.8044 | 1.8193 | 1.5443
5 | SH-15-MH | 05-SH-15-MH | 3457.7362 | 1448.3257 | 1476.4036 | 1266.4322 | 2653.058 | 172.6957 | 79.2407 | 327.7865 | 319.5088 | 181.9927 | 1.5926 | 1.2272 | 1.8655 | 1.8715 | 1.5679
5 | SH-15-ML | 05-SH-15-ML | 3191.6396 | 1357.6804 | 1408.5195 | 1208.563 | 2461.5801 | 173.1927 | 75.7172 | 330.543 | 321.8949 | 182.0565 | 1.5783 | 1.2051 | 1.8482 | 1.8461 | 1.551
5 | SH-15-MM | 05-SH-15-MM | 3331.9084 | 1439.3013 | 1482.0479 | 1269.8169 | 2576.3869 | 169.1508 | 75.3624 | 318.2998 | 310.7996 | 177.2941 | 1.5767 | 1.2143 | 1.8073 | 1.8127 | 1.5446
5 | SH-16-CH | 05-SH-16-CH | 3571.1145 | 1535.6115 | 1477.7963 | 1269.7186 | 2739.9334 | 194.5678 | 87.6095 | 345.9948 | 338.7634 | 200.3962 | 1.6732 | 1.2573 | 1.8827 | 1.8608 | 1.6246
5 | SH-16-CL | 05-SH-16-CL | 3333.0825 | 1426.7287 | 1399.6956 | 1203.9481 | 2559.7126 | 191.5828 | 85.9868 | 341.7033 | 334.4047 | 197.4467 | 1.694 | 1.268 | 1.9059 | 1.883 | 1.6437
5 | SH-16-LH | 05-SH-16-LH | 3783.0866 | 1601.8096 | 1546.5684 | 1333.7466 | 2894.1338 | 183.0854 | 83.0344 | 321.7951 | 321.8834 | 188.3115 | 1.4686 | 1.1271 | 1.6467 | 1.6402 | 1.4304
5 | SH-16-LL | 05-SH-16-LL | 3549.4457 | 1459.7998 | 1450.8099 | 1246.205 | 2706.0904 | 190.1778 | 85.496 | 339.8972 | 337.2169 | 196.3788 | 1.5848 | 1.2049 | 1.8219 | 1.7827 | 1.5481
5 | SH-16-LM | 05-SH-16-LM | 3862.6385 | 1606.772 | 1561.4063 | 1345.1387 | 2945.6912 | 190.0232 | 87.0833 | 339.6732 | 340.0958 | 196.7247 | 1.5356 | 1.1816 | 1.7572 | 1.7319 | 1.5021
5 | SH-16-TH | 05-SH-16-TH | 4378.3835 | 1934.3228 | 1699.8081 | 1449.7399 | 3349.2097 | 176.5937 | 80.5342 | 291.9583 | 291.762 | 178.2371 | 1.4911 | 1.1282 | 1.6812 | 1.6459 | 1.4493
5 | SH-16-TL | 05-SH-16-TL | 4360.5555 | 1897.4389 | 1691.2751 | 1434.6368 | 3328.8302 | 190.7497 | 84.3543 | 319.8596 | 315.5892 | 192.627 | 1.6734 | 1.2525 | 1.9046 | 1.8557 | 1.6266
5 | SH-16-TM | 05-SH-16-TM | 4410.5715 | 1923.7545 | 1709.8265 | 1452.0319 | 3367.8911 | 188.5377 | 83.0471 | 316.4054 | 311.9864 | 190.363 | 1.6548 | 1.2412 | 1.8714 | 1.832 | 1.6072
5 | SH-17-CM | 05-SH-17-CM | 3672.2859 | 1541.9639 | 1443.4023 | 1232.7695 | 2795.5484 | 180.813 | 81.2213 | 321.9416 | 315.151 | 186.2619 | 1.5987 | 1.198 | 1.8004 | 1.7796 | 1.5518
5 | SH-17-LM | 05-SH-17-LM | 3386.3644 | 1412.8356 | 1395.6943 | 1199.0776 | 2588.0781 | 178.1717 | 78.9932 | 315.5405 | 312.9766 | 183.2003 | 1.4938 | 1.1315 | 1.6678 | 1.6576 | 1.4503
5 | SH-17-TH | 05-SH-17-TH | 4354.6373 | 1926.0215 | 1675.5157 | 1425.7679 | 3328.6098 | 164.9171 | 74.5412 | 276.7634 | 275.6782 | 167.0442 | 1.44 | 1.0863 | 1.622 | 1.5986 | 1.3992
5 | SH-17-TL | 05-SH-17-TL | 4336.029 | 1909.0957 | 1659.9527 | 1409.9773 | 3310.9175 | 165.4944 | 74.2237 | 277.4182 | 276.1766 | 167.4412 | 1.4532 | 1.0933 | 1.6462 | 1.6141 | 1.4127
5 | SH-18-LH | 05-SH-18-LH | 3916.8295 | 1631.7054 | 1503.5887 | 1273.1645 | 2971.9428 | 166.1758 | 73.8089 | 294.4316 | 292.2145 | 170.9279 | 1.4191 | 1.0717 | 1.6134 | 1.5874 | 1.3818
5 | SH-18-LL | 05-SH-18-LL | 3572.1359 | 1454.0232 | 1413.6649 | 1206.9597 | 2711.4291 | 171.6851 | 77.92 | 308.8628 | 305.9694 | 177.7954 | 1.4779 | 1.1233 | 1.6921 | 1.6638 | 1.4427
5 | SH-18-LM | 05-SH-18-LM | 4125.8605 | 1725.8444 | 1560.9756 | 1315.614 | 3127.5867 | 166.2875 | 73.6856 | 294.5609 | 291.8983 | 170.9723 | 1.4088 | 1.0635 | 1.6023 | 1.569 | 1.3714
5 | SH-18-TM | 05-SH-18-TM | 4320.4577 | 1919.7789 | 1625.4216 | 1380.6624 | 3297.5166 | 153.0734 | 70.6279 | 257.2174 | 257.1074 | 155.4545 | 1.3848 | 1.0407 | 1.6195 | 1.5966 | 1.3559
6 | SA-10-HH | 06-SA-10-HH | 780.6359 | 527.1028 | 1142.4181 | 1137.9087 | 791.333 | 780.6359 | 527.1028 | 1142.4181 | 1137.9087 | 791.333 | 1.7951 | 1.5735 | 2.2554 | 2.3539 | 1.8558
6 | SA-10-HL | 06-SA-10-HL | 763.8354 | 517.3845 | 1135.7464 | 1125.9052 | 778.3939 | 763.8354 | 517.3845 | 1135.7464 | 1125.9052 | 778.3939 | 1.8221 | 1.6041 | 2.3181 | 2.4631 | 1.8999
6 | SA-10-HM | 06-SA-10-HM | 769.6439 | 520.0555 | 1143.7759 | 1136.8208 | 784.2297 | 769.6439 | 520.0555 | 1143.7759 | 1136.8208 | 784.2297 | 1.8241 | 1.6055 | 2.3287 | 2.4743 | 1.9039
6 | SA-10-LH | 06-SA-10-LH | 743.9819 | 502.1234 | 1116.0381 | 1113.6298 | 761.1321 | 743.9819 | 502.1234 | 1116.0381 | 1113.6298 | 761.1321 | 1.7466 | 1.5313 | 2.2502 | 2.3929 | 1.8267
6 | SA-10-LL | 06-SA-10-LL | 785.1407 | 534.2671 | 1180.6284 | 1164.89 | 803.257 | 785.1407 | 534.2671 | 1180.6284 | 1164.89 | 803.257 | 1.8806 | 1.7345 | 2.4391 | 2.5297 | 1.9876
6 | SA-10-LM | 06-SA-10-LM | 754.7057 | 509.4271 | 1131.7981 | 1127.2232 | 771.7149 | 754.7057 | 509.4271 | 1131.7981 | 1127.2232 | 771.7149 | 1.7798 | 1.5638 | 2.2862 | 2.4306 | 1.8607
6 | SA-10-MH | 06-SA-10-MH | 759.2968 | 509.7908 | 1119.5424 | 1122.5468 | 772.0085 | 759.2968 | 509.7908 | 1119.5424 | 1122.5468 | 772.0085 | 1.7311 | 1.5102 | 2.1981 | 2.3485 | 1.8016
6 | SA-10-ML | 06-SA-10-ML | 789.6776 | 535.2077 | 1179.2403 | 1163.8567 | 805.2782 | 789.6776 | 535.2077 | 1179.2403 | 1163.8567 | 805.2782 | 1.8967 | 1.6762 | 2.4336 | 2.5339 | 1.9769
6 | SA-10-MM | 06-SA-10-MM | 736.7782 | 498.8094 | 1100.709 | 1090.9254 | 751.9833 | 736.7782 | 498.8094 | 1100.709 | 1090.9254 | 751.9833 | 1.7256 | 1.5632 | 2.26 | 2.3224 | 1.8172
6 | SA-13-HH | 06-SA-13-HH | 584.4557 | 400.0495 | 878.86 | 876.1544 | 600.0489 | 584.4557 | 400.0495 | 878.86 | 876.1544 | 600.0489 | 1.3643 | 1.259 | 1.757 | 1.8642 | 1.4454
6 | SA-13-HL | 06-SA-13-HL | 574.6102 | 388.1917 | 869.6706 | 857.7182 | 588.3246 | 574.6102 | 388.1917 | 869.6706 | 857.7182 | 588.3246 | 1.3859 | 1.2755 | 1.8409 | 1.8875 | 1.4715
6 | SA-13-HM | 06-SA-13-HM | 579.8595 | 394.524 | 890.8877 | 868.9357 | 596.3147 | 579.8595 | 394.524 | 890.8877 | 868.9357 | 596.3147 | 1.3808 | 1.2627 | 1.8914 | 1.8655 | 1.4666
6 | SA-13-LH | 06-SA-13-LH | 574.0382 | 386.1253 | 862.0459 | 842.8407 | 584.435 | 574.0382 | 386.1253 | 862.0459 | 842.8407 | 584.435 | 1.3336 | 1.1575 | 1.688 | 1.665 | 1.3635
6 | SA-13-LL | 06-SA-13-LL | 593.3608 | 400.3068 | 888.141 | 879.3669 | 605.4533 | 593.3608 | 400.3068 | 888.141 | 879.3669 | 605.4533 | 1.4044 | 1.2408 | 1.7981 | 1.8799 | 1.4639
6 | SA-13-LM | 06-SA-13-LM | 599.4992 | 403.3798 | 895.0927 | 878.7965 | 609.693 | 599.4992 | 403.3798 | 895.0927 | 878.7965 | 609.693 | 1.3915 | 1.2185 | 1.7862 | 1.7602 | 1.4318
6 | SA-13-MH | 06-SA-13-MH | 555.1346 | 374.6688 | 819.3755 | 817.0632 | 564.5479 | 555.1346 | 374.6688 | 819.3755 | 817.0632 | 564.5479 | 1.2979 | 1.1424 | 1.6357 | 1.745 | 1.3503
6 | SA-13-ML | 06-SA-13-ML | 576.6677 | 391.0164 | 875.357 | 863.5807 | 591.5418 | 576.6677 | 391.0164 | 875.357 | 863.5807 | 591.5418 | 1.3754 | 1.2503 | 1.8083 | 1.8656 | 1.4527
6 | SA-13-MM | 06-SA-13-MM | 555.8146 | 374.8013 | 822.0675 | 816.9999 | 565.1329 | 555.8146 | 374.8013 | 822.0675 | 816.9999 | 565.1329 | 1.32 | 1.1681 | 1.6675 | 1.7699 | 1.3749
6 | SA-14-HH | 06-SA-14-HH | 552.6216 | 374.0185 | 830.9705 | 826.6665 | 565.7874 | 552.6216 | 374.0185 | 830.9705 | 826.6665 | 565.7874 | 1.2937 | 1.1325 | 1.6743 | 1.7678 | 1.3525
6 | SA-14-HL | 06-SA-14-HL | 529.0077 | 358.0712 | 804.6287 | 794.6308 | 542.9825 | 529.0077 | 358.0712 | 804.6287 | 794.6308 | 542.9825 | 1.2685 | 1.1118 | 1.6692 | 1.727 | 1.3282
6 | SA-14-HM | 06-SA-14-HM | 528.1618 | 357.6929 | 803.3452 | 793.3188 | 542.168 | 528.1618 | 357.6929 | 803.3452 | 793.3188 | 542.168 | 1.27 | 1.1511 | 1.6764 | 1.7304 | 1.3421
6 | SA-14-MH | 06-SA-14-MH | 569.3162 | 382.933 | 845.3209 | 831.3552 | 578.0237 | 569.3162 | 382.933 | 845.3209 | 831.3552 | 578.0237 | 1.3036 | 1.1313 | 1.6503 | 1.6306 | 1.3332
6 | SA-14-ML | 06-SA-14-ML | 540.4045 | 365.484 | 818.9999 | 812.7731 | 554.4685 | 540.4045 | 365.484 | 818.9999 | 812.7731 | 554.4685 | 1.2869 | 1.1678 | 1.693 | 1.7498 | 1.3593
6 | SA-14-MM | 06-SA-14-MM | 548.8673 | 369.9001 | 819.3921 | 805.6639 | 558.5388 | 548.8673 | 369.9001 | 819.3921 | 805.6639 | 558.5388 | 1.2634 | 1.1024 | 1.6102 | 1.6225 | 1.3014
6 | SA-15-HH | 06-SA-15-HH | 489.4803 | 336.1294 | 748.0253 | 729.409 | 503.3208 | 489.4803 | 336.1294 | 748.0253 | 729.409 | 503.3208 | 1.1383 | 1.0588 | 1.5465 | 1.5234 | 1.2111
6 | SA-15-HL | 06-SA-15-HL | 482.3761 | 329.7332 | 725.4476 | 719.2074 | 494.5144 | 482.3761 | 329.7332 | 725.4476 | 719.2074 | 494.5144 | 1.1422 | 1.058 | 1.4757 | 1.5561 | 1.2111
6 | SA-15-HM | 06-SA-15-HM | 499.1075 | 339.881 | 764.944 | 745.607 | 512.8312 | 499.1075 | 339.881 | 764.944 | 745.607 | 512.8312 | 1.1674 | 1.0481 | 1.5962 | 1.5728 | 1.2331
6 | SA-15-MH | 06-SA-15-MH | 495.4293 | 333.928 | 742.3066 | 736.9348 | 505.9163 | 495.4293 | 333.928 | 742.3066 | 736.9348 | 505.9163 | 1.1558 | 1.016 | 1.5133 | 1.5604 | 1.2084
6 | SA-15-ML | 06-SA-15-ML | 503.4267 | 339.6396 | 751.2069 | 744.8793 | 513.2866 | 503.4267 | 339.6396 | 751.2069 | 744.8793 | 513.2866 | 1.1965 | 1.0544 | 1.5381 | 1.6263 | 1.2508
6 | SA-15-MM | 06-SA-15-MM | 502.3469 | 338.8634 | 758.5991 | 750.1792 | 514.0717 | 502.3469 | 338.8634 | 758.5991 | 750.1792 | 514.0717 | 1.1936 | 1.0918 | 1.5688 | 1.6178 | 1.2625
6 | SA-16-CH | 06-SA-16-CH | 569.1568 | 382.3578 | 825.4126 | 809.7414 | 572.5947 | 569.1568 | 382.3578 | 825.4126 | 809.7414 | 572.5947 | 1.2853 | 1.1598 | 1.7036 | 1.6833 | 1.3469
6 | SA-16-CL | 06-SA-16-CL | 533.217 | 361.1586 | 778.2239 | 763.2975 | 538.5248 | 533.217 | 361.1586 | 778.2239 | 763.2975 | 538.5248 | 1.2167 | 1.0992 | 1.6269 | 1.6076 | 1.279
6 | SA-16-CM | 06-SA-16-CM | 544.9962 | 367.8354 | 798.7007 | 783.7333 | 550.877 | 544.9962 | 367.8354 | 798.7007 | 783.7333 | 550.877 | 1.2362 | 1.1176 | 1.6482 | 1.6273 | 1.2983
6 | SA-16-LH | 06-SA-16-LH | 534.1956 | 357.0844 | 744.5222 | 743.8929 | 531.5788 | 534.1956 | 357.0844 | 744.5222 | 743.8929 | 531.5788 | 1.1762 | 1.0217 | 1.4633 | 1.4893 | 1.2036
6 | SA-16-LL | 06-SA-16-LL | 548.7374 | 368.9399 | 776.3422 | 774.0583 | 549.3088 | 548.7374 | 368.9399 | 776.3422 | 774.0583 | 549.3088 | 1.2213 | 1.0607 | 1.5368 | 1.5589 | 1.2532
6 | SA-16-LM | 06-SA-16-LM | 552.1593 | 370.0138 | 784.7763 | 783.941 | 553.4695 | 552.1593 | 370.0138 | 784.7763 | 783.941 | 553.4695 | 1.2393 | 1.0698 | 1.5501 | 1.5832 | 1.269
6 | SA-16-NM | 06-SA-16-NM | 541.3458 | 363.2704 | 785.8112 | 773.662 | 545.0958 | 541.3458 | 363.2704 | 785.8112 | 773.662 | 545.0958 | 1.2173 | 1.0662 | 1.5629 | 1.6184 | 1.2647
6 | SA-16-TH | 06-SA-16-TH | 555.8074 | 369.5721 | 746.8756 | 737.1538 | 544.2273 | 555.8074 | 369.5721 | 746.8756 | 737.1538 | 544.2273 | 1.1718 | 1.0314 | 1.4334 | 1.4673 | 1.1984
6 | SA-16-TL | 06-SA-16-TL | 544.1263 | 366.7629 | 739.4332 | 722.7654 | 535.2548 | 544.1263 | 366.7629 | 739.4332 | 722.7654 | 535.2548 | 1.1834 | 1.0722 | 1.4785 | 1.5049 | 1.2262
6 | SA-17-CH | 06-SA-17-CH | 520.0349 | 353.242 | 761.5668 | 747.2115 | 526.1919 | 520.0349 | 353.242 | 761.5668 | 747.2115 | 526.1919 | 1.1891 | 1.0752 | 1.587 | 1.5681 | 1.2495
6 | SA-17-CL | 06-SA-17-CL | 519.4228 | 353.0407 | 762.1667 | 747.4972 | 525.9573 | 519.4228 | 353.0407 | 762.1667 | 747.4972 | 525.9573 | 1.196 | 1.0816 | 1.6025 | 1.5846 | 1.2585
6 | SA-17-CM | 06-SA-17-CM | 527.0694 | 355.2594 | 768.472 | 752.9773 | 531.4758 | 527.0694 | 355.2594 | 768.472 | 752.9773 | 531.4758 | 1.2266 | 1.0865 | 1.6044 | 1.5864 | 1.2741
6 | SA-17-LH | 06-SA-17-LH | 503.5036 | 338.3803 | 712.4332 | 711.3487 | 504.1596 | 503.5036 | 338.3803 | 712.4332 | 711.3487 | 504.1596 | 1.1176 | 0.9731 | 1.4108 | 1.4346 | 1.1492
6 | SA-17-LL | 06-SA-17-LL | 520.562 | 350.9433 | 738.6576 | 733.1671 | 521.4223 | 520.562 | 350.9433 | 738.6576 | 733.1671 | 521.4223 | 1.1507 | 1.0269 | 1.4577 | 1.4779 | 1.1916
6 | SA-17-LM | 06-SA-17-LM | 525.7025 | 354.262 | 749.1759 | 746.5519 | 527.7718 | 525.7025 | 354.262 | 749.1759 | 746.5519 | 527.7718 | 1.1691 | 1.0127 | 1.46 | 1.4913 | 1.1977
6 | SA-17-TH | 06-SA-17-TH | 469.5445 | 314.8492 | 636.7772 | 631.1082 | 462.4014 | 469.5445 | 314.8492 | 636.7772 | 631.1082 | 462.4014 | 0.99943 | 0.89097 | 1.2375 | 1.2701 | 1.0299
6 | SA-17-TL | 06-SA-17-TL | 445.6977 | 302.695 | 627.7693 | 609.2246 | 443.8382 | 445.6977 | 302.695 | 627.7693 | 609.2246 | 443.8382 | 1.034 | 0.92302 | 1.2826 | 1.3195 | 1.067
6 | SA-17-TM | 06-SA-17-TM | 540.9916 | 357.5709 | 711.6629 | 698.2048 | 524.6633 | 540.9916 | 357.5709 | 711.6629 | 698.2048 | 524.6633 | 1.2205 | 1.0303 | 1.3977 | 1.428 | 1.2104
6 | SA-18-LH | 06-SA-18-LH | 493.0836 | 330.0523 | 691.8824 | 691.8013 | 492.0344 | 493.0836 | 330.0523 | 691.8824 | 691.8013 | 492.0344 | 1.0923 | 0.94492 | 1.358 | 1.3831 | 1.1165
6 | SA-18-LL | 06-SA-18-LL | 478.004 | 321.6208 | 679.0269 | 675.2699 | 478.9843 | 478.004 | 321.6208 | 679.0269 | 675.2699 | 478.9843 | 1.0869 | 0.97065 | 1.3684 | 1.3931 | 1.1245
6 | SA-18-TH | 06-SA-18-TH | 461.2308 | 307.9331 | 621.5725 | 617.7705 | 453.1021 | 461.2308 | 307.9331 | 621.5725 | 617.7705 | 453.1021 | 0.97561 | 0.85081 | 1.1817 | 1.209 | 0.99233
6 | SA-18-TL | 06-SA-18-TL | 471.5273 | 315.8617 | 643.428 | 632.829 | 464.481 | 471.5273 | 315.8617 | 643.428 | 632.829 | 464.481 | 1.0243 | 0.90454 | 1.254 | 1.2846 | 1.0489
6 | SA-18-TM | 06-SA-18-TM | 477.7111 | 319.4782 | 648.103 | 643.8502 | 470.478 | 477.7111 | 319.4782 | 648.103 | 643.8502 | 470.478 | 1.0032 | 0.88997 | 1.2372 | 1.2706 | 1.0313
6 | SH-10-HH | 06-SH-10-HH | 2269.5696 | 1428.6328 | 1559.853 | 1427.8142 | 1969.4615 | 752.0699 | 513.9475 | 1115.3566 | 1115.708 | 768.6842 | 1.7276 | 1.5998 | 2.1981 | 2.3428 | 1.798
6 | SH-10-HL | 06-SH-10-HL | 2314.3764 | 1441.2897 | 1603.963 | 1464.003 | 2007.1162 | 773.6586 | 522.2261 | 1155.4702 | 1149.6838 | 790.3103 | 1.8117 | 1.5956 | 2.3102 | 2.416 | 1.8661
6 | SH-10-HM | 06-SH-10-HM | 2225.4945 | 1395.3327 | 1559.479 | 1423.1478 | 1934.6786 | 761.3889 | 513.6646 | 1123.6897 | 1117.5036 | 775.3378 | 1.7785 | 1.5655 | 2.2594 | 2.3594 | 1.8299
6 | SH-10-LH | 06-SH-10-LH | 2387.1794 | 1479.641 | 1601.0514 | 1458.8688 | 2059.8228 | 763.8522 | 512.0937 | 1127.7238 | 1126.3452 | 777.7399 | 1.7264 | 1.4955 | 2.1728 | 2.2734 | 1.7683
6 | SH-10-LL | 06-SH-10-LL | 2259.0981 | 1411.1927 | 1592.7353 | 1455.663 | 1964.6845 | 777.2811 | 523.6834 | 1157.6572 | 1150.0829 | 793.0914 | 1.8392 | 1.6148 | 2.3497 | 2.447 | 1.8932
6 | SH-10-LM | 06-SH-10-LM | 2250.5587 | 1406.0901 | 1577.2818 | 1444.9888 | 1956.0671 | 774.4657 | 520.0908 | 1140.8318 | 1137.754 | 788.115 | 1.7867 | 1.5634 | 2.2652 | 2.3605 | 1.8352
6 | SH-10-MH | 06-SH-10-MH | 2334.2738 | 1448.6153 | 1575.418 | 1437.7493 | 2016.3574 | 752.0465 | 505.8702 | 1114.9874 | 1114.303 | 766.9289 | 1.7376 | 1.5115 | 2.199 | 2.3085 | 1.7839
6 | SH-10-ML | 06-SH-10-ML | 2145.5041 | 1345.1749 | 1555.4008 | 1424.5691 | 1874.2259 | 765.8361 | 517.5738 | 1148.5764 | 1139.5919 | 782.9665 | 1.826 | 1.6116 | 2.3609 | 2.4971 | 1.8899
6 | SH-10-MM | 06-SH-10-MM | 2295.9504 | 1433.3046 | 1580.5551 | 1439.2647 | 1989.7393 | 772.9639 | 522.761 | 1134.8163 | 1127.0347 | 786.1998 | 1.8057 | 1.5902 | 2.2719 | 2.3795 | 1.8547
6 | SH-13-HH | 06-SH-13-HH | 2021.196 | 1253.5458 | 1280.0649 | 1152.4044 | 1730.3653 | 575.4729 | 388.1499 | 854.5177 | 853.3188 | 587.2323 | 1.3283 | 1.1644 | 1.6884 | 1.7988 | 1.3693
6 | SH-13-HL | 06-SH-13-HL | 1816.2796 | 1136.37 | 1243.5838 | 1112.9843 | 1571.5796 | 570.3151 | 389.4503 | 878.253 | 858.9573 | 586.6463 | 1.3611 | 1.2477 | 1.87 | 1.8451 | 1.425
6 | SH-13-HM | 06-SH-13-HM | 1862.1158 | 1159.6974 | 1237.0245 | 1120.7734 | 1605.2702 | 576.5464 | 389.2105 | 858.209 | 854.9685 | 588.5652 | 1.3438 | 1.1835 | 1.718 | 1.8226 | 1.3874
6 | SH-13-LH | 06-SH-13-LH | 2067.6018 | 1270.3 | 1289.0355 | 1161.4889 | 1764.4838 | 576.1567 | 387.9771 | 859.6763 | 859.12 | 588.5868 | 1.3309 | 1.1601 | 1.6966 | 1.7798 | 1.3689
6 | SH-13-LL | 06-SH-13-LL | 1870.0638 | 1159.3724 | 1214.0307 | 1091.9677 | 1605.6768 | 559.0797 | 377.1604 | 831.8601 | 823.7015 | 570.1492 | 1.3168 | 1.1582 | 1.6828 | 1.7477 | 1.3555
6 | SH-13-LM | 06-SH-13-LM | 1796.5414 | 1116.579 | 1248.9382 | 1141.6696 | 1558.3948 | 602.6339 | 406.4625 | 903.5293 | 900.4586 | 616.2834 | 1.4052 | 1.2331 | 1.8142 | 1.928 | 1.4533
6 | SH-13-MH | 06-SH-13-MH | 1994.476 | 1248.1957 | 1228.325 | 1103.9803 | 1703.7879 | 545.8733 | 373.9362 | 802.6023 | 803.7898 | 556.9879 | 1.2345 | 1.1322 | 1.5614 | 1.6605 | 1.2806
6 | SH-13-ML | 06-SH-13-ML | 1977.0122 | 1217.8379 | 1283.8886 | 1157.1247 | 1696.263 | 591.9705 | 400.1655 | 889.4813 | 882.0865 | 605.4767 | 1.4064 | 1.247 | 1.835 | 1.9346 | 1.4591
6 | SH-13-MM | 06-SH-13-MM | 1916.6788 | 1189.2238 | 1230.5622 | 1106.7054 | 1643.62 | 559.7481 | 377.9267 | 833.1864 | 828.1165 | 571.2428 | 1.3223 | 1.1612 | 1.6864 | 1.7893 | 1.3638
6 | SH-14-HH | 06-SH-14-HH | 1853.6653 | 1151.6077 | 1194.3438 | 1076.4776 | 1590.7907 | 540.2607 | 364.834 | 807.7108 | 805.1168 | 552.1987 | 1.2591 | 1.0975 | 1.6094 | 1.7112 | 1.298
6 | SH-14-HL | 06-SH-14-HL | 1821.2389 | 1135.961 | 1190.8602 | 1070.7322 | 1566.4579 | 540.2886 | 369.0767 | 817.7452 | 809.8199 | 554.2849 | 1.2917 | 1.1834 | 1.6737 | 1.7694 | 1.3459
6 | SH-14-HM | 06-SH-14-HM | 1812.7524 | 1125.7215 | 1189.9703 | 1075.9945 | 1559.5299 | 546.6428 | 368.6129 | 818.7624 | 815.5245 | 558.8225 | 1.278 | 1.1141 | 1.635 | 1.7371 | 1.3176
6 | SH-14-MH | 06-SH-14-MH | 1885.4702 | 1161.4952 | 1199.1498 | 1067.7166 | 1612.3402 | 542.4752 | 364.866 | 810.6494 | 796.3586 | 553.0073 | 1.2494 | 1.0846 | 1.5854 | 1.5635 | 1.2735
6 | SH-14-ML | 06-SH-14-ML | 1934.1035 | 1180.3713 | 1196.6195 | 1067.1211 | 1646.4526 | 525.4882 | 354.3171 | 799.5382 | 789.5651 | 538.7072 | 1.2639 | 1.1568 | 1.6664 | 1.7157 | 1.3176
6 | SH-14-MM | 06-SH-14-MM | 1788.7539 | 1107.6083 | 1178.0463 | 1065.4057 | 1538.9053 | 538.0662 | 363.9623 | 816.1317 | 812.0781 | 551.969 | 1.2672 | 1.1053 | 1.6382 | 1.7386 | 1.3095
6 | SH-15-HH | 06-SH-15-HH | 2012.8786 | 1240.9889 | 1182.8678 | 1049.5525 | 1705.244 | 502.2888 | 342.7038 | 750.4956 | 745.9954 | 513.7993 | 1.158 | 1.0407 | 1.4818 | 1.5699 | 1.1997
6 | SH-15-HL | 06-SH-15-HL | 1614.6416 | 1012.0343 | 1089.0289 | 985.6797 | 1395.8023 | 507.2421 | 345.6431 | 763.5853 | 757.9002 | 519.6605 | 1.2006 | 1.1003 | 1.5516 | 1.64 | 1.2504
6 | SH-15-HM | 06-SH-15-HM | 1633.8963 | 1026.4704 | 1069.8462 | 963.9001 | 1407.1922 | 486.0924 | 332.6105 | 729.4724 | 725.2758 | 497.9856 | 1.1356 | 1.0422 | 1.466 | 1.5458 | 1.1823
6 | SH-15-MH | 06-SH-15-MH | 1845.3078 | 1125.0098 | 1111.0344 | 988.9029 | 1565.4443 | 481.3568 | 324.9259 | 726.9839 | 720.2593 | 492.8252 | 1.1392 | 1.0047 | 1.4968 | 1.5411 | 1.1792
6 | SH-15-ML | 06-SH-15-ML | 1725.414 | 1058.8842 | 1100.0966 | 984.1933 | 1475.5752 | 491.7266 | 331.7307 | 749.0159 | 738.9524 | 504.209 | 1.1805 | 1.0708 | 1.5632 | 1.6042 | 1.2294
6 | SH-15-MM | 06-SH-15-MM | 1780.7016 | 1105.4457 | 1111.8208 | 978.15 | 1519.9105 | 480.4284 | 328.1113 | 732.2304 | 713.7319 | 492.6611 | 1.1296 | 1.0167 | 1.5281 | 1.5076 | 1.1749
6 | SH-16-CH | 06-SH-16-CH | 1845.8747 | 1123.6147 | 1154.9583 | 1032.1849 | 1573.0996 | 554.9818 | 373.7499 | 801.0923 | 785.2163 | 560.823 | 1.2429 | 1.1205 | 1.6437 | 1.6235 | 1.2867
6 | SH-16-CL | 06-SH-16-CL | 1753.2885 | 1069.2802 | 1128.0462 | 1012.9066 | 1500.1193 | 550.6306 | 371.0727 | 798.8192 | 783.2577 | 557.1897 | 1.2546 | 1.1323 | 1.6675 | 1.6488 | 1.3007
6 | SH-16-LH | 06-SH-16-LH | 1978.8229 | 1221.5471 | 1136.4885 | 1023.3452 | 1673.809 | 527.3123 | 360.8793 | 729.9985 | 734.7388 | 530.4493 | 1.1329 | 1.0235 | 1.3961 | 1.4234 | 1.1598
6 | SH-16-LL | 06-SH-16-LL | 1861.8132 | 1133.238 | 1153.3973 | 1037.8941 | 1585.4507 | 553.0677 | 371.6504 | 792.922 | 784.7826 | 558.5168 | 1.2479 | 1.0806 | 1.5733 | 1.5959 | 1.2739
6 | SH-16-LM | 06-SH-16-LM | 1999.2677 | 1215.1473 | 1177.2181 | 1063.0936 | 1692.4394 | 550.6224 | 368.4452 | 773.1884 | 776.6806 | 554.0185 | 1.1948 | 1.0337 | 1.4922 | 1.5189 | 1.2175
6 | SH-16-TH | 06-SH-16-TH | 2105.4803 | 1278.792 | 1135.7625 | 982.8543 | 1761.0145 | 508.2456 | 346.3512 | 695.3593 | 674.2496 | 507.1216 | 1.0703 | 0.96149 | 1.4027 | 1.3565 | 1.1024
6 | SH-16-TL | 06-SH-16-TL | 2146.961 | 1277.0919 | 1182.4988 | 1037.6441 | 1795.731 | 549.8962 | 368.6281 | 765.5597 | 745.8615 | 550.0796 | 1.225 | 1.0845 | 1.5172 | 1.5545 | 1.2518
6 | SH-16-TM | 06-SH-16-TM | 2173.0015 | 1292.3445 | 1183.7044 | 1037.5009 | 1815.2213 | 544.4722 | 364.8843 | 757.3597 | 738.9615 | 544.6246 | 1.2114 | 1.0689 | 1.4915 | 1.5305 | 1.2359
6 | SH-17-CM | 06-SH-17-CM | 1915.5132 | 1138.9081 | 1115.5331 | 989.9006 | 1612.9003 | 518.7592 | 348.5522 | 752.8198 | 737.6736 | 524.7304 | 1.1829 | 1.068 | 1.5717 | 1.554 | 1.2263
6 | SH-17-LM | 06-SH-17-LM | 1786.9313 | 1096.2256 | 1082.2227 | 972.7242 | 1519.1806 | 512.2463 | 349.4522 | 730.5956 | 725.3812 | 517.875 | 1.1537 | 1.0135 | 1.4153 | 1.4424 | 1.1743
6 | SH-17-TH | 06-SH-17-TH | 2064.6781 | 1247.6194 | 1076.3603 | 943.2129 | 1720.7298 | 474.5323 | 323.7614 | 647.4761 | 639.1545 | 474.3286 | 1.0176 | 0.91657 | 1.2671 | 1.2943 | 1.0438
6 | SH-17-TL | 06-SH-17-TL | 2048.0392 | 1234.3546 | 1075.0066 | 941.1403 | 1707.3378 | 476.8169 | 325.0039 | 653.1449 | 642.8199 | 476.8082 | 1.0299 | 0.92755 | 1.2894 | 1.314 | 1.0573
6 | SH-18-LH | 06-SH-18-LH | 1902.8949 | 1144.6547 | 1062.932 | 944.8139 | 1597.6346 | 477.1407 | 321.8517 | 678.2819 | 674.464 | 481.3784 | 1.0648 | 0.94293 | 1.3405 | 1.3616 | 1.0909
6 | SH-18-LL | 06-SH-18-LL | 1793.6117 | 1087.371 | 1065.0932 | 956.99 | 1518.8205 | 493.8755 | 332.9303 | 708.9254 | 707.0895 | 499.6115 | 1.1179 | 0.96886 | 1.4063 | 1.4331 | 1.1414
6 | SH-18-LM | 06-SH-18-LM | 1978.5777 | 1187.2035 | 1082.3734 | 960.2466 | 1656.6928 | 481.9937 | 324.9006 | 680.3737 | 678.0281 | 485.5382 | 1.0652 | 0.95277 | 1.35 | 1.3712 | 1.0947
6 | SH-18-TM | 06-SH-18-TM | 1977.889 | 1178.0951 | 1006.4011 | 876.6305 | 1640.5574 | 436.2385 | 293.6189 | 596.8914 | 585.7582 | 435.2267 | 0.93426 | 0.84687 | 1.2025 | 1.2177 | 0.96522
7 | SA-10-HH | 07-SA-10-HH | 1071.1724 | 800.2544 | 1408.7464 | 1402.5311 | 1095.9791 | 1071.1724 | 800.2544 | 1408.7464 | 1402.5311 | 1095.9791 | 2.3255 | 2.1636 | 2.534 | 2.6654 | 2.3522
7 | SA-10-HL | 07-SA-10-HL | 1053.733 | 789.2 | 1405.0199 | 1392.9807 | 1084.3643 | 1053.733 | 789.2 | 1405.0199 | 1392.9807 | 1084.3643 | 2.3949 | 2.2359 | 2.6485 | 2.7719 | 2.4361
7 | SA-10-HM | 07-SA-10-HM | 1056.8251 | 789.2333 | 1405.4692 | 1395.7766 | 1085.8735 | 1056.8251 | 789.2333 | 1405.4692 | 1395.7766 | 1085.8735 | 2.3605 | 2.2011 | 2.5996 | 2.729 | 2.3974
7 | SA-10-LH | 07-SA-10-LH | 1013.2603 | 755.6309 | 1362.7036 | 1361.381 | 1046.1527 | 1013.2603 | 755.6309 | 1362.7036 | 1361.381 | 1046.1527 | 2.275 | 2.1236 | 2.5209 | 2.6468 | 2.3162
7 | SA-10-LL | 07-SA-10-LL | 1073.7336 | 802.1987 | 1443.8589 | 1431.7888 | 1108.2075 | 1073.7336 | 802.1987 | 1443.8589 | 1431.7888 | 1108.2075 | 2.4288 | 2.2804 | 2.7072 | 2.8267 | 2.4807
7 | SA-10-LM | 07-SA-10-LM | 1028.9665 | 768.5973 | 1381.5639 | 1379.4002 | 1061.9717 | 1028.9665 | 768.5973 | 1381.5639 | 1379.4002 | 1061.9717 | 2.3164 | 2.1652 | 2.5601 | 2.6885 | 2.3572
7 | SA-10-MH | 07-SA-10-MH | 1029.309 | 764.9182 | 1363.203 | 1363.0562 | 1055.3496 | 1029.309 | 764.9182 | 1363.203 | 1363.0562 | 1055.3496 | 2.2377 | 2.0795 | 2.4531 | 2.5904 | 2.2681
7 | SA-10-ML | 07-SA-10-ML | 1083.8653 | 811.2816 | 1445.5359 | 1437.7432 | 1115.664 | 1083.8653 | 811.2816 | 1445.5359 | 1437.7432 | 1115.664 | 2.4658 | 2.3084 | 2.7316 | 2.8569 | 2.5115
7 | SA-10-MM | 07-SA-10-MM | 1009.2428 | 754.4027 | 1351.1926 | 1313.6212 | 1037.9975 | 1009.2428 | 754.4027 | 1351.1926 | 1313.6212 | 1037.9975 | 2.2683 | 2.139 | 2.5097 | 2.5099 | 2.3057
7 | SA-13-HH | 07-SA-13-HH | 801.2292 | 600.0292 | 1079.3586 | 1072.8444 | 828.1718 | 801.2292 | 600.0292 | 1079.3586 | 1072.8444 | 828.1718 | 1.7822 | 1.6657 | 1.9849 | 2.0784 | 1.818
7 | SA-13-HL | 07-SA-13-HL | 788.762 | 590.5633 | 1066.3448 | 1053.774 | 815.9966 | 788.762 | 590.5633 | 1066.3448 | 1053.774 | 815.9966 | 1.8136 | 1.7192 | 2.0558 | 2.1356 | 1.8675
7 | SA-13-HM | 07-SA-13-HM | 794.0957 | 598.6064 | 1090.2239 | 1068.1871 | 827.3151 | 794.0957 | 598.6064 | 1090.2239 | 1068.1871 | 827.3151 | 1.817 | 1.7656 | 2.1492 | 2.1355 | 1.9054
7 | SA-13-LH | 07-SA-13-LH | 780.6811 | 581.4034 | 1048.3903 | 1021.8763 | 803.4719 | 780.6811 | 581.4034 | 1048.3903 | 1021.8763 | 803.4719 | 1.7226 | 1.5979 | 1.8922 | 1.8925 | 1.7388
7 | SA-13-LL | 07-SA-13-LL | 811.8353 | 607.5178 | 1092.5111 | 1064.6853 | 837.112 | 811.8353 | 607.5178 | 1092.5111 | 1064.6853 | 837.112 | 1.8183 | 1.707 | 2.026 | 2.0248 | 1.8504
7 | SA-13-LM | 07-SA-13-LM | 812.6702 | 606.2494 | 1092.1746 | 1064.0425 | 836.924 | 812.6702 | 606.2494 | 1092.1746 | 1064.0425 | 836.924 | 1.7827 | 1.6639 | 1.9744 | 1.9736 | 1.8075
7 | SA-13-MH | 07-SA-13-MH | 764.5794 | 570.8747 | 1015.0168 | 1014.5851 | 785.4688 | 764.5794 | 570.8747 | 1015.0168 | 1014.5851 | 785.4688 | 1.7239 | 1.612 | 1.9068 | 2.0028 | 1.755
7 | SA-13-ML | 07-SA-13-ML | 791.1755 | 592.0545 | 1075.702 | 1061.8804 | 820.2349 | 791.1755 | 592.0545 | 1075.702 | 1061.8804 | 820.2349 | 1.7896 | 1.6931 | 2.0201 | 2.1034 | 1.8394
7 | SA-13-MM | 07-SA-13-MM | 767.2056 | 572.6365 | 1020.7546 | 1016.6984 | 788.5568 | 767.2056 | 572.6365 | 1020.7546 | 1016.6984 | 788.5568 | 1.7628 | 1.6557 | 1.9569 | 2.0449 | 1.7983
7 | SA-14-HH | 07-SA-14-HH | 759.7776 | 567.1892 | 1023.7104 | 1020.6361 | 785.0711 | 759.7776 | 567.1892 | 1023.7104 | 1020.6361 | 785.0711 | 1.7015 | 1.5953 | 1.9078 | 1.9893 | 1.7406
7 | SA-14-HL | 07-SA-14-HL | 726.1264 | 543.8288 | 986.8125 | 978.1607 | 753.0815 | 726.1264 | 543.8288 | 986.8125 | 978.1607 | 753.0815 | 1.6762 | 1.572 | 1.8957 | 1.9721 | 1.7197
7 | SA-14-HM | 07-SA-14-HM | 727.3534 | 544.1333 | 987.3722 | 979.9961 | 753.9129 | 727.3534 | 544.1333 | 987.3722 | 979.9961 | 753.9129 | 1.6826 | 1.5852 | 1.904 | 1.9863 | 1.7292
7 | SA-14-MH | 07-SA-14-MH | 771.7013 | 575.0714 | 1031.2199 | 1005.6981 | 792.773 | 771.7013 | 575.0714 | 1031.2199 | 1005.6981 | 792.773 | 1.6692 | 1.5484 | 1.8342 | 1.8336 | 1.685
7 | SA-14-ML | 07-SA-14-ML | 739.0426 | 551.6356 | 1007.3776 | 995.7859 | 766.667 | 739.0426 | 551.6356 | 1007.3776 | 995.7859 | 766.667 | 1.6758 | 1.5821 | 1.8923 | 1.9751 | 1.722
7 | SA-14-MM | 07-SA-14-MM | 746.9615 | 558.2098 | 1003.0647 | 977.7426 | 769.3334 | 746.9615 | 558.2098 | 1003.0647 | 977.7426 | 769.3334 | 1.6306 | 1.5172 | 1.8029 | 1.8016 | 1.6508
7 | SA-15-HH | 07-SA-15-HH | 672.0232 | 508.8994 | 920.4421 | 901.8732 | 700.1457 | 672.0232 | 508.8994 | 920.4421 | 901.8732 | 700.1457 | 1.5163 | 1.4703 | 1.7871 | 1.7759 | 1.5872
7 | SA-15-HL | 07-SA-15-HL | 666.3835 | 503.9411 | 900.3492 | 892.4033 | 690.9136 | 666.3835 | 503.9411 | 900.3492 | 892.4033 | 690.9136 | 1.5348 | 1.4897 | 1.7223 | 1.7947 | 1.5857
7 | SA-15-HM | 07-SA-15-HM | 684.0188 | 518.0106 | 937.1153 | 918.3054 | 712.7348 | 684.0188 | 518.0106 | 937.1153 | 918.3054 | 712.7348 | 1.535 | 1.4886 | 1.8093 | 1.797 | 1.6068
7 | SA-15-MH | 07-SA-15-MH | 680.8847 | 509.1415 | 914.7801 | 910.3587 | 702.8556 | 680.8847 | 509.1415 | 914.7801 | 910.3587 | 702.8556 | 1.5292 | 1.4361 | 1.7203 | 1.7986 | 1.5672
7 | SA-15-ML | 07-SA-15-ML | 693.447 | 518.4426 | 929.1709 | 923.3887 | 714.9185 | 693.447 | 518.4426 | 929.1709 | 923.3887 | 714.9185 | 1.5747 | 1.4838 | 1.7648 | 1.8449 | 1.6132
7 | SA-15-MM | 07-SA-15-MM | 687.7581 | 513.479 | 927.5355 | 921.0998 | 710.6795 | 687.7581 | 513.479 | 927.5355 | 921.0998 | 710.6795 | 1.5629 | 1.4702 | 1.762 | 1.8353 | 1.6032
7 | SA-16-CH | 07-SA-16-CH | 794.7018 | 589.9517 | 1030.3015 | 1007.7113 | 805.9988 | 794.7018 | 589.9517 | 1030.3015 | 1007.7113 | 805.9988 | 1.7259 | 1.6585 | 1.9773 | 1.9633 | 1.784
7 | SA-16-CL | 07-SA-16-CL | 748.1842 | 558.0156 | 976.7347 | 954.8848 | 761.6849 | 748.1842 | 558.0156 | 976.7347 | 954.8848 | 761.6849 | 1.6671 | 1.5993 | 1.9156 | 1.9007 | 1.7241
7 | SA-16-CM | 07-SA-16-CM | 764.8183 | 571.3479 | 1000.6616 | 978.6799 | 779.6205 | 764.8183 | 571.3479 | 1000.6616 | 978.6799 | 779.6205 | 1.685 | 1.6184 | 1.9322 | 1.918 | 1.742
7 | SA-16-LH | 07-SA-16-LH | 741.0314 | 546.2446 | 933.506 | 928.8389 | 742.9972 | 741.0314 | 546.2446 | 933.506 | 928.8389 | 742.9972 | 1.5811 | 1.4838 | 1.7189 | 1.771 | 1.5992
7 | SA-16-LL | 07-SA-16-LL | 762.9751 | 567.1119 | 972.8159 | 967.1343 | 770.026 | 762.9751 | 567.1119 | 972.8159 | 967.1343 | 770.026 | 1.6357 | 1.5319 | 1.7998 | 1.8483 | 1.6598
7 | SA-16-LM | 07-SA-16-LM | 765.066 | 567.4525 | 979.475 | 971.3218 | 772.8556 | 765.066 | 567.4525 | 979.475 | 971.3218 | 772.8556 | 1.6275 | 1.5158 | 1.7766 | 1.8359 | 1.6453
7 | SA-16-NM | 07-SA-16-NM | 734.8961 | 540.9861 | 959.8257 | 938.9501 | 746.2015 | 734.8961 | 540.9861 | 959.8257 | 938.9501 | 746.2015 | 1.5367 | 1.4444 | 1.7254 | 1.7506 | 1.5704
7 | SA-16-TH | 07-SA-16-TH | 798.2976 | 583.7339 | 960.4407 | 957.6095 | 784.8883 | 798.2976 | 583.7339 | 960.4407 | 957.6095 | 784.8883 | 1.6715 | 1.5418 | 1.7894 | 1.8621 | 1.6751
7 | SA-16-TL | 07-SA-16-TL | 780.7655 | 570.616 | 949.0251 | 934.4282 | 769.7642 | 780.7655 | 570.616 | 949.0251 | 934.4282 | 769.7642 | 1.7009 | 1.5774 | 1.8268 | 1.8824 | 1.7076
7 | SA-17-CH | 07-SA-17-CH | 723.1675 | 540.1401 | 950.5287 | 929.1276 | 738.4679 | 723.1675 | 540.1401 | 950.5287 | 929.1276 | 738.4679 | 1.5964 | 1.5373 | 1.8401 | 1.8263 | 1.6546
7 | SA-17-CL | 07-SA-17-CL | 723.521 | 540.8187 | 951.6983 | 930.777 | 739.2111 | 723.521 | 540.8187 | 951.6983 | 930.777 | 739.2111 | 1.6115 | 1.5515 | 1.862 | 1.8467 | 1.6714
7 | SA-17-CM | 07-SA-17-CM | 738.7485 | 548.1518 | 958.6128 | 937.868 | 749.4588 | 738.7485 | 548.1518 | 958.6128 | 937.868 | 749.4588 | 1.6197 | 1.5581 | 1.8654 | 1.8497 | 1.6776
7 | SA-17-LH | 07-SA-17-LH | 701.6243 | 519.0233 | 894.3889 | 888.284 | 707.2345 | 701.6243 | 519.0233 | 894.3889 | 888.284 | 707.2345 | 1.5031 | 1.4112 | 1.6486 | 1.6948 | 1.5248
7 | SA-17-LL | 07-SA-17-LL | 725.7783 | 539.4165 | 924.8281 | 919.9775 | 732.3341 | 725.7783 | 539.4165 | 924.8281 | 919.9775 | 732.3341 | 1.5601 | 1.4518 | 1.7032 | 1.7547 | 1.5765
7 | SA-17-LM | 07-SA-17-LM | 732.1373 | 542.5226 | 935.2239 | 929.4898 | 738.9275 | 732.1373 | 542.5226 | 935.2239 | 929.4898 | 738.9275 | 1.5489 | 1.4414 | 1.6919 | 1.7469 | 1.5657
7 | SA-17-TH | 07-SA-17-TH | 676.5782 | 498.8786 | 825.6897 | 823.5941 | 670.1701 | 676.5782 | 498.8786 | 825.6897 | 823.5941 | 670.1701 | 1.4548 | 1.3418 | 1.5559 | 1.6234 | 1.4577
7 | SA-17-TL | 07-SA-17-TL | 654.8128 | 483.9805 | 823.5443 | 800.2155 | 655.1291 | 654.8128 | 483.9805 | 823.5443 | 800.2155 | 655.1291 | 1.5198 | 1.4016 | 1.6606 | 1.7027 | 1.5318
7 | SA-17-TM | 07-SA-17-TM | 768.0317 | 553.9124 | 905.0751 | 897.3032 | 746.4783 | 768.0317 | 553.9124 | 905.0751 | 897.3032 | 746.4783 | 1.6085 | 1.4849 | 1.6998 | 1.7717 | 1.6054
7 | SA-18-LH | 07-SA-18-LH | 686.0141 | 507.5679 | 868.7905 | 862.3404 | 689.6937 | 686.0141 | 507.5679 | 868.7905 | 862.3404 | 689.6937 | 1.4559 | 1.3573 | 1.5883 | 1.6347 | 1.4714
7 | SA-18-LL | 07-SA-18-LL | 667.8218 | 497.6312 | 856.0448 | 844.741 | 675.3481 | 667.8218 | 497.6312 | 856.0448 | 844.741 | 675.3481 | 1.4625 | 1.3678 | 1.6056 | 1.6464 | 1.4822
7 | SA-18-TH | 07-SA-18-TH | 662.5609 | 486.4744 | 798.8752 | 799.1056 | 652.7653 | 662.5609 | 486.4744 | 798.8752 | 799.1056 | 652.7653 | 1.3974 | 1.2832 | 1.4817 | 1.5467 | 1.3944
7 | SA-18-TL | 07-SA-18-TL | 681.7047 | 501.7338 | 832.1547 | 825.3823 | 674.7009 | 681.7047 | 501.7338 | 832.1547 | 825.3823 | 674.7009 | 1.4786 | 1.3625 | 1.5777 | 1.6431 | 1.4797
7 | SA-18-TM | 07-SA-18-TM | 681.4549 | 500.9095 | 833.1384 | 830.6711 | 674.9779 | 681.4549 | 500.9095 | 833.1384 | 830.6711 | 674.9779 | 1.434 | 1.3222 | 1.536 | 1.599 | 1.4372
7 | SH-10-HH | 07-SH-10-HH | 2330.4837 | 1478.8319 | 1687.7899 | 1582.7995 | 1905.1784 | 1024.471 | 763.5982 | 1366.7253 | 1366.0656 | 992.7215 | 2.2618 | 2.1063 | 2.4839 | 2.6155 | 2.2543
7 | SH-10-HL | 07-SH-10-HL | 2378.3843 | 1510.9633 | 1740.2056 | 1619.6718 | 1947.2996 | 1055.0389 | 787.846 | 1416.6153 | 1401.9231 | 1023.6253 | 2.37 | 2.2087 | 2.6033 | 2.739 | 2.3627
7 | SH-10-HM | 07-SH-10-HM | 2305.9546 | 1475.9302 | 1696.019 | 1593.4722 | 1894.3803 | 1044.9659 | 780.2692 | 1381.3148 | 1381.0656 | 1010.8207 | 2.3177 | 2.1626 | 2.5497 | 2.6772 | 2.3119
7 | SH-10-LH | 07-SH-10-LH | 2428.108 | 1527.8576 | 1706.5388 | 1597.9201 | 1971.1206 | 1032.8353 | 767.4164 | 1366.2511 | 1367.6448 | 998.0092 | 2.2102 | 2.0453 | 2.409 | 2.5537 | 2.196
7 | SH-10-LL | 07-SH-10-LL | 2343.0387 | 1496.2017 | 1734.2051 | 1620.1977 | 1924.9552 | 1060.7174 | 792.3212 | 1417.8636 | 1406.6247 | 1028.2957 | 2.3764 | 2.212 | 2.6038 | 2.7364 | 2.3668
7 | SH-10-LM | 07-SH-10-LM | 2328.544 | 1485.5796 | 1710.338 | 1604.3407 | 1910.6601 | 1052.8726 | 783.3108 | 1393.4443 | 1390.0775 | 1017.5554 | 2.2853 | 2.1245 | 2.5108 | 2.6399 | 2.2764
7 | SH-10-MH | 07-SH-10-MH | 2385.3818 | 1505.3262 | 1695.4149 | 1584.9215 | 1941.1393 | 1023.0805 | 762.7779 | 1363.531 | 1360.8447 | 991.0853 | 2.2493 | 2.0891 | 2.4623 | 2.5999 | 2.2389
7 | SH-10-ML | 07-SH-10-ML | 2242.8235 | 1440.6514 | 1705.8657 | 1601.7419 | 1854.1543 | 1048.4973 | 783.2318 | 1409.7548 | 1401.7451 | 1018.1289 | 2.3805 | 2.2282 | 2.6625 | 2.7782 | 2.3839
7 | SH-10-MM | 07-SH-10-MM | 2374.1231 | 1513.9061 | 1725.0875 | 1584.089 | 1942.3909 | 1064.0061 | 796.3664 | 1403.2014 | 1368.8771 | 1027.2046 | 2.3572 | 2.1974 | 2.5671 | 2.5676 | 2.3379
7 | SH-13-HH | 07-SH-13-HH | 2038.518 | 1273.5214 | 1364.2189 | 1265.8767 | 1638.8616 | 791.7459 | 590.5343 | 1056.8922 | 1058.2041 | 767.5793 | 1.7681 | 1.6491 | 1.9661 | 2.0668 | 1.7674
7 | SH-13-HL | 07-SH-13-HL | 1856.8634 | 1181.7649 | 1343.8812 | 1235.8342 | 1517.5538 | 783.752 | 592.5919 | 1079.9181 | 1059.359 | 767.367 | 1.7921 | 1.7411 | 2.1272 | 2.112 | 1.833
7 | SH-13-HM | 07-SH-13-HM | 1901.4995 | 1199.9869 | 1334.0203 | 1243.0233 | 1544.0691 | 793.6044 | 592.1646 | 1060.3511 | 1058.3288 | 769.4359 | 1.7865 | 1.6727 | 1.989 | 2.0837 | 1.7881
7 | SH-13-LH | 07-SH-13-LH | 2074.6063 | 1285.0385 | 1361.8675 | 1256.0872 | 1658.8413 | 783.4512 | 583.7361 | 1051.2916 | 1045.6703 | 759.87 | 1.7195 | 1.5971 | 1.8951 | 2.0011 | 1.7139
7 | SH-13-LL | 07-SH-13-LL | 1899.9924 | 1192.32 | 1299.7891 | 1205.8764 | 1534.3229 | 769.7182 | 575.0809 | 1023.3459 | 1019.8901 | 745.5362 | 1.7393 | 1.6365 | 1.9358 | 2.0195 | 1.743
7 | SH-13-LM | 07-SH-13-LM | 1841.038 | 1167.3999 | 1351.625 | 1240.6236 | 1506.2874 | 818.207 | 611.0827 | 1103.463 | 1075.0127 | 793.6854 | 1.8035 | 1.6855 | 2.0064 | 2.005 | 1.7977
7 | SH-13-MH | 07-SH-13-MH | 2003.7809 | 1246.2647 | 1300.8113 | 1205.9833 | 1601.8744 | 751.3901 | 560.2993 | 992.7267 | 996.8561 | 726.7421 | 1.6481 | 1.535 | 1.8234 | 1.9152 | 1.6449
7 | SH-13-ML | 07-SH-13-ML | 2000.4561 | 1249.6473 | 1376.2999 | 1275.6294 | 1614.6957 | 810.5021 | 606.6843 | 1091.8264 | 1084.8791 | 787.791 | 1.8264 | 1.7173 | 2.0554 | 2.1464 | 1.8342
7 | SH-13-MM | 07-SH-13-MM | 1942.7516 | 1217.9346 | 1323.0375 | 1224.6603 | 1567.1968 | 774.4768 | 578.5739 | 1035.3544 | 1031.0932 | 751.0921 | 1.765 | 1.659 | 1.97 | 2.061 | 1.7696
7 | SH-14-HH | 07-SH-14-HH | 1878.1289 | 1177.2423 | 1280.2698 | 1186.7774 | 1515.3248 | 745.547 | 556.7878 | 1000.9123 | 998.3057 | 723.8248 | 1.6832 | 1.5723 | 1.8793 | 1.9695 | 1.6844
7 | SH-14-HL | 07-SH-14-HL | 1850.8371 | 1162.1412 | 1281.3045 | 1183.095 | 1497.1607 | 744.9505 | 558.2814 | 1010.7474 | 1001.147 | 725.4077 | 1.7165 | 1.6142 | 1.932 | 2.0126 | 1.7236
7 | SH-14-HM | 07-SH-14-HM | 1844.4001 | 1158.4321 | 1277.2068 | 1185.8516 | 1492.5412 | 749.6275 | 559.244 | 1007.8417 | 1004.1451 | 727.7688 | 1.6836 | 1.5738 | 1.8787 | 1.965 | 1.6848
7 | SH-14-MH | 07-SH-14-MH | 1900.2308 | 1182.6923 | 1270.4723 | 1153.2215 | 1524.2995 | 736.6381 | 549.2072 | 988.5806 | 964.2893 | 713.4294 | 1.6122 | 1.4956 | 1.7733 | 1.7728 | 1.5995
7 | SH-14-ML | 07-SH-14-ML | 1937.9895 | 1193.8837 | 1262.6596 | 1161.0225 | 1545.3925 | 718.9055 | 537.6962 | 974.7159 | 967.3047 | 699.6566 | 1.6632 | 1.5675 | 1.8729 | 1.9502 | 1.6714
7 | SH-14-MM | 07-SH-14-MM | 1814.9161 | 1136.5845 | 1265.9405 | 1163.9096 | 1468.38 | 734.3035 | 548.6264 | 1003.7424 | 987.4151 | 715.3488 | 1.6529 | 1.5473 | 1.8489 | 1.9348 | 1.6557
7 | SH-15-HH | 07-SH-15-HH | 1995.6729 | 1224.349 | 1236.399 | 1132.6887 | 1578.2058 | 690.4624 | 516.3056 | 923.9201 | 922.5967 | 670.1023 | 1.5358 | 1.4338 | 1.7068 | 1.7832 | 1.5348
7 | SH-15-HL | 07-SH-15-HL | 1651.7318 | 1045.0197 | 1177.8388 | 1093.4164 | 1345.2751 | 697.0923 | 521.6282 | 941.9333 | 934.727 | 677.9396 | 1.5869 | 1.4919 | 1.787 | 1.8595 | 1.5934
7 | SH-15-HM | 07-SH-15-HM | 1660.1119 | 1046.3068 | 1152.9971 | 1063.0582 | 1344.8326 | 669.3487 | 501.8439 | 906.7712 | 896.8246 | 651.5349 | 1.5202 | 1.4243 | 1.7017 | 1.7748 | 1.5231
7 | SH-15-MH | 07-SH-15-MH | 1835.6512 | 1127.0817 | 1173.5134 | 1075.8327 | 1458.3336 | 661.6068 | 496.3026 | 896.2932 | 889.6345 | 644.2918 | 1.5142 | 1.4275 | 1.7128 | 1.7898 | 1.5236
7 | SH-15-ML | 07-SH-15-ML | 1740.3091 | 1079.722 | 1169.0442 | 1077.4196 | 1396.7538 | 672.856 | 503.535 | 914.5694 | 906.2707 | 655.2656 | 1.5622 | 1.4732 | 1.7678 | 1.8363 | 1.5716
7 | SH-15-MM | 07-SH-15-MM | 1790.956 | 1119.5702 | 1171.2696 | 1073.2112 | 1434.4771 | 665.1774 | 504.3927 | 897.3642 | 888.5661 | 648.8932 | 1.5293 | 1.484 | 1.7157 | 1.7874 | 1.551
7 | SH-16-CH | 07-SH-16-CH | 1903.9047 | 1176.2535 | 1258.5473 | 1153.4535 | 1522.3288 | 774.9724 | 576.4656 | 999.7268 | 979.1217 | 743.1734 | 1.6775 | 1.6122 | 1.9229 | 1.908 | 1.6973
7 | SH-16-CL | 07-SH-16-CL | 1821.3752 | 1130.5459 | 1238.8549 | 1139.1292 | 1464.5175 | 770.7013 | 572.3689 | 997.2479 | 976.0139 | 739.2464 | 1.6942 | 1.6288 | 1.9449 | 1.9324 | 1.715
7 | SH-16-LH | 07-SH-16-LH | 1993.1017 | 1218.547 | 1212.2281 | 1118.8184 | 1571.2535 | 732.0107 | 542.4837 | 916.6864 | 918.172 | 697.6067 | 1.5254 | 1.4167 | 1.6535 | 1.708 | 1.513
7 | SH-16-LL | 07-SH-16-LL | 1903.6397 | 1174.9921 | 1245.1363 | 1151.5509 | 1520.0686 | 767.3198 | 569.2056 | 983.0631 | 975.3699 | 734.8487 | 1.6396 | 1.5344 | 1.8042 | 1.859 | 1.635
7 | SH-16-LM | 07-SH-16-LM | 2019.1785 | 1238.5261 | 1259.0858 | 1163.6776 | 1598.7544 | 759.761 | 564.2938 | 965.1765 | 964.4635 | 726.8174 | 1.5828 | 1.4776 | 1.7304 | 1.7879 | 1.5753
7 | SH-16-TH | 07-SH-16-TH | 2134.424 | 1295.4628 | 1201.9272 | 1097.0533 | 1661.7395 | 729.0757 | 545.2884 | 881.4223 | 878.3557 | 690.6444 | 1.5698 | 1.4824 | 1.6967 | 1.7552 | 1.565
7 | SH-16-TL | 07-SH-16-TL | 2193.1701 | 1314.1013 | 1286.279 | 1171.5288 | 1710.1582 | 793.5596 | 583.9093 | 979.6374 | 964.4166 | 751.1938 | 1.7364 | 1.6043 | 1.8662 | 1.9382 | 1.717
7 | SH-16-TM | 07-SH-16-TM | 2210.9817 | 1322.1907 | 1281.4053 | 1166.0365 | 1720.4013 | 785.6313 | 577.7307 | 968.3366 | 954.7161 | 743.3847 | 1.7161 | 1.5823 | 1.8369 | 1.9113 | 1.6946
7 | SH-17-CM | 07-SH-17-CM | 1933.9551 | 1164.0767 | 1202.8346 | 1096.408 | 1521.8777 | 726.4216 | 539.6083 | 939.8293 | 920.4227 | 696.8339 | 1.5968 | 1.5362 | 1.8348 | 1.8223 | 1.6171
7 | SH-17-LM | 07-SH-17-LM | 1822.3381 | 1121.077 | 1165.6005 | 1080.5008 | 1449.3752 | 716.4059 | 531.1072 | 910.3419 | 908.2948 | 684.9487 | 1.5255 | 1.4137 | 1.6527 | 1.7169 | 1.5124
7 | SH-17-TH | 07-SH-17-TH | 2079.2779 | 1242.4414 | 1153.7147 | 1044.8699 | 1608.3463 | 682.522 | 503.1357 | 836.5561 | 829.6738 | 645.7251 | 1.4839 | 1.3716 | 1.5954 | 1.6551 | 1.4675
7 | SH-17-TL | 07-SH-17-TL | 2068.0269 | 1235.6456 | 1155.0831 | 1048.2693 | 1601.0704 | 686.5756 | 506.5233 | 843.5189 | 836.6985 | 650.0662 | 1.504 | 1.3933 | 1.6262 | 1.6881 | 1.4902
7 | SH-18-LH | 07-SH-18-LH | 1911.3736 | 1154.0502 | 1133.3465 | 1036.7296 | 1495.9799 | 667.9735 | 496.941 | 851.8367 | 847.112 | 639.6324 | 1.4371 | 1.3379 | 1.5695 | 1.6213 | 1.4287
7 | SH-18-LL | 07-SH-18-LL | 1817.7625 | 1114.0724 | 1149.7595 | 1056.9182 | 1441.4347 | 687.5803 | 513.0851 | 890.5618 | 881.9403 | 661.187 | 1.4831 | 1.3833 | 1.6304 | 1.6845 | 1.4773
7 | SH-18-LM | 07-SH-18-LM | 1980.2759 | 1189.8346 | 1152.8701 | 1051.0527 | 1543.9058 | 674.0301 | 501.2041 | 858.3111 | 852.6607 | 645.0668 | 1.4572 | 1.3598 | 1.5955 | 1.6431 | 1.4502
7 | SH-18-TM | 07-SH-18-TM | 1996.8472 | 1187.522 | 1084.3464 | 980.6458 | 1538.3842 | 635.7438 | 470.9227 | 779.4943 | 773.4178 | 602.3482 | 1.3933 | 1.2993 | 1.522 | 1.5851 | 1.3868
8 | SA-10-HH | 08-SA-10-HH | 1735.8992 | 1406.4554 | 2101.6797 | 2041.6091 | 1695.5506 | 1735.8992 | 1406.4554 | 2101.6797 | 2041.6091 | 1695.5506 | 3.2868 | 2.8776 | 3.1335 | 3.1312 | 3.1391
8 | SA-10-HL | 08-SA-10-HL | 1749.0612 | 1421.6302 | 2151.4819 | 2087.2182 | 1715.2067 | 1749.0612 | 1421.6302 | 2151.4819 | 2087.2182 | 1715.2067 | 3.587 | 3.1465 | 3.4263 | 3.424 | 3.4287
8 | SA-10-HM | 08-SA-10-HM | 1731.3505 | 1401.8356 | 2127.6874 | 2062.6827 | 1695.8047 | 1731.3505 | 1401.8356 | 2127.6874 | 2062.6827 | 1695.8047 | 3.459 | 3.0298 | 3.3012 | 3.296 | 3.3044
8 | SA-10-LH | 08-SA-10-LH | 1615.9815 | 1308.2121 | 2008.87 | 1945.2416 | 1586.4146 | 1615.9815 | 1308.2121 | 2008.87 | 1945.2416 | 1586.4146 | 3.2777 | 2.8541 | 3.1089 | 3.1076 | 3.1232
8 | SA-10-LL | 08-SA-10-LL | 1741.2689 | 1415.4055 | 2160.3134 | 2092.1434 | 1710.4267 | 1741.2689 | 1415.4055 | 2160.3134 | 2092.1434 | 1710.4267 | 3.4754 | 3.0575 | 3.3303 | 3.3288 | 3.3265
8 | SA-10-LM | 08-SA-10-LM | 1643.2635 | 1331.6334 | 2037.5196 | 1973.4998 | 1612.7528 | 1643.2635 | 1331.6334 | 2037.5196 | 1973.4998 | 1612.7528 | 3.3 | 2.8752 | 3.1269 | 3.1262 | 3.1444
8 | SA-10-MH | 08-SA-10-MH | 1635.4804 | 1319.9038 | 2006.0957 | 1944.5746 | 1599.9784 | 1635.4804 | 1319.9038 | 2006.0957 | 1944.5746 | 1599.9784 | 3.1831 | 2.7702 | 3.0124 | 3.0114 | 3.0315
8 | SA-10-ML | 08-SA-10-ML | 1775.2781 | 1442.7922 | 2188.3538 | 2122.0498 | 1741.5811 | 1775.2781 | 1442.7922 | 2188.3538 | 2122.0498 | 1741.5811 | 3.5195 | 3.0821 | 3.3559 | 3.3534 | 3.3617
8 | SA-10-MM | 08-SA-10-MM | 1598.9867 | 1304.4479 | 1994.3847 | 1931.3377 | 1573.8163 | 1598.9867 | 1304.4479 | 1994.3847 | 1931.3377 | 1573.8163 | 3.0851 | 2.8482 | 3.0688 | 3.0661 | 3.0117
8 | SA-13-HH | 08-SA-13-HH | 1313.1164 | 1067.9192 | 1631.5658 | 1606.3874 | 1292.1157 | 1313.1164 | 1067.9192 | 1631.5658 | 1606.3874 | 1292.1157 | 2.681 | 2.3557 | 2.5545 | 2.8832 | 2.5841
8 | SA-13-HL | 08-SA-13-HL | 1283.9409 | 1042.3912 | 1600.9513 | 1550.3589 | 1262.1499 | 1283.9409 | 1042.3912 | 1600.9513 | 1550.3589 | 1262.1499 | 2.8591 | 2.5356 | 2.7826 | 2.7813 | 2.7499
8 | SA-13-HM | 08-SA-13-HM | 1305.9731 | 1062.9292 | 1628.6977 | 1594.6486 | 1285.7622 | 1305.9731 | 1062.9292 | 1628.6977 | 1594.6486 | 1285.7622 | 2.7673 | 2.4612 | 2.6924 | 3.0012 | 2.6835
8 | SA-13-LH | 08-SA-13-LH | 1248.3008 | 1008.8223 | 1543.4188 | 1497.6453 | 1223.7525 | 1248.3008 | 1008.8223 | 1543.4188 | 1497.6453 | 1223.7525 | 2.5095 | 2.1988 | 2.3989 | 2.3975 | 2.3983
8 | SA-13-LL | 08-SA-13-LL | 1315.797 | 1068.6469 | 1629.7875 | 1579.1804 | 1291.8305 | 1315.797 | 1068.6469 | 1629.7875 | 1579.1804 | 1291.8305 | 2.6984 | 2.3703 | 2.5872 | 2.5857 | 2.582
8 | SA-13-LM | 08-SA-13-LM | 1289.095 | 1052.3356 | 1608.5685 | 1559.4425 | 1269.2381 | 1289.095 | 1052.3356 | 1608.5685 | 1559.4425 | 1269.2381 | 2.4634 | 2.2934 | 2.4972 | 2.4964 | 2.4184
8 | SA-13-MH | 08-SA-13-MH | 1248.5708 | 1013.5764 | 1534.238 | 1486.9525 | 1223.6695 | 1248.5708 | 1013.5764 | 1534.238 | 1486.9525 | 1223.6695 | 2.6081 | 2.3002 | 2.5115 | 2.5104 | 2.5002
8 | SA-13-ML | 08-SA-13-ML | 1291.7524 | 1051.6415 | 1610.0478 | 1558.7578 | 1270.5609 | 1291.7524 | 1051.6415 | 1610.0478 | 1558.7578 | 1270.5609 | 2.7686 | 2.4481 | 2.6781 | 2.6778 | 2.658
8 | SA-13-MM | 08-SA-13-MM | 1258.7479 | 1022.282 | 1545.4048 | 1516.1602 | 1234.7348 | 1258.7479 | 1022.282 | 1545.4048 | 1516.1602 | 1234.7348 | 2.6245 | 2.333 | 2.5594 | 2.8526 | 2.5457
8 | SA-14-HH | 08-SA-14-HH | 1250.0996 | 1016.5527 | 1552.6762 | 1503.7339 | 1228.3675 | 1250.0996 | 1016.5527 | 1552.6762 | 1503.7339 | 1228.3675 | 2.6422 | 2.3284 | 2.5433 | 2.5426 | 2.5322
8 | SA-14-HL | 08-SA-14-HL | 1190.3282 | 965.8857 | 1494.2149 | 1444.0821 | 1171.4492 | 1190.3282 | 965.8857 | 1494.2149 | 1444.0821 | 1171.4492 | 2.6113 | 2.332 | 2.565 | 2.5644 | 2.5203
8 | SA-14-HM | 08-SA-14-HM | 1192.1816 | 966.1137 | 1499.4293 | 1449.9841 | 1173.4286 | 1192.1816 | 966.1137 | 1499.4293 | 1449.9841 | 1173.4286 | 2.7189 | 2.3899 | 2.6198 | 2.6181 | 2.6042
8 | SA-14-MH | 08-SA-14-MH | 1226.3962 | 1001.385 | 1523.3868 | 1477.791 | 1206.4793 | 1226.3962 | 1001.385 | 1523.3868 | 1477.791 | 1206.4793 | 2.2816 | 2.1226 | 2.3097 | 2.3089 | 2.2389
8 | SA-14-ML | 08-SA-14-ML | 1195.7812 | 967.9997 | 1498.5693 | 1450.7932 | 1175.8752 | 1195.7812 | 967.9997 | 1498.5693 | 1450.7932 | 1175.8752 | 2.6083 | 2.3015 | 2.5172 | 2.5156 | 2.5016
8 | SA-14-MM | 08-SA-14-MM | 1191.6393 | 974.6287 | 1488.4474 | 1443.7734 | 1174.1316 | 1191.6393 | 974.6287 | 1488.4474 | 1443.7734 | 1174.1316 | 2.2928 | 2.1354 | 2.3249 | 2.324 | 2.2513
8 | SA-15-HH | 08-SA-15-HH | 1117.3222 | 909.4644 | 1384.4301 | 1362.1312 | 1098.9792 | 1117.3222 | 909.4644 | 1384.4301 | 1362.1312 | 1098.9792 | 2.3633 | 2.0962 | 2.2884 | 2.5514 | 2.2881
8 | SA-15-HL | 08-SA-15-HL | 1092.7004 | 891.1863 | 1368.4726 | 1338.0005 | 1077.1774 | 1092.7004 | 891.1863 | 1368.4726 | 1338.0005 | 1077.1774 | 2.4225 | 2.1607 | 2.3627 | 2.6296 | 2.3517
8 | SA-15-HM | 08-SA-15-HM | 1129.6893 | 919.8762 | 1403.6334 | 1377.1236 | 1111.6439 | 1129.6893 | 919.8762 | 1403.6334 | 1377.1236 | 1111.6439 | 2.3585 | 2.1025 | 2.3017 | 2.5628 | 2.2895
8 | SA-15-MH | 08-SA-15-MH | 1112.995 | 900.9385 | 1380.6897 | 1336.704 | 1092.1074 | 1112.995 | 900.9385 | 1380.6897 | 1336.704 | 1092.1074 | 2.4589 | 2.1719 | 2.3748 | 2.3755 | 2.3594
8 | SA-15-ML | 08-SA-15-ML | 1135.054 | 923.1479 | 1405.9498 | 1360.6516 | 1114.6654 | 1135.054 | 923.1479 | 1405.9498 | 1360.6516 | 1114.6654 | 2.4093 | 2.1259 | 2.3263 | 2.3249 | 2.3109
8 | SA-15-MM | 08-SA-15-MM | 1112.2133 | 900.1776 | 1389.2158 | 1345.2452 | 1092.8989 | 1112.2133 | 900.1776 | 1389.2158 | 1345.2452 | 1092.8989 | 2.4461 | 2.1601 | 2.3656 | 2.3647 | 2.3474
8 | SA-16-CH | 08-SA-16-CH | 1350.9978 | 1075.4914 | 1574.8975 | 1548.697 | 1305.0047 | 1350.9978 | 1075.4914 | 1574.8975 | 1548.697 | 1305.0047 | 2.6214 | 2.2987 | 2.4898 | 2.7585 | 2.5205
8 | SA-16-CL | 08-SA-16-CL | 1282.402 | 1026.3431 | 1509.0763 | 1473.3885 | 1242.0527 | 1282.402 | 1026.3431 | 1509.0763 | 1473.3885 | 1242.0527 | 2.5643 | 2.2682 | 2.4739 | 2.6719 | 2.4737
8 | SA-16-CM | 08-SA-16-CM | 1312.2149 | 1049.0692 | 1537.4738 | 1509.4747 | 1270.0129 | 1312.2149 | 1049.0692 | 1537.4738 | 1509.4747 | 1270.0129 | 2.5915 | 2.2897 | 2.4738 | 2.6997 | 2.4964
8 | SA-16-LH | 08-SA-16-LH | 1216.6568 | 976.6846 | 1418.1747 | 1377.7029 | 1176.5542 | 1216.6568 | 976.6846 | 1418.1747 | 1377.7029 | 1176.5542 | 2.3074 | 2.0489 | 2.25 | 2.2469 | 2.2206
8 | SA-16-LL | 08-SA-16-LL | 1277.9319 | 1024.5981 | 1490.6945 | 1449.0499 | 1235.67 | 1277.9319 | 1024.5981 | 1490.6945 | 1449.0499 | 1235.67 | 2.4839 | 2.2054 | 2.4172 | 2.4157 | 2.3897
8 | SA-16-LM | 08-SA-16-LM | 1268.0274 | 1016.9777 | 1485.4498 | 1443.7786 | 1227.2274 | 1268.0274 | 1016.9777 | 1485.4498 | 1443.7786 | 1227.2274 | 2.4367 | 2.1571 | 2.3621 | 2.3602 | 2.3408
8 | SA-16-NM | 08-SA-16-NM | 1189.6966 | 949.5891 | 1420.564 | 1374.8856 | 1154.1572 | 1189.6966 | 949.5891 | 1420.564 | 1374.8856 | 1154.1572 | 2.3247 | 2.0902 | 2.3016 | 2.2998 | 2.2509
8 | SA-16-TH | 08-SA-16-TH | 1384.0205 | 1091.0667 | 1530.3042 | 1487.0305 | 1318.6796 | 1384.0205 | 1091.0667 | 1530.3042 | 1487.0305 | 1318.6796 | 2.6781 | 2.3692 | 2.5882 | 2.5853 | 2.5709
8 | SA-16-TL | 08-SA-16-TL | 1333.672 | 1051.5055 | 1487.0342 | 1451.0907 | 1273.203 | 1333.672 | 1051.5055 | 1487.0342 | 1451.0907 | 1273.203 | 2.5821 | 2.3105 | 2.5354 | 2.7893 | 2.5097
8 | SA-17-CH | 08-SA-17-CH | 1239.9151 | 992.7219 | 1462.3427 | 1433.3527 | 1201.9199 | 1239.9151 | 992.7219 | 1462.3427 | 1433.3527 | 1201.9199 | 2.4718 | 2.1766 | 2.3673 | 2.6284 | 2.3832
8 | SA-17-CL | 08-SA-17-CL | 1243.9439 | 996.9452 | 1471.2059 | 1436.8172 | 1206.473 | 1243.9439 | 996.9452 | 1471.2059 | 1436.8172 | 1206.473 | 2.5049 | 2.2167 | 2.4183 | 2.6659 | 2.4205
8 | SA-17-CM | 08-SA-17-CM | 1263.6266 | 1007.6178 | 1477.2451 | 1446.2712 | 1221.3986 | 1263.6266 | 1007.6178 | 1477.2451 | 1446.2712 | 1221.3986 | 2.499 | 2.2095 | 2.4058 | 2.666 | 2.4139
8 | SA-17-LH | 08-SA-17-LH | 1165.2326 | 937.3287 | 1367.0831 | 1326.6697 | 1128.7808 | 1165.2326 | 937.3287 | 1367.0831 | 1326.6697 | 1128.7808 | 2.2684 | 2.0049 | 2.1958 | 2.1943 | 2.1777
8 | SA-17-LL | 08-SA-17-LL | 1221.0773 | 976.2987 | 1419.7095 | 1382.2888 | 1179.2552 | 1221.0773 | 976.2987 | 1419.7095 | 1382.2888 | 1179.2552 | 2.3933 | 2.1224 | 2.3231 | 2.3218 | 2.3008
8 | SA-17-LM | 08-SA-17-LM | 1219.9032 | 979.5437 | 1428.113 | 1386.6203 | 1180.7457 | 1219.9032 | 979.5437 | 1428.113 | 1386.6203 | 1180.7457 | 2.3753 | 2.1096 | 2.3131 | 2.3124 | 2.2857
8 | SA-17-TH | 08-SA-17-TH | 1161.9276 | 925.1563 | 1312.1548 | 1275.5473 | 1114.3963 | 1161.9276 | 925.1563 | 1312.1548 | 1275.5473 | 1114.3963 | 2.2967 | 2.0285 | 2.2124 | 2.211 | 2.2026
8 | SA-17-TL | 08-SA-17-TL | 1125.0168 | 904.8979 | 1308.3821 | 1267.054 | 1087.7126 | 1125.0168 | 904.8979 | 1308.3821 | 1267.054 | 1087.7126 | 2.3975 | 2.1094 | 2.3243 | 2.3078 | 2.2984
8 | SA-17-TM | 08-SA-17-TM | 1317.6626 | 1031.0077 | 1428.8256 | 1403.8532 | 1249.4632 | 1317.6626 | 1031.0077 | 1428.8256 | 1403.8532 | 1249.4632 | 2.3902 | 2.1132 | 2.2867 | 2.5324 | 2.3062
8 | SA-18-LH | 08-SA-18-LH | 1144.2584 | 917.1205 | 1328.0584 | 1290.9547 | 1105.2103 | 1144.2584 | 917.1205 | 1328.0584 | 1290.9547 | 1105.2103 | 2.212 | 1.9651 | 2.1553 | 2.1541 | 2.1289
8 | SA-18-LL | 08-SA-18-LL | 1113.2604 | 894.6536 | 1311.0344 | 1271.7361 | 1078.9609 | 1113.2604 | 894.6536 | 1311.0344 | 1271.7361 | 1078.9609 | 2.2218 | 1.9726 | 2.1641 | 2.162 | 2.1378
8 | SA-18-TH | 08-SA-18-TH | 1131.2291 | 897.718 | 1263.4445 | 1257.3015 | 1083.5955 | 1131.2291 | 897.718 | 1263.4445 | 1257.3015 | 1083.5955 | 2.1756 | 1.9298 | 2.1088 | 2.3327 | 2.1056
8 | SA-18-TL | 08-SA-18-TL | 1196.9718 | 949.2838 | 1335.8669 | 1303.334 | 1144.5474 | 1196.9718 | 949.2838 | 1335.8669 | 1303.334 | 1144.5474 | 2.3705 | 2.0774 | 2.2474 | 2.2464 | 2.2625
8 | SA-18-TM | 08-SA-18-TM | 1158.9333 | 919.8766 | 1308.3937 | 1273.7183 | 1110.7171 | 1158.9333 | 919.8766 | 1308.3937 | 1273.7183 | 1110.7171 | 2.2653 | 2.0017 | 2.1832 | 2.1811 | 2.1729
8 | SH-10-HH | 08-SH-10-HH | 3157.6619 | 2236.525 | 2525.6988 | 2380.5359 | 2867.126 | 1640.6575 | 1330.4443 | 2027.8241 | 2003.9425 | 1618.126 | 3.2854 | 2.9022 | 3.1605 | 3.5435 | 3.2056
8 | SH-10-HL | 08-SH-10-HL | 3239.5372 | 2301.4503 | 2612.0646 | 2453.7329 | 2945.0718 | 1700.5494 | 1382.1703 | 2109.1538 | 2075.2299 | 1678.2997 | 3.4556 | 3.0444 | 3.3167 | 3.7248 | 3.3693
8 | SH-10-HM | 08-SH-10-HM | 3155.3606 | 2254.0744 | 2551.7228 | 2364.1974 | 2870.4277 | 1682.3207 | 1364.6932 | 2057.9307 | 1994.6867 | 1654.5787 | 3.3509 | 2.9373 | 3.203 | 3.2001 | 3.2406
8 | SH-10-LH | 08-SH-10-LH | 3242.0963 | 2269.1473 | 2514.9879 | 2326.4998 | 2925.9625 | 1632.1229 | 1316.5612 | 1993.4521 | 1935.9493 | 1603.3917 | 3.1252 | 2.7251 | 2.9645 | 2.9628 | 3.0164
8 | SH-10-LL | 08-SH-10-LL | 3202.5102 | 2277.937 | 2586.555 | 2396.7572 | 2910.7592 | 1684.6892 | 1365.9206 | 2083.8354 | 2019.9261 | 1659.5584 | 3.3406 | 2.938 | 3.2058 | 3.2045 | 3.2344
8 | SH-10-LM | 08-SH-10-LM | 3165.0535 | 2249.682 | 2538.6538 | 2354.1953 | 2874.3506 | 1664.1964 | 1346.4571 | 2038.4253 | 1978.8168 | 1636.4568 | 3.1992 | 2.8172 | 3.0744 | 3.0736 | 3.0989
8 | SH-10-MH | 08-SH-10-MH | 3213.4319 | 2258.5049 | 2517.589 | 2330.4935 | 2905.2335 | 1631.2341 | 1319.0422 | 2003.8856 | 1945.6092 | 1604.6055 | 3.2283 | 2.8156 | 3.064 | 3.0623 | 3.1162
8 | SH-10-ML | 08-SH-10-ML | 3104.7435 | 2227.3334 | 2571.5142 | 2388.135 | 2834.0216 | 1689.2421 | 1372.2682 | 2098.7796 | 2033.3787 | 1665.7101 | 3.4935 | 3.0868 | 3.3745 | 3.3733 | 3.3883
8 | SH-10-MM | 08-SH-10-MM | 3230.0068 | 2308.5266 | 2587.4638 | 2397.8215 | 2935.6746 | 1702.2946 | 1390.1564 | 2083.0088 | 2020.7501 | 1676.4554 | 3.1101 | 2.8808 | 3.1157 | 3.1132 | 3.0597
8 | SH-13-HH | 08-SH-13-HH | 2781.1286 | 1941.0558 | 2104.6396 | 1967.4692 | 2503.5581 | 1323.439 | 1073.2484 | 1626.9862 | 1606.4166 | 1304.1228 | 2.7602 | 2.4374 | 2.656 | 2.9739 | 2.6929
8 | SH-13-HL | 08-SH-13-HL | 2547.2078 | 1800.8852 | 2033.8595 | 1888.6868 | 2310.1505 | 1285.8505 | 1046.5627 | 1619.5017 | 1577.8829 | 1271.5251 | 2.7998 | 2.499 | 2.7348 | 3.0474 | 2.7419
8 | SH-13-HM | 08-SH-13-HM | 2614.8689 | 1846.2458 | 2049.84 | 1919.3222 | 2367.2804 | 1318.1276 | 1069.9189 | 1621.062 | 1596.1823 | 1298.9423 | 2.7358 | 2.4219 | 2.6434 | 2.9574 | 2.6717
8 | SH-13-LH | 08-SH-13-LH | 2787.5283 | 1916.3108 | 2034.1552 | 1867.9103 | 2491.9788 | 1254.4431 | 1014.3009 | 1551.6445 | 1505.8977 | 1235.2108 | 2.5467 | 2.2258 | 2.4249 | 2.4244 | 2.4603
8 | SH-13-LL | 08-SH-13-LL | 2578.8045 | 1803.39 | 1966.7577 | 1810.4489 | 2322.5102 | 1247.0208 | 1011.4399 | 1533.374 | 1485.8898 | 1227.3709 | 2.5718 | 2.2803 | 2.4958 | 2.4951 | 2.4976
8 | SH-13-LM | 08-SH-13-LM | 2478.7658 | 1764.3478 | 2011.822 | 1864.3571 | 2254.3958 | 1300.2476 | 1061.7881 | 1629.2337 | 1578.127 | 1285.016 | 2.5209 | 2.3484 | 2.5573 | 2.5567 | 2.487
8 | SH-13-MH | 08-SH-13-MH | 2691.0902 | 1860.5847 | 1980.9867 | 1849.8238 | 2411.8294 | 1220.1714 | 986.9743 | 1501.1894 | 1484.9001 | 1202.0882 | 2.556 | 2.2554 | 2.4372 | 2.7122 | 2.4895
8 | SH-13-ML | 08-SH-13-ML | 2706.7672 | 1886.6455 | 2079.5633 | 1914.7456 | 2438.2047 | 1316.4449 | 1069.604 | 1638.3402 | 1585.5974 | 1298.3873 | 2.8311 | 2.4838 | 2.7115 | 2.7108 | 2.7391
8 | SH-13-MM | 08-SH-13-MM | 2641.7042 | 1851.508 | 2023.9031 | 1860.0941 | 2381.0074 | 1274.3031 | 1032.8306 | 1573.7362 | 1523.4215 | 1254.8021 | 2.735 | 2.4212 | 2.6512 | 2.6497 | 2.6548
8 | SH-14-HH | 08-SH-14-HH | 2580.6835 | 1810.248 | 1982.3687 | 1851.5515 | 2328.5731 | 1252.0303 | 1017.3181 | 1545.7052 | 1522.0349 | 1234.7695 | 2.651 | 2.3446 | 2.5566 | 2.8602 | 2.5877
8 | SH-14-HL | 08-SH-14-HL | 2552.3516 | 1791.6072 | 1974.6204 | 1834.2573 | 2304.4141 | 1241.2622 | 1011.368 | 1547.669 | 1513.9772 | 1226.0973 | 2.6468 | 2.35 | 2.567 | 2.8643 | 2.5872
8 | SH-14-HM | 08-SH-14-HM | 2534.6315 | 1778.857 | 1961.8091 | 1833.0649 | 2289.0348 | 1242.466 | 1008.5824 | 1538.0144 | 1512.9722 | 1225.5458 | 2.5632 | 2.2702 | 2.4765 | 2.7606 | 2.5028
8 | SH-14-MH | 08-SH-14-MH | 2552.3027 | 1767.2717 | 1898.3058 | 1744.8556 | 2288.8553 | 1165.7523 | 952.6919 | 1458.1807 | 1414.6351 | 1152.0712 | 2.2313 | 2.0798 | 2.2659 | 2.2655 | 2.2019
8 | SH-14-ML | 08-SH-14-ML | 2623.2072 | 1790.812 | 1912.4578 | 1763.8632 | 2342.4998 | 1162.2065 | 939.4111 | 1459.9924 | 1424.2338 | 1147.4447 | 2.5569 | 2.2594 | 2.4719 | 2.7631 | 2.4961
8 | SH-14-MM | 08-SH-14-MM | 2464.5989 | 1716.4613 | 1898.8095 | 1749.3405 | 2220.441 | 1186.8632 | 960.3078 | 1486.8712 | 1441.0032 | 1170.9904 | 2.5066 | 2.2147 | 2.4224 | 2.4218 | 2.4313
8 | SH-15-HH | 08-SH-15-HH | 2695.8853 | 1844.6829 | 1894.7044 | 1752.954 | 2400.2226 | 1144.8767 | 930.3898 | 1412.7098 | 1389.7844 | 1128.9669 | 2.3569 | 2.0903 | 2.2802 | 2.5421 | 2.3024
8 | SH-15-HL | 08-SH-15-HL | 2278.1631 | 1613.7895 | 1808.4222 | 1686.4106 | 2065.955 | 1154.8734 | 940.1005 | 1436.7997 | 1406.9331 | 1140.2601 | 2.439 | 2.1704 | 2.3753 | 2.6602 | 2.3869
8 | SH-15-HM | 08-SH-15-HM | 2259.8565 | 1587.253 | 1756.7122 | 1631.8722 | 2041.5481 | 1093.0196 | 888.2348 | 1369.4033 | 1339.8614 | 1079.961 | 2.3863 | 2.1193 | 2.2969 | 2.5531 | 2.3298
8 | SH-15-MH | 08-SH-15-MH | 2472.3008 | 1684.3949 | 1786.3624 | 1634.1886 | 2204.3466 | 1089.1032 | 882.4881 | 1358.919 | 1315.0715 | 1074.0512 | 2.467 | 2.1764 | 2.3858 | 2.3848 | 2.3923
8 | SH-15-ML | 08-SH-15-ML | 2365.3268 | 1628.8202 | 1773.0698 | 1640.2263 | 2121.395 | 1090.7802 | 882.6482 | 1371.0311 | 1338.5364 | 1077.2938 | 2.415 | 2.144 | 2.3513 | 2.6199 | 2.3615
8 | SH-15-MM | 08-SH-15-MM | 2431.161 | 1682.3818 | 1793.0513 | 1656.879 | 2178.6686 | 1090.4122 | 887.5734 | 1360.841 | 1330.8553 | 1077.0281 | 2.3814 | 2.1172 | 2.3013 | 2.5477 | 2.3262
8 | SH-16-CH | 08-SH-16-CH | 2686.0069 | 1845.5792 | 1942.8087 | 1816.6329 | 2400.7321 | 1314.8994 | 1047.9873 | 1528.4032 | 1504.5106 | 1280.5871 | 2.5394 | 2.249 | 2.4541 | 2.6872 | 2.477
8 | SH-16-CL | 08-SH-16-CL | 2595.3212 | 1794.3667 | 1924.0214 | 1800.2042 | 2327.811 | 1318.1696 | 1050.4795 | 1535.4089 | 1508.5282 | 1283.9824 | 2.6108 | 2.2916 | 2.4798 | 2.7421 | 2.538
8 | SH-16-LH | 08-SH-16-LH | 2702.5101 | 1834.113 | 1847.4964 | 1696.6088 | 2395.8936 | 1204.4715 | 966.7732 | 1396.1523 | 1358.8309 | 1173.2337 | 2.2976 | 2.0391 | 2.2365 | 2.2353 | 2.2326
8 | SH-16-LL | 08-SH-16-LL | 2635.7917 | 1810.7734 | 1903.4661 | 1756.9287 | 2354.1764 | 1268.7678 | 1019.9706 | 1492.8265 | 1450.2709 | 1238.7694 | 2.4869 | 2.1982 | 2.406 | 2.404 | 2.4126
8 | SH-16-LM | 08-SH-16-LM | 2759.0795 | 1877.6051 | 1916.1745 | 1760.0711 | 2450.7653 | 1255.2533 | 1007.6014 | 1466.2587 | 1424.1965 | 1223.9274 | 2.4052 | 2.1231 | 2.321 | 2.3198 | 2.3321
8 | SH-16-TH | 08-SH-16-TH | 2953.8413 | 1980.5103 | 1903.6636 | 1762.4446 | 2600.3688 | 1245.1967 | 989.7361 | 1396.9655 | 1378.1577 | 1206.0966 | 2.4915 | 2.2202 | 2.4334 | 2.6618 | 2.4365
8 | SH-16-TL | 08-SH-16-TL | 3093.347 | 2078.1924 | 2054.2726 | 1890.3375 | 2730.7125 | 1386.8101 | 1096.3367 | 1556.637 | 1517.0016 | 1341.0217 | 2.7222 | 2.3949 | 2.6139 | 2.6102 | 2.6359
8 | SH-16-TM | 08-SH-16-TM | 3103.4591 | 2081.7096 | 2043.1134 | 1876.7511 | 2736.6049 | 1370.9123 | 1083.8405 | 1536.8369 | 1497.2706 | 1325.4029 | 2.6666 | 2.3471 | 2.5611 | 2.5575 | 2.5824
8 | SH-17-CM | 08-SH-17-CM | 2688.9656 | 1812.0545 | 1864.8596 | 1734.4832 | 2385.3803 | 1243.7408 | 991.9475 | 1449.3216 | 1424.0801 | 1211.7393 | 2.4744 | 2.172 | 2.3485 | 2.5938 | 2.405
8 | SH-17-LM | 08-SH-17-LM | 2536.926 | 1736.4496 | 1804.4798 | 1667.8558 | 2261.2896 | 1211.0835 | 970.1671 | 1405.0895 | 1369.4849 | 1179.5102 | 2.3219 | 2.0614 | 2.2537 | 2.2538 | 2.2556
8 | SH-17-TH | 08-SH-17-TH | 2870.7545 | 1919.2428 | 1828.9065 | 1687.8002 | 2523.165 | 1169.8684 | 931.1541 | 1323.9624 | 1305.8128 | 1134.8132 | 2.3471 | 2.0804 | 2.2755 | 2.5066 | 2.2916
8 | SH-17-TL | 08-SH-17-TL | 2869.2654 | 1919.011 | 1836.9638 | 1693.6927 | 2523.0145 | 1181.0333 | 940.7004 | 1338.6254 | 1317.4077 | 1145.8828 | 2.3935 | 2.1264 | 2.3258 | 2.5656 | 2.3388
8 | SH-18-LH | 08-SH-18-LH | 2641.7014 | 1776.4657 | 1753.2041 | 1603.5785 | 2331.729 | 1121.5977 | 900.9487 | 1309.453 | 1272.4076 | 1093.6932 | 2.2569 | 1.99 | 2.1742 | 2.173 | 2.1873
8 | SH-18-LL | 08-SH-18-LL | 2524.5388 | 1721.603 | 1772.6133 | 1630.2507 | 2245.643 | 1155.8282 | 930.3035 | 1365.1042 | 1326.1856 | 1129.3784 | 2.345 | 2.0682 | 2.2595 | 2.2586 | 2.2729
8 | SH-18-LM | 08-SH-18-LM | 2740.7108 | 1832.7213 | 1788.6494 | 1632.7185 | 2413.0575 | 1137.8544 | 910.1819 | 1323.8308 | 1286.5751 | 1108.1456 | 2.2691 | 2.0073 | 2.1953 | 2.1944 | 2.2017
8 | SH-18-TM | 08-SH-18-TM | 2765.381 | 1853.5402 | 1748.6337 | 1592.3851 | 2428.8812 | 1089.6374 | 882.7341 | 1257.5821 | 1223.3965 | 1062.4896 | 2.1896 | 2.0303 | 2.1566 | 2.1635 | 2.1505
9 | SA-10-HH | 09-SA-10-HH | 2136.827 | 2124.0586 | 2553.2685 | 2709.8769 | 2182.0931 | 2136.827 | 2124.0586 | 2553.2685 | 2709.8769 | 2182.0931 | 4.052 | 3.7207 | 4.0239 | 4.4629 | 3.9756
9 | SA-10-HL | 09-SA-10-HL | 2199.01 | 2199.5187 | 2702.8055 | 2847.8725 | 2256.6129 | 2199.01 | 2199.5187 | 2702.8055 | 2847.8725 | 2256.6129 | 4.4226 | 4.0629 | 4.7493 | 5.1118 | 4.3739
9 | SA-10-HM | 09-SA-10-HM | 2146.5669 | 2145.2312 | 2647.4796 | 2790.6782 | 2203.3279 | 2146.5669 | 2145.2312 | 2647.4796 | 2790.6782 | 2203.3279 | 3.8975 | 3.5824 | 4.2364 | 4.5883 | 3.8614
9 | SA-10-LH | 09-SA-10-LH | 1970.3421 | 1974.26 | 2450.2087 | 2590.3906 | 2026.1663 | 1970.3421 | 1974.26 | 2450.2087 | 2590.3906 | 2026.1663 | 3.8101 | 3.5381 | 3.887 | 4.315 | 3.7599
9 | SA-10-LL | 09-SA-10-LL | 2140.4288 | 2145.3149 | 2646.66 | 2789.4987 | 2199.3659 | 2140.4288 | 2145.3149 | 2646.66 | 2789.4987 | 2199.3659 | 4.2202 | 3.8882 | 4.5596 | 4.8991 | 4.1794
9 | SA-10-LM | 09-SA-10-LM | 1996.7426 | 1998.4734 | 2466.2434 | 2606.0768 | 2050.8916 | 1996.7426 | 1998.4734 | 2466.2434 | 2606.0768 | 2050.8916 | 3.8917 | 3.6029 | 3.9376 | 4.3676 | 3.8339
9 | SA-10-MH | 09-SA-10-MH | 1999.1179 | 1999.585 | 2465.4093 | 2615.0749 | 2052.8923 | 1999.1179 | 1999.585 | 2465.4093 | 2615.0749 | 2052.8923 | 3.7308 | 3.4579 | 3.7901 | 4.2129 | 3.6784
9 | SA-10-ML | 09-SA-10-ML | 2196.887 | 2198.8565 | 2685.2427 | 2849.993 | 2253.8322 | 2196.887 | 2198.8565 | 2685.2427 | 2849.993 | 2253.8322 | 4.2804 | 3.9429 | 4.2554 | 5.015 | 4.2123
9 | SA-10-MM | 09-SA-10-MM | 1961.1061 | 1974.5995 | 2447.1734 | 2580.9254 | 2019.8942 | 1961.1061 | 1974.5995 | 2447.1734 | 2580.9254 | 2019.8942 | 3.665 | 3.5985 | 3.9413 | 4.3658 | 3.6894
9 | SA-13-HH | 09-SA-13-HH | 1637.5736 | 1642.5311 | 2040.6451 | 2155.1132 | 1684.8014 | 1637.5736 | 1642.5311 | 2040.6451 | 2155.1132 | 1684.8014 | 3.2914 | 3.0532 | 3.6172 | 3.892 | 3.2717
9 | SA-13-HL | 09-SA-13-HL | 1586.8768 | 1588.2007 | 1976.6912 | 2076.7701 | 1631.3265 | 1586.8768 | 1588.2007 | 1976.6912 | 2076.7701 | 1631.3265 | 3.3745 | 3.1463 | 3.732 | 3.9892 | 3.3602
9 | SA-13-HM | 09-SA-13-HM | 1625.1345 | 1642.1827 | 2026.6987 | 2133.5288 | 1675.1345 | 1625.1345 | 1642.1827 | 2026.6987 | 2133.5288 | 1675.1345 | 3.4098 | 3.284 | 3.6684 | 3.9379 | 3.4123
9 | SA-13-LH | 09-SA-13-LH | 1523.5495 | 1526.3436 | 1910.5797 | 2015.6331 | 1568.2386 | 1523.5495 | 1526.3436 | 1910.5797 | 2015.6331 | 1568.2386 | 2.9691 | 2.7621 | 3.2861 | 3.529 | 2.9557
9 | SA-13-LL | 09-SA-13-LL | 1607.0669 | 1612.8042 | 1981.8292 | 2088.7041 | 1651.2858 | 1607.0669 | 1612.8042 | 1981.8292 | 2088.7041 | 1651.2858 | 3.2389 | 3.0114 | 3.2994 | 3.6524 | 3.1964
9 | SA-13-LM | 09-SA-13-LM | 1586.5157 | 1591.6022 | 1966.8847 | 2078.0782 | 1631.285 | 1586.5157 | 1591.6022 | 1966.8847 | 2078.0782 | 1631.285 | 3.0912 | 2.8737 | 3.1617 | 3.5084 | 3.0521
9 | SA-13-MH | 09-SA-13-MH | 1565.6586 | 1563.636 | 1940.7898 | 2045.8663 | 1607.8348 | 1565.6586 | 1563.636 | 1940.7898 | 2045.8663 | 1607.8348 | 3.0515 | 2.8285 | 3.3419 | 3.59 | 3.0313
9 | SA-13-ML | 09-SA-13-ML | 1603.0164 | 1604.5454 | 1964.4116 | 2080.5914 | 1645.0042 | 1603.0164 | 1604.5454 | 1964.4116 | 2080.5914 | 1645.0042 | 3.3377 | 3.1072 | 3.3938 | 3.9095 | 3.2988
9 | SA-13-MM | 09-SA-13-MM | 1557.2208 | 1555.8848 | 1907.8255 | 2009.8308 | 1596.8979 | 1557.2208 | 1555.8848 | 1907.8255 | 2009.8308 | 1596.8979 | 3.2241 | 2.9989 | 3.5187 | 3.7678 | 3.2038
9 | SA-14-HH | 09-SA-14-HH | 1564.4 | 1567.7638 | 1924.4302 | 2034.2378 | 1606.5327 | 1564.4 | 1567.7638 | 1924.4302 | 2034.2378 | 1606.5327 | 3.1768 | 2.9527 | 3.241 | 3.5997 | 3.1357
9 | SA-14-HL | 09-SA-14-HL | 1482.7665 | 1487.8582 | 1855.672 | 1952.1209 | 1526.309 | 1482.7665 | 1487.8582 | 1855.672 | 1952.1209 | 1526.309 | 3.1624 | 2.9209 | 3.4349 | 3.6991 | 3.1359
9 | SA-14-HM | 09-SA-14-HM | 1489.2302 | 1495.3476 | 1883.2273 | 1979.092 | 1535.2476 | 1489.2302 | 1495.3476 | 1883.2273 | 1979.092 | 1535.2476 | 3.1193 | 2.9172 | 3.4834 | 3.7415 | 3.1126
9 | SA-14-MH | 09-SA-14-MH | 1516.5389 | 1519.9885 | 1869.5008 | 1978.9529 | 1557.938 | 1516.5389 | 1519.9885 | 1869.5008 | 1978.9529 | 1557.938 | 2.8857 | 2.6805 | 2.9408 | 3.2699 | 2.8477
9 | SA-14-ML | 09-SA-14-ML | 1472.1053 | 1477.3168 | 1850.7435 | 1946.5782 | 1516.2653 | 1472.1053 | 1477.3168 | 1850.7435 | 1946.5782 | 1516.2653 | 3.0459 | 2.8442 | 3.3942 | 3.6384 | 3.0372
9 | SA-14-MM | 09-SA-14-MM | 1462.495 | 1482.8067 | 1831.6696 | 1935.9211 | 1509.8548 | 1462.495 | 1482.8067 | 1831.6696 | 1935.9211 | 1509.8548 | 2.7004 | 2.6897 | 2.9591 | 3.2841 | 2.7346
9 | SA-15-HH | 09-SA-15-HH | 1414.9477 | 1429.6618 | 1764.8512 | 1860.1796 | 1458.5455 | 1414.9477 | 1429.6618 | 1764.8512 | 1860.1796 | 1458.5455 | 2.9122 | 2.7867 | 3.1178 | 3.3515 | 2.9081
9 | SA-15-HL | 09-SA-15-HL | 1371.9728 | 1383.9926 | 1716.6684 | 1806.5877 | 1414.1555 | 1371.9728 | 1383.9926 | 1716.6684 | 1806.5877 | 1414.1555 | 2.8719 | 2.7754 | 3.1344 | 3.3641 | 2.8812
9 | SA-15-HM | 09-SA-15-HM | 1415.1795 | 1425.7646 | 1757.2272 | 1852.3385 | 1456.8633 | 1415.1795 | 1425.7646 | 1757.2272 | 1852.3385 | 1456.8633 | 2.7827 | 2.669 | 3.0125 | 3.2388 | 2.784
9 | SA-15-MH | 09-SA-15-MH | 1395.6735 | 1399.2203 | 1733.618 | 1847.766 | 1435.6547 | 1395.6735 | 1399.2203 | 1733.618 | 1847.766 | 1435.6547 | 2.8645 | 2.6834 | 2.9872 | 3.4534 | 2.8441
9 | SA-15-ML | 09-SA-15-ML | 1398.1646 | 1403.7516 | 1725.4418 | 1827.576 | 1437.1946 | 1398.1646 | 1403.7516 | 1725.4418 | 1827.576 | 1437.1946 | 2.8875 | 2.6908 | 2.9536 | 3.397 | 2.8563
9 | SA-15-MM | 09-SA-15-MM | 1370.1315 | 1373.7733 | 1721.5476 | 1809.2076 | 1410.7659 | 1370.1315 | 1373.7733 | 1721.5476 | 1809.2076 | 1410.7659 | 2.8539 | 2.6697 | 3.176 | 3.3947 | 2.8463
9 | SA-16-CH | 09-SA-16-CH | 1734.8154 | 1683.1002 | 1965.8968 | 2070.4969 | 1748.7996 | 1734.8154 | 1683.1002 | 1965.8968 | 2070.4969 | 1748.7996 | 3.1319 | 2.8877 | 3.4127 | 3.6719 | 3.1055
9 | SA-16-CL | 09-SA-16-CL | 1648.9591 | 1606.0359 | 1862.3364 | 1962.8728 | 1663.2523 | 1648.9591 | 1606.0359 | 1862.3364 | 1962.8728 | 1663.2523 | 3.1686 | 3.0165 | 3.3024 | 3.5312 | 3.1498
9 | SA-16-CM | 09-SA-16-CM | 1696.3285 | 1655.799 | 1924.692 | 2029.0922 | 1712.9433 | 1696.3285 | 1655.799 | 1924.692 | 2029.0922 | 1712.9433 | 3.1672 | 3.04 | 3.406 | 3.6564 | 3.1666
9 | SA-16-LH | 09-SA-16-LH | 1525.1524 | 1488.7267 | 1741.227 | 1867.3838 | 1542.1945 | 1525.1524 | 1488.7267 | 1741.227 | 1867.3838 | 1542.1945 | 2.8407 | 2.6114 | 2.8388 | 3.2717 | 2.7936
9 | SA-16-LL | 09-SA-16-LL | 1614.0883 | 1580.7671 | 1838.6927 | 1942.6042 | 1632.1758 | 1614.0883 | 1580.7671 | 1838.6927 | 1942.6042 | 1632.1758 | 3.154 | 2.9058 | 3.1529 | 3.4619 | 3.0983
9 | SA-16-LM | 09-SA-16-LM | 1594.9315 | 1561.8752 | 1829.7693 | 1932.7712 | 1614.1402 | 1594.9315 | 1561.8752 | 1829.7693 | 1932.7712 | 1614.1402 | 3.0448 | 2.8028 | 3.0328 | 3.3386 | 2.9894
9 | SA-16-NM | 09-SA-16-NM | 1464.4816 | 1425.8902 | 1666.7891 | 1754.4272 | 1478.3536 | 1464.4816 | 1425.8902 | 1666.7891 | 1754.4272 | 1478.3536 | 2.8029 | 2.5634 | 2.7395 | 3.0272 | 2.7422
9 | SA-16-TH | 09-SA-16-TH | 1839.0501 | 1757.7865 | 1977.7179 | 2125.0799 | 1836.8457 | 1839.0501 | 1757.7865 | 1977.7179 | 2125.0799 | 1836.8457 | 3.2947 | 3.0431 | 3.301 | 3.7966 | 3.2444
9 | SA-16-TL | 09-SA-16-TL | 1712.6855 | 1632.9553 | 1847.6672 | 1947.2077 | 1709.0626 | 1712.6855 | 1632.9553 | 1847.6672 | 1947.2077 | 1709.0626 | 2.9242 | 2.6909 | 3.1649 | 3.4111 | 2.896
9 | SA-17-CH | 09-SA-17-CH | 1599.8057 | 1554.6781 | 1819.9785 | 1916.5203 | 1614.12 | 1599.8057 | 1554.6781 | 1819.9785 | 1916.5203 | 1614.12 | 2.99 | 2.7573 | 3.2493 | 3.4966 | 2.9639
9 | SA-17-CL | 09-SA-17-CL | 1602.4613 | 1555.9197 | 1816.0416 | 1911.5455 | 1615.6798 | 1602.4613 | 1555.9197 | 1816.0416 | 1911.5455 | 1615.6798 | 3.0474 | 2.8093 | 3.2958 | 3.5384 | 3.0187
9 | SA-17-CM | 09-SA-17-CM | 1627.4218 | 1576.1346 | 1831.9707 | 1929.8489 | 1638.5187 | 1627.4218 | 1576.1346 | 1831.9707 | 1929.8489 | 1638.5187 | 3.0325 | 2.7957 | 3.2848 | 3.5318 | 3.0046
9 | SA-17-LH | 09-SA-17-LH | 1471.1015 | 1438.9724 | 1686.829 | 1783.4473 | 1488.3462 | 1471.1015 | 1438.9724 | 1686.829 | 1783.4473 | 1488.3462 | 2.7953 | 2.5609 | 2.7697 | 3.0534 | 2.7398
9 | SA-17-LL | 09-SA-17-LL | 1547.3372 | 1514.4805 | 1758.5415 | 1856.5109 | 1563.9551 | 1547.3372 | 1514.4805 | 1758.5415 | 1856.5109 | 1563.9551 | 3.0128 | 2.7743 | 3.0066 | 3.3087 | 2.9588
9 | SA-17-LM | 09-SA-17-LM | 1534.3193 | 1505.6192 | 1760.9573 | 1860.3517 | 1553.6937 | 1534.3193 | 1505.6192 | 1760.9573 | 1860.3517 | 1553.6937 | 2.9089 | 2.6806 | 2.9105 | 3.2005 | 2.8581
9 | SA-17-TH | 09-SA-17-TH | 1527.5172 | 1482.4595 | 1701.0269 | 1834.2824 | 1538.0269 | 1527.5172 | 1482.4595 | 1701.0269 | 1834.2824 | 1538.0269 | 2.7298 | 2.529 | 2.7565 | 3.2089 | 2.6937
9 | SA-17-TL | 09-SA-17-TL | 1449.3578 | 1399.3589 | 1612.5003 | 1697.3097 | 1456.0337 | 1449.3578 | 1399.3589 | 1612.5003 | 1697.3097 | 1456.0337 | 2.575 | 2.3899 | 2.8808 | 3.1171 | 2.566
9 | SA-17-TM | 09-SA-17-TM | 1741.1057 | 1663.0108 | 1833.4902 | 1936.0985 | 1733.5096 | 1741.1057 | 1663.0108 | 1833.4902 | 1936.0985 | 1733.5096 | 3.0335 | 2.9046 | 3.2379 | 3.4816 | 3.0287
9 | SA-18-LH | 09-SA-18-LH | 1452.0278 | 1418.3322 | 1647.1907 | 1742.0138 | 1466.6406 | 1452.0278 | 1418.3322 | 1647.1907 | 1742.0138 | 1466.6406 | 2.793 | 2.5729 | 2.788 | 3.0667 | 2.7433
9 | SA-18-LL | 09-SA-18-LL | 1397.3529 | 1369.4834 | 1603.939 | 1690.6597 | 1414.4506 | 1397.3529 | 1369.4834 | 1603.939 | 1690.6597 | 1414.4506 | 2.6661 | 2.4576 | 2.6771 | 2.9664 | 2.6214
9 | SA-18-TH | 09-SA-18-TH | 1479.3645 | 1431.1671 | 1669.448 | 1766.2153 | 1489.7101 | 1479.3645 | 1431.1671 | 1669.448 | 1766.2153 | 1489.7101 | 2.5533 | 2.3648 | 2.7803 | 2.9849 | 2.5341
9 | SA-18-TL | 09-SA-18-TL | 1603.1688 | 1538.722 | 1761.6355 | 1857.3637 | 1605.9026 | 1603.1688 | 1538.722 | 1761.6355 | 1857.3637 | 1605.9026 | 2.9628 | 2.7345 | 3.2282 | 3.4726 | 2.9384
9 | SA-18-TM | 09-SA-18-TM | 1511.7992 | 1465.9354 | 1683.826 | 1814.8157 | 1521.874 | 1511.7992 | 1465.9354 | 1683.826 | 1814.8157 | 1521.874 | 2.6382 | 2.4414 | 2.6584 | 3.0884 | 2.6017
9 | SH-10-HH | 09-SH-10-HH | 3635.7722 | 2845.1723 | 2982.9654 | 3006.9244 | 3417.8074 | 2027.1858 | 2034.8634 | 2542 | 2684.1588 | 2074.7172 | 3.9549 | 3.675 | 4.3397 | 4.681 | 3.9358
9 | SH-10-HL | 09-SH-10-HL | 3733.8235 | 2925.9634 | 3059.7182 | 3084.3582 | 3510.5118 | 2106.5911 | 2110.0597 | 2617.7237 | 2761.4586 | 2152.9727 | 4.1622 | 3.866 | 4.5378 | 4.8833 | 4.1391
9 | SH-10-HM | 09-SH-10-HM | 3620.7644 | 2847.1908 | 2949.7499 | 3002.3372 | 3405.3469 | 2064.0933 | 2058.8242 | 2519.9094 | 2686.1262 | 2104.457 | 4.0786 | 3.7729 | 4.0861 | 4.7528 | 4.0288
9 | SH-10-LH | 09-SH-10-LH | 3693.0826 | 2844.0708 | 2904.2391 | 2927.392 | 3451.5953 | 1982.714 | 1983.6232 | 2439.9657 | 2586.3944 | 2024.0958 | 3.7012 | 3.4319 | 3.7567 | 4.1722 | 3.6581
9 | SH-10-LL | 09-SH-10-LL | 3651.9528 | 2857.7155 | 2985.7172 | 3009.2164 | 3432.0992 | 2059.1403 | 2056.2635 | 2551.6639 | 2690.9831 | 2102.5618 | 3.9412 | 3.6481 | 4.3048 | 4.6125 | 3.917
9 | SH-10-LM | 09-SH-10-LM | 3604.4911 | 2819.5204 | 2946.5294 | 2970.071 | 3387.2507 | 2019.3694 | 2018.0527 | 2509.6952 | 2649.3282 | 2062.9354 | 3.893 | 3.6149 | 4.2429 | 4.5263 | 3.8702
9 | SH-10-MH | 09-SH-10-MH | 3664.9763 | 2831.0378 | 2902.6388 | 2953.3408 | 3429.3639 | 1990.8128 | 1990.6395 | 2450.2792 | 2619.9687 | 2032.6044 | 3.8434 | 3.561 | 3.8952 | 4.5415 | 3.8017
9 | SH-10-ML | 09-SH-10-ML | 3554.5376 | 2817.3464 | 2977.3373 | 3003.7957 | 3354.0207 | 2070.4885 | 2070.0938 | 2571.671 | 2706.9006 | 2115.0716 | 4.1556 | 3.8593 | 4.5902 | 4.9254 | 4.1372
9 | SH-10-MM | 09-SH-10-MM | 3706.6304 | 2891.889 | 2962.4512 | 2988.1136 | 3476.0332 | 2088.4879 | 2079.0957 | 2523.8871 | 2667.1286 | 2125.8423 | 4.0475 | 3.7321 | 4.035 | 4.4818 | 3.9898
9 | SH-13-HH | 09-SH-13-HH | 3210.4084 | 2461.4913 | 2514.4032 | 2517.1995 | 2997.0383 | 1678.5367 | 1687.648 | 2090.9237 | 2207.1732 | 1717.2699 | 3.3152 | 3.0531 | 3.5966 | 3.875 | 3.2899
9 | SH-13-HL | 09-SH-13-HL | 2906.9545 | 2263.6061 | 2344.7828 | 2352.2121 | 2726.7563 | 1585.8753 | 1600.5454 | 1986.4385 | 2090.0507 | 1624.5235 | 3.3721 | 3.2708 | 3.7753 | 4.0569 | 3.3904
9 | SH-13-HM | 09-SH-13-HM | 3022.0043 | 2353.8833 | 2429.2176 | 2441.0366 | 2834.1938 | 1657.4241 | 1665.631 | 2053.1292 | 2166.4131 | 1694.5131 | 3.3341 | 3.0656 | 3.5882 | 3.8605 | 3.3051
9 | SH-13-LH | 09-SH-13-LH | 3126.5669 | 2336.6136 | 2337.8081 | 2358.2215 | 2897.2581 | 1539.183 | 1543.4485 | 1913.3194 | 2044.5522 | 1573.9916 | 2.9759 | 2.7724 | 3.0629 | 3.5746 | 2.9509
9 | SH-13-LL | 09-SH-13-LL | 2925.9129 | 2231.5518 | 2276.0133 | 2276.6032 | 2727.6618 | 1533.0606 | 1532.4363 | 1897.0287 | 1999.6838 | 1565.4535 | 3.1353 | 2.9189 | 3.4443 | 3.7032 | 3.1214
9 | SH-13-LM | 09-SH-13-LM | 2850.3599 | 2231.2553 | 2325.4253 | 2346.0456 | 2678.5588 | 1599.3532 | 1605.8922 | 1989.2849 | 2100.2723 | 1635.5682 | 3.1417 | 2.9257 | 3.228 | 3.5802 | 3.111
9 | SH-13-MH | 09-SH-13-MH | 3077.9376 | 2335.348 | 2356.8202 | 2347.8107 | 2863.5423 | 1531.2307 | 1550.1199 | 1930.2305 | 2034.9805 | 1570.6429 | 3.084 | 3.0029 | 3.4061 | 3.6733 | 3.0994
9 | SH-13-ML | 09-SH-13-ML | 3070.7053 | 2343.2657 | 2394.6554 | 2400.4866 | 2863.5138 | 1616.178 | 1622.1831 | 2010.5209 | 2119.6425 | 1652.6167 | 3.3176 | 3.0954 | 3.4244 | 3.7899 | 3.2876
9 | SH-13-MM | 09-SH-13-MM | 3023.0771 | 2315.5652 | 2368.3786 | 2366.3474 | 2821.6508 | 1584.0006 | 1591.7672 | 1975.4447 | 2078.7281 | 1620.4483 | 3.3047 | 3.0866 | 3.6408 | 3.9137 | 3.293
9 | SH-14-HH | 09-SH-14-HH | 2983.5251 | 2298.5213 | 2357.0154 | 2362.0164 | 2789.2587 | 1591.031 | 1595.5196 | 1973.0772 | 2081.2229 | 1626.1051 | 3.1424 | 2.8968 | 3.4146 | 3.676 | 3.1195
9 | SH-14-HL | 09-SH-14-HL | 2915.8103 | 2242.5498 | 2291.6314 | 2295.3489 | 2724.1455 | 1555.2163 | 1560.7494 | 1922.9214 | 2025.6554 | 1589.1988 | 3.1419 | 2.8916 | 3.3894 | 3.6432 | 3.1158
9 | SH-14-HM | 09-SH-14-HM | 2903.9951 | 2239.2151 | 2299.1748 | 2305.0214 | 2715.7512 | 1554.5416 | 1559.3988 | 1929.184 | 2034.0375 | 1589.0072 | 3.0171 | 2.7767 | 3.2632 | 3.5103 | 2.9928
9 | SH-14-MH | 09-SH-14-MH | 2872.9493 | 2163.2626 | 2176.8426 | 2179.6233 | 2667.6904 | 1441.4794 | 1445.6158 | 1791.122 | 1896.044 | 1473.6991 | 2.8023 | 2.6109 | 2.8808 | 3.1956 | 2.7753
9 | SH-14-ML | 09-SH-14-ML | 2932.171 | 2173.8211 | 2191.7521 | 2178.2491 | 2712.8073 | 1434.3384 | 1435.5471 | 1799.7783 | 1891.6245 | 1467.0261 | 3.0202 | 2.8094 | 3.3334 | 3.5756 | 3.0075
9 | SH-14-MM | 09-SH-14-MM | 2779.7497 | 2123.3424 | 2168.6093 | 2183.6133 | 2592.8847 | 1450.6443 | 1458.4792 | 1812.0006 | 1921.0867 | 1484.6927 | 2.9571 | 2.7641 | 3.0574 | 3.5183 | 2.9344
9 | SH-15-HH | 09-SH-15-HH | 3036.048 | 2233.025 | 2212.1745 | 2196.0068 | 2800.3826 | 1436.9016 | 1439.5299 | 1783.4665 | 1882.6067 | 1468.4395 | 2.7656 | 2.5476 | 2.9909 | 3.2176 | 2.7438
9 | SH-15-HL | 09-SH-15-HL | 2617.6789 | 2040.5857 | 2109.0079 | 2117.831 | 2455.7111 | 1441.7964 | 1449.0178 | 1787.1522 | 1882.2813 | 1474.1063 | 3.0136 | 2.7964 | 3.2859 | 3.5287 | 2.9962
9 | SH-15-HM | 09-SH-15-HM | 2581.5344 | 2000.4056 | 2060.2987 | 2058.2703 | 2417.4679 | 1366.6857 | 1383.2537 | 1722.7493 | 1811.5038 | 1401.7061 | 2.8788 | 2.7687 | 3.1305 | 3.3635 | 2.8816
9 | SH-15-MH | 09-SH-15-MH | 2800.9396 | 2079.1911 | 2104.2218 | 2089.0991 | 2592.7881 | 1367.5974 | 1370.7181 | 1725.7491 | 1813.4135 | 1399.9886 | 2.8463 | 2.6621 | 3.1681 | 3.3905 | 2.8395
9 | SH-15-ML | 09-SH-15-ML | 2658.3573 | 1996.6885 | 2030.9402 | 2025.0889 | 2468.6357 | 1344.2865 | 1345.7618 | 1684.2768 | 1771.6375 | 1374.8072 | 2.8705 | 2.6762 | 3.1589 | 3.3813 | 2.8588
9 | SH-15-MM | 09-SH-15-MM | 2751.5255 | 2066.7696 | 2087.164 | 2075.0047 | 2553.8033 | 1365.1423 | 1372.7068 | 1711.5779 | 1800.5247 | 1397.4948 | 2.8486 | 2.6534 | 3.099 | 3.3335 | 2.8337
9 | SH-16-CH | 09-SH-16-CH | 3119.3674 | 2323.3695 | 2262.0007 | 2273.4979 | 2882.878 | 1686.9169 | 1635.1953 | 1910.9606 | 2016.3878 | 1697.044 | 3.1045 | 2.8453 | 3.2697 | 3.5031 | 3.0692
9 | SH-16-CL | 09-SH-16-CL | 3031.5665 | 2291.9736 | 2250.8883 | 2266.396 | 2813.2652 | 1703.5602 | 1652.877 | 1925.0906 | 2028.2687 | 1713.648 | 3.1319 | 2.891 | 3.4285 | 3.6887 | 3.112
9 | SH-16-LH | 09-SH-16-LH | 3095.3327 | 2263.5545 | 2157.2242 | 2162.5982 | 2844.5434 | 1527.1699 | 1495.2416 | 1754.3468 | 1865.2384 | 1541.7621 | 2.7978 | 2.5786 | 2.8067 | 3.1103 | 2.759
9 | SH-16-LL | 09-SH-16-LL | 2993.6125 | 2240.9968 | 2182.3698 | 2189.7339 | 2769.8937 | 1585.599 | 1557.171 | 1827.7308 | 1929.6196 | 1601.9974 | 3.064 | 2.8226 | 3.0535 | 3.3612 | 3.019
9 | SH-16-LM | 09-SH-16-LM | 3146.5874 | 2313.8759 | 2219.3772 | 2225.4065 | 2896.5322 | 1581.4823 | 1550.2313 | 1820.1697 | 1930.9116 | 1597.1777 | 2.9063 | 2.6695 | 2.9011 | 3.2009 | 2.8627
9 | SH-16-TH | 09-SH-16-TH | 3436.4897 | 2438.3388 | 2256.1681 | 2244.8141 | 3130.6147 | 1633.1459 | 1571.1855 | 1814.7267 | 1919.4066 | 1637.5758 | 2.966 | 2.7451 | 3.1968 | 3.4211 | 2.944
9 | SH-16-TL | 09-SH-16-TL | 3620.6237 | 2597.4254 | 2396.1684 | 2403.3307 | 3306.217 | 1828.3709 | 1751.8254 | 1981.39 | 2099.5827 | 1827.6451 | 3.3806 | 3.117 | 3.388 | 3.9393 | 3.3373
9 | SH-16-TM | 09-SH-16-TM | 3632.2372 | 2594.9677 | 2401.6347 | 2389.9469 | 3314.0391 | 1807.1746 | 1732.261 | 1977.802 | 2079.5727 | 1807.9481 | 3.3205 | 3.0604 | 3.5959 | 3.8709 | 3.2951
9 | SH-17-CM | 09-SH-17-CM | 3129.5032 | 2273.4696 | 2173.8539 | 2175.9219 | 2872.1577 | 1610.2861 | 1562.6243 | 1820.8098 | 1918.184 | 1619.9638 | 2.9755 | 2.7469 | 3.2577 | 3.5052 | 2.9567
9 | SH-17-LM | 09-SH-17-LM | 2923.2396 | 2193.1083 | 2120.5011 | 2150.2425 | 2705.3193 | 1553.7921 | 1526.7147 | 1774.4006 | 1895.1778 | 1569.0275 | 2.9352 | 2.6976 | 2.904 | 3.4008 | 2.8929
9 | SH-17-TH | 09-SH-17-TH | 3329.8214 | 2342.9679 | 2156.5957 | 2137.9361 | 3026.7396 | 1532.5198 | 1480.9886 | 1722.1196 | 1817.771 | 1539.6074 | 2.7742 | 2.5662 | 3.0129 | 3.2304 | 2.7554
9 | SH-17-TL | 09-SH-17-TL | 3325.8902 | 2342.4522 | 2157.1185 | 2140.425 | 3023.927 | 1546.7643 | 1493.5325 | 1731.489 | 1827.164 | 1553.0913 | 2.8462 | 2.6348 | 3.0785 | 3.2975 | 2.8262
9 | SH-18-LH | 09-SH-18-LH | 2998.6637 | 2138.1193 | 2012.1872 | 2003.3391 | 2737.5872 | 1423.4572 | 1394.906 | 1632.9022 | 1725.2867 | 1436.9039 | 2.7213 | 2.4945 | 2.6964 | 2.9792 | 2.6777
9 | SH-18-LL | 09-SH-18-LL | 2868.5536 | 2115.7292 | 2047.0143 | 2047.3538 | 2643.7922 | 1462.4823 | 1437.7349 | 1696.3737 | 1790.4754 | 1478.801 | 2.7656 | 2.5371 | 2.7585 | 3.0496 | 2.7233
9 | SH-18-LM | 09-SH-18-LM | 3109.7068 | 2196.0777 | 2042.4639 | 2029.53 | 2830.7859 | 1448.0558 | 1415.8316 | 1646.6527 | 1738.9867 | 1459.8309 | 2.8408 | 2.5954 | 2.7591 | 3.0365 | 2.7885
9 | SH-18-TM | 09-SH-18-TM | 3236.8019 | 2266.1014 | 2048.7684 | 2031.926 | 2935.8557 | 1469.6186 | 1425.0601 | 1635.1252 | 1727.1963 | 1476.0586 | 2.7985 | 2.5986 | 2.838 | 3.132 | 2.7661
10 | SA-10-HH | 10-SA-10-HH | 2788.1003 | 2698.2567 | 3151.266 | 3299.3495 | 2860.5519 | 2788.1003 | 2698.2567 | 3151.266 | 3299.3495 | 2860.5519 | 4.4253 | 4.0268 | 4.2879 | 4.7632 | 4.2641
10 | SA-10-HL | 10-SA-10-HL | 2918.9022 | 2836.0265 | 3328.6161 | 3488.8886 | 3008.7026 | 2918.9022 | 2836.0265 | 3328.6161 | 3488.8886 | 3008.7026 | 4.9866 | 4.5101 | 4.7325 | 5.5316 | 4.8044
10 | SA-10-HM | 10-SA-10-HM | 2838.7816 | 2754.5598 | 3239.5522 | 3401.5111 | 2925.8383 | 2838.7816 | 2754.5598 | 3239.5522 | 3401.5111 | 2925.8383 | 4.5765 | 4.1271 | 4.3343 | 5.1206 | 4.4088
10 | SA-10-LH | 10-SA-10-LH | 2677.6716 | 2597.6629 | 3084.7223 | 3228.3374 | 2765.7304 | 2677.6716 | 2597.6629 | 3084.7223 | 3228.3374 | 2765.7304 | 4.2148 | 3.8615 | 4.1547 | 4.6203 | 4.0944
10 | SA-10-LL | 10-SA-10-LL | 2796.794 | 2722.916 | 3209.316 | 3358.2235 | 2890.0646 | 2796.794 | 2722.916 | 3209.316 | 3358.2235 | 2890.0646 | 4.607 | 4.1828 | 4.4035 | 5.1395 | 4.4543
10 | SA-10-LM | 10-SA-10-LM | 2690.8312 | 2609.463 | 3088.5841 | 3229.6311 | 2775.4209 | 2690.8312 | 2609.463 | 3088.5841 | 3229.6311 | 2775.4209 | 4.2742 | 3.9061 | 4.1873 | 4.6576 | 4.1403
10 | SA-10-MH | 10-SA-10-MH | 2689.2673 | 2608.6637 | 3086.736 | 3242.9421 | 2776.3899 | 2689.2673 | 2608.6637 | 3086.736 | 3242.9421 | 2776.3899 | 4.1043 | 3.7595 | 4.047 | 4.5091 | 3.9884
10 | SA-10-ML | 10-SA-10-ML | 2882.3138 | 2803.2789 | 3295.0704 | 3433.9969 | 2971.6475 | 2882.3138 | 2803.2789 | 3295.0704 | 3433.9969 | 2971.6475 | 4.698 | 4.2754 | 4.5137 | 5.0385 | 4.52
10 | SA-10-MM | 10-SA-10-MM | 2666.2102 | 2569.8693 | 3111.6291 | 3253.9539 | 2756.076 | 2666.2102 | 2569.8693 | 3111.6291 | 3253.9539 | 2756.076 | 3.9871 | 3.4266 | 4.153 | 4.6399 | 3.8272
10 | SA-13-HH | 10-SA-13-HH | 2166.1527 | 2112.1587 | 2527.8974 | 2629.2442 | 2248.9287 | 2166.1527 | 2112.1587 | 2527.8974 | 2629.2442 | 2248.9287 | 3.7017 | 3.3924 | 3.9423 | 4.2318 | 3.6554
10 | SA-13-HL | 10-SA-13-HL | 2180.9165 | 2118.6322 | 2518.4887 | 2634.9455 | 2255.5498 | 2180.9165 | 2118.6322 | 2518.4887 | 2634.9455 | 2255.5498 | 3.8936 | 3.5831 | 3.8801 | 4.476 | 3.8256
10 | SA-13-HM | 10-SA-13-HM | 2160.6665 | 2108.3997 | 2508.9036 | 2606.013 | 2240.1433 | 2160.6665 | 2108.3997 | 2508.9036 | 2606.013 | 2240.1433 | 3.8287 | 3.4896 | 3.9703 | 4.252 | 3.7409
10 | SA-13-LH | 10-SA-13-LH | 2055.0974 | 1994.3226 | 2362.5008 | 2499.7288 | 2125.6628 | 2055.0974 | 1994.3226 | 2362.5008 | 2499.7288 | 2125.6628 | 3.3321 | 3.0601 | 3.3102 | 3.8503 | 3.2726
10 | SA-13-LL | 10-SA-13-LL | 2160.3729 | 2102.2435 | 2494.0377 | 2599.0747 | 2234.3429 | 2160.3729 | 2102.2435 | 2494.0377 | 2599.0747 | 2234.3429 | 3.6218 | 3.3226 | 3.5834 | 3.9704 | 3.5221
10 | SA-13-LM | 10-SA-13-LM | 2146.0473 | 2089.0746 | 2482.9827 | 2599.236 | 2223.0888 | 2146.0473 | 2089.0746 | 2482.9827 | 2599.236 | 2223.0888 | 3.462 | 3.1805 | 3.447 | 3.8295 | 3.3764
10 | SA-13-MH | 10-SA-13-MH | 2110.9714 | 2045.1746 | 2441.6056 | 2544.1433 | 2180.0238 | 2110.9714 | 2045.1746 | 2441.6056 | 2544.1433 | 2180.0238 | 3.5779 | 3.282 | 3.819 | 4.1085 | 3.5383
10 | SA-13-ML | 10-SA-13-ML | 2152.3524 | 2090.3188 | 2465.0139 | 2569.916 | 2218.9116 | 2152.3524 | 2090.3188 | 2465.0139 | 2569.916 | 2218.9116 | 3.7631 | 3.4457 | 3.6817 | 4.0584 | 3.6417
10 | SA-13-MM | 10-SA-13-MM | 2083.032 | 2016.0247 | 2379.9438 | 2479.4576 | 2142.2524 | 2083.032 | 2016.0247 | 2379.9438 | 2479.4576 | 2142.2524 | 3.6285 | 3.3194 | 3.8243 | 4.067 | 3.5637
10 | SA-14-HH | 10-SA-14-HH | 2103.5218 | 2043.2103 | 2404.3085 | 2512.7907 | 2168.3562 | 2103.5218 | 2043.2103 | 2404.3085 | 2512.7907 | 2168.3562 | 3.5841 | 3.2905 | 3.532 | 3.9015 | 3.481
10 | SA-14-HL | 10-SA-14-HL | 2011.8375 | 1954.3824 | 2332.7402 | 2423.4481 | 2080.7003 | 2011.8375 | 1954.3824 | 2332.7402 | 2423.4481 | 2080.7003 | 3.5917 | 3.3024 | 3.8238 | 4.0773 | 3.5477
10 | SA-14-HM | 10-SA-14-HM | 2080.5631 | 2020.9375 | 2409.6667 | 2526.6439 | 2154.3683 | 2080.5631 | 2020.9375 | 2409.6667 | 2526.6439 | 2154.3683 | 3.5957 | 3.3023 | 3.5611 | 4.1271 | 3.5261
10 | SA-14-MH | 10-SA-14-MH | 2010.5943 | 1983.3975 | 2356.2148 | 2469.1298 | 2104.0079 | 2010.5943 | 1983.3975 | 2356.2148 | 2469.1298 | 2104.0079 | 2.9603 | 2.9573 | 3.2093 | 3.5711 | 3.077
10 | SA-14-ML | 10-SA-14-ML | 2023.8546 | 1967.8917 | 2341.4247 | 2456.8616 | 2096.2214 | 2023.8546 | 1967.8917 | 2341.4247 | 2456.8616 | 2096.2214 | 3.4874 | 3.2149 | 3.4896 | 4.0456 | 3.4362
10 | SA-14-MM | 10-SA-14-MM | 1979.8442 | 1929.1914 | 2316.261 | 2424.6073 | 2058.6848 | 1979.8442 | 1929.1914 | 2316.261 | 2424.6073 | 2058.6848 | 2.9935 | 2.7705 | 3.2297 | 3.5961 | 2.9997
10 | SA-15-HH | 10-SA-15-HH | 1891.3922 | 1844.155 | 2200.2925 | 2289.814 | 1961.9605 | 1891.3922 | 1844.155 | 2200.2925 | 2289.814 | 1961.9605 | 3.3089 | 3.0168 | 3.4548 | 3.706 | 3.2407
10 | SA-15-HL | 10-SA-15-HL | 1852.0321 | 1811.5005 | 2159.7945 | 2239.9681 | 1924.2149 | 1852.0321 | 1811.5005 | 2159.7945 | 2239.9681 | 1924.2149 | 3.3673 | 3.2215 | 3.5859 | 3.8197 | 3.3873
10 | SA-15-HM | 10-SA-15-HM | 1873.4952 | 1824.1102 | 2173.5725 | 2260.5414 | 1940.3339 | 1873.4952 | 1824.1102 | 2173.5725 | 2260.5414 | 1940.3339 | 3.191 | 2.9065 | 3.3299 | 3.5708 | 3.1232
10 | SA-15-MH | 10-SA-15-MH | 1937.2223 | 1881.9751 | 2231.0211 | 2334.9946 | 2002.0536 | 1937.2223 | 1881.9751 | 2231.0211 | 2334.9946 | 2002.0536 | 3.3358 | 3.0762 | 3.3425 | 3.7004 | 3.263
10 | SA-15-ML | 10-SA-15-ML | 1896.0502 | 1843.4143 | 2186.5697 | 2277.342 | 1959.3629 | 1896.0502 | 1843.4143 | 2186.5697 | 2277.342 | 1959.3629 | 3.2594 | 2.9932 | 3.2351 | 3.5685 | 3.1716
10 | SA-15-MM | 10-SA-15-MM | 1889.1338 | 1834.7363 | 2179.3544 | 2287.9674 | 1954.1319 | 1889.1338 | 1834.7363 | 2179.3544 | 2287.9674 | 1954.1319 | 3.2919 | 3.026 | 3.2618 | 3.7534 | 3.2261
10 | SA-16-CH | 10-SA-16-CH | 2308.1639 | 2167.9404 | 2405.2404 | 2519.8032 | 2281.5952 | 2308.1639 | 2167.9404 | 2405.2404 | 2519.8032 | 2281.5952 | 3.5066 | 3.2107 | 3.4334 | 4.024 | 3.4294
10 | SA-16-CL | 10-SA-16-CL | 2172.6217 | 2038.1406 | 2273.4656 | 2369.5275 | 2147.1266 | 2172.6217 | 2038.1406 | 2273.4656 | 2369.5275 | 2147.1266 | 3.5789 | 3.2132 | 3.5579 | 3.8002 | 3.4298
10 | SA-16-CM | 10-SA-16-CM | 2242.9786 | 2104.8799 | 2355.8705 | 2458.1499 | 2219.7669 | 2242.9786 | 2104.8799 | 2355.8705 | 2458.1499 | 2219.7669 | 3.6007 | 3.2727 | 3.6817 | 3.9316 | 3.4978
10 | SA-16-LH | 10-SA-16-LH | 1975.4014 | 1876.9064 | 2120.2486 | 2220.6185 | 1979.6584 | 1975.4014 | 1876.9064 | 2120.2486 | 2220.6185 | 1979.6584 | 3.2968 | 2.9817 | 3.1639 | 3.4938 | 3.1562
10 | SA-16-LL | 10-SA-16-LL | 2107.9128 | 1995.9413 | 2242.2596 | 2338.0044 | 2102.1433 | 2107.9128 | 1995.9413 | 2242.2596 | 2338.0044 | 2102.1433 | 3.6201 | 3.2818 | 3.4405 | 3.7774 | 3.457
10 | SA-16-LM | 10-SA-16-LM | 2082.4263 | 1976.5929 | 2233.2135 | 2331.9897 | 2084.3996 | 2082.4263 | 1976.5929 | 2233.2135 | 2331.9897 | 2084.3996 | 3.4729 | 3.1478 | 3.3005 | 3.6323 | 3.3174
10 | SA-16-NM | 10-SA-16-NM | 1879.291 | 1780.9913 | 2008.7425 | 2084.8515 | 1876.0569 | 1879.291 | 1780.9913 | 2008.7425 | 2084.8515 | 1876.0569 | 3.2512 | 2.9079 | 3.0517 | 3.3514 | 3.075
10 | SA-16-TH | 10-SA-16-TH | 2440.1757 | 2267.9332 | 2470.1886 | 2594.936 | 2381.921 | 2440.1757 | 2267.9332 | 2470.1886 | 2594.936 | 2381.921 | 3.8215 | 3.4797 | 3.662 | 4.0491 | 3.6693
10 | SA-16-TL | 10-SA-16-TL | 2211.8673 | 2050.7323 | 2245.9515 | 2340.2041 | 2155.6297 | 2211.8673 | 2050.7323 | 2245.9515 | 2340.2041 | 2155.6297 | 3.5847 | 3.2245 | 3.6342 | 3.8915 | 3.4589
10 | SA-17-CH | 10-SA-17-CH | 2135.9907 | 2008.2839 | 2247.4019 | 2337.8401 | 2115.7444 | 2135.9907 | 2008.2839 | 2247.4019 | 2337.8401 | 2115.7444 | 3.389 | 3.1 | 3.5942 | 3.8482 | 3.3382
10 | SA-17-CL | 10-SA-17-CL | 2129.7055 | 1999.8169 | 2232.4278 | 2320.6857 | 2105.8027 | 2129.7055 | 1999.8169 | 2232.4278 | 2320.6857 | 2105.8027 | 3.4619 | 3.162 | 3.5946 | 3.8397 | 3.3855
10 | SA-17-CM | 10-SA-17-CM | 2160.7657 | 2026.374 | 2254.5629 | 2344.2249 | 2132.5346 | 2160.7657 | 2026.374 | 2254.5629 | 2344.2249 | 2132.5346 | 3.4388 | 3.1422 | 3.5996 | 3.8486 | 3.372
10 | SA-17-LH | 10-SA-17-LH | 1905.0486 | 1831.8879 | 2069.7151 | 2162.9825 | 1925.849 | 1905.0486 | 1831.8879 | 2069.7151 | 2162.9825 | 1925.849 | 2.9726 | 2.9194 | 3.0854 | 3.4001 | 3.0223
10 | SA-17-LL | 10-SA-17-LL | 2031.8716 | 1921.7347 | 2153.4347 | 2244.0746 | 2022.9165 | 2031.8716 | 1921.7347 | 2153.4347 | 2244.0746 | 2022.9165 | 3.471 | 3.1487 | 3.3025 | 3.628 | 3.317
10 | SA-17-LM | 10-SA-17-LM | 2010.016 | 1909.2355 | 2152.1707 | 2245.5852 | 2011.4262 | 2010.016 | 1909.2355 | 2152.1707 | 2245.5852 | 2011.4262 | 3.3423 | 3.0433 | 3.2257 | 3.5474 | 3.2127
10 | SA-17-TH | 10-SA-17-TH | 2033.2379 | 1918.0412 | 2131.8622 | 2273.7858 | 2023.3722 | 2033.2379 | 1918.0412 | 2131.8622 | 2273.7858 | 2023.3722 | 3.2143 | 2.9286 | 3.1173 | 3.6295 | 3.1243
10 | SA-17-TL | 10-SA-17-TL | 1903.0159 | 1786.3995 | 1983.9125 | 2060.7398 | 1878.2462 | 1903.0159 | 1786.3995 | 1983.9125 | 2060.7398 | 1878.2462 | 3.2747 | 2.9149 | 3.3207 | 3.5563 | 3.145
10 | SA-17-TM | 10-SA-17-TM | 2281.3452 | 2094.8687 | 2247.9362 | 2347.2388 | 2195.8274 | 2281.3452 | 2094.8687 | 2247.9362 | 2347.2388 | 2195.8274 | 3.4455 | 3.1439 | 3.6294 | 3.892 | 3.3843
10 | SA-18-LH | 10-SA-18-LH | 1894.4849 | 1792.5639 | 2012.3685 | 2102.0936 | 1888.4639 | 1894.4849 | 1792.5639 | 2012.3685 | 2102.0936 | 1888.4639 | 3.2118 | 2.9151 | 3.0595 | 3.36 | 3.0709
10 | SA-18-LL | 10-SA-18-LL | 1831.9046 | 1739.1123 | 1969.8966 | 2051.9194 | 1834.4685 | 1831.9046 | 1739.1123 | 1969.8966 | 2051.9194 | 1834.4685 | 3.1206 | 2.8292 | 3.0105 | 3.3269 | 2.9956
10 | SA-18-TH | 10-SA-18-TH | 1959.9954 | 1841.8244 | 2073.5179 | 2173.9932 | 1946.4529 | 1959.9954 | 1841.8244 | 2073.5179 | 2173.9932 | 1946.4529 | 3.0479 | 2.7645 | 3.1703 | 3.3957 | 2.974
10 | SA-18-TL | 10-SA-18-TL | 2159.9323 | 2013.8992 | 2225.1768 | 2322.6864 | 2119.7038 | 2159.9323 | 2013.8992 | 2225.1768 | 2322.6864 | 2119.7038 | 3.4624 | 3.1771 | 3.7064 | 3.9592 | 3.4233
10 | SA-18-TM | 10-SA-18-TM | 2007.6729 | 1890.9229 | 2099.9203 | 2209.621 | 1990.638 | 2007.6729 | 1890.9229 | 2099.9203 | 2209.621 | 1990.638 | 3.1336 | 2.8521 | 3.0235 | 3.3509 | 3.0151
10 | SH-10-HH | 10-SH-10-HH | 4842.6037 | 3819.7073 | 3881.5308 | 3869.7486 | 4154.9599 | 2681.8724 | 2613.5276 | 3141.1397 | 3274.4332 | 2774.8913 | 4.4563 | 4.0915 | 4.6969 | 5.0362 | 4.3907
10 | SH-10-HL | 10-SH-10-HL | 4972.9274 | 3929.6165 | 3981.9997 | 3964.9571 | 4268.4338 | 2785.9328 | 2712.8664 | 3239.1334 | 3369.5711 | 2875.0403 | 4.6614 | 4.247 | 4.8582 | 5.2184 | 4.5658
10 | SH-10-HM | 10-SH-10-HM | 4852.1875 | 3846.5519 | 3865.1159 | 3868.4595 | 4168.2272 | 2744.6388 | 2659.2744 | 3135.4711 | 3280.9139 | 2815.5859 | 4.5467 | 4.1779 | 4.4889 | 4.9923 | 4.4308
10 | SH-10-LH | 10-SH-10-LH | 4915.9819 | 3831.2403 | 3814.4764 | 3823.3537 | 4170.3298 | 2647.6186 | 2572.85 | 3049.6727 | 3204.8314 | 2727.2086 | 4.0951 | 3.7544 | 4.0524 | 4.5042 | 3.9888
10 | SH-10-LL | 10-SH-10-LL | 4929.8726 | 3865.595 | 3859.3952 | 3877.286 | 4201.845 | 2712.3829 | 2631.4459 | 3111.4434 | 3272.4928 | 2789.2396 | 4.461 | 4.0768 | 4.3444 | 5.0825 | 4.3544
10 | SH-10-LM | 10-SH-10-LM | 4830.0486 | 3793.8309 | 3781.4793 | 3817.089 | 4122.0685 | 2652.0088 | 2573.015 | 3036.8399 | 3211.9522 | 2728.2276 | 4.2852 | 3.9341 | 4.2048 | 4.9043 | 4.1971
10 | SH-10-MH | 10-SH-10-MH | 4930.5992 | 3847.3723 | 3832.9076 | 3834.9836 | 4185.6512 | 2678.4955 | 2598.6728 | 3076.6689 | 3224.6477 | 2753.9805 | 4.2837 | 3.9194 | 4.2177 | 4.6853 | 4.1634
10 | SH-10-ML | 10-SH-10-ML | 4848.9546 | 3845.8118 | 3876.3861 | 3895.3089 | 4171.4863 | 2766.5426 | 2681.1699 | 3167.2327 | 3322.176 | 2840.9935 | 4.6958 | 4.2962 | 4.5864 | 5.3635 | 4.5889
10 | SH-10-MM | 10-SH-10-MM | 4960.5711 | 3902.8557 | 3895.346 | 3893.2623 | 4234.1823 | 2765.4904 | 2681.2537 | 3154.1519 | 3296.6066 | 2836.0605 | 4.4442 | 4.0543 | 4.3594 | 4.8397 | 4.3095
10 | SH-13-HH | 10-SH-13-HH | 4342.8819 | 3351.3811 | 3328.7847 | 3297.1203 | 3654.5515 | 2255.7994 | 2195.7792 | 2615.4751 | 2723.6917 | 2326.1992 | 3.8012 | 3.453 | 3.9666 | 4.2596 | 3.7197
10 | SH-13-HL | 10-SH-13-HL | 3949.0046 | 3084.4403 | 3096.8865 | 3067.754 | 3356.0861 | 2131.9502 | 2076.1478 | 2482.6757 | 2575.8567 | 2200.2538 | 3.8382 | 3.5442 | 4.1701 | 4.4556 | 3.819
10 | SH-13-HM | 10-SH-13-HM | 4071.0018 | 3190.5715 | 3193.1599 | 3173.1389 | 3466.0864 | 2210.5926 | 2151.5122 | 2552.7086 | 2659.1651 | 2277.1054 | 3.7729 | 3.4187 | 3.9076 | 4.1933 | 3.6806
10 | SH-13-LH | 10-SH-13-LH | 4363.6849 | 3233.5796 | 3131.3986 | 3110.7402 | 3563.3129 | 2093.9292 | 2035.48 | 2416.4999 | 2533.0119 | 2157.4621 | 3.3511 | 3.0828 | 3.3453 | 3.7172 | 3.2759
10 | SH-13-LL | 10-SH-13-LL | 3973.6748 | 3046.9585 | 2979.7301 | 2978.8554 | 3323.255 | 2052.5871 | 1989.0632 | 2339.0956 | 2461.3577 | 2106.1663 | 3.5248 | 3.2583 | 3.5092 | 4.0852 | 3.4742
10 | SH-13-LM | 10-SH-13-LM | 3832.9313 | 3040.4514 | 3075.9104 | 3080.156 | 3298.998 | 2150.4408 | 2116.9026 | 2517.6261 | 2631.5636 | 2235.2914 | 3.2555 | 3.2488 | 3.5262 | 3.9171 | 3.3654
10 | SH-13-MH | 10-SH-13-MH | 4180.5069 | 3177.5264 | 3140.8804 | 3100.5033 | 3479.9319 | 2061.3212 | 2005.9843 | 2418.9825 | 2518.4939 | 2132.2579 | 3.5117 | 3.2438 | 3.787 | 4.0554 | 3.4889
10 | SH-13-ML | 10-SH-13-ML | 4201.4684 | 3241.4674 | 3227.2525 | 3209.2043 | 3538.4 | 2218.0641 | 2161.447 | 2581.3217 | 2690.1531 | 2290.9146 | 3.7805 | 3.4852 | 3.7916 | 4.2046 | 3.7023
10 | SH-13-MM | 10-SH-13-MM | 4121.2216 | 3191.1581 | 3144.6755 | 3145.8232 | 3473.5964 | 2162.1593 | 2098.9765 | 2478.9063 | 2608.7241 | 2223.8956 | 3.7556 | 3.4604 | 3.741 | 4.3159 | 3.6921
10 | SH-14-HH | 10-SH-14-HH | 4042.0276 | 3137.3231 | 3122.6459 | 3095.4438 | 3415.5525 | 2134.0849 | 2077.3471 | 2469.2313 | 2571.0807 | 2199.4463 | 3.6329 | 3.2939 | 3.7744 | 4.0505 | 3.5478
10 | SH-14-HL | 10-SH-14-HL | 3972.8609 | 3059.051 | 3021.0313 | 2987.8889 | 3333.9583 | 2069.2963 | 2015.2406 | 2386.4982 | 2479.4392 | 2130.5561 | 3.5917 | 3.2555 | 3.709 | 3.9754 | 3.5011
10 | SH-14-HM | 10-SH-14-HM | 3941.6344 | 3047.489 | 3024.6809 | 2998.2647 | 3320.5985 | 2061.9516 | 2008.5828 | 2387.4627 | 2485.2958 | 2126.0806 | 3.4522 | 3.1287 | 3.5737 | 3.8322 | 3.3672
10 | SH-14-MH | 10-SH-14-MH | 3998.7255 | 2992.2604 | 2912.3419 | 2895.9067 | 3288.7493 | 1954.0141 | 1899.0522 | 2255.1578 | 2364.0837 | 2013.1677 | 3.1592 | 2.9062 | 3.1549 | 3.5027 | 3.0882
10 | SH-14-ML | 10-SH-14-ML | 4153.8109 | 3048.4098 | 2952.3032 | 2911.4439 | 3369.192 | 1974.4368 | 1911.2143 | 2281.1151 | 2372.1689 | 2028.862 | 3.4574 | 3.173 | 3.6736 | 3.9096 | 3.4093
10 | SH-14-MM | 10-SH-14-MM | 3826.6225 | 2934.4807 | 2892.9174 | 2890.026 | 3205.5972 | 1973.2937 | 1919.6151 | 2281.2652 | 2396.0339 | 2035.3627 | 3.3538 | 3.0882 | 3.3477 | 3.8765 | 3.2998
10 | SH-15-HH | 10-SH-15-HH | 4221.2658 | 3052.4849 | 2923.6194 | 2875.5111 | 3384.6909 | 1904.8383 | 1854.765 | 2209.5313 | 2301.2592 | 1964.8321 | 3.1757 | 2.8905 | 3.3056 | 3.5458 | 3.1077
10 | SH-15-HL | 10-SH-15-HL | 3536.7909 | 2771.5265 | 2768.927 | 2746.8718 | 3009.2795 | 1914.3796 | 1866.9627 | 2213.5538 | 2301.6241 | 1973.8228 | 3.3971 | 3.1074 | 3.5533 | 3.8003 | 3.334
10 | SH-15-HM | 10-SH-15-HM | 3514.4526 | 2742.0612 | 2735.876 | 2702.5417 | 2979.7855 | 1836.1167 | 1802.7346 | 2154.9202 | 2236.828 | 1905.6869 | 3.2851 | 3.1359 | 3.4835 | 3.7143 | 3.2933
10 | SH-15-MH | 10-SH-15-MH | 3906.7417 | 2910.1288 | 2828.2279 | 2823.5875 | 3204.5574 | 1905.5662 | 1850.2131 | 2200.5752 | 2316.1333 | 1963.9619 | 3.2924 | 3.0207 | 3.2668 | 3.7534 | 3.2257
10 | SH-15-ML | 10-SH-15-ML | 3728.693 | 2796.3333 | 2733.9444 | 2700.1846 | 3071.3358 | 1848.8033 | 1789.8597 | 2134.3401 | 2217.9923 | 1899.297 | 3.2911 | 3.0133 | 3.4887 | 3.6962 | 3.238
10 | SH-15-MM | 10-SH-15-MM | 3809.5564 | 2856.8665 | 2791.0948 | 2744.6757 | 3135.8722 | 1832.1009 | 1786.5074 | 2142.0527 | 2222.5202 | 1893.9062 | 3.2582 | 2.9924 | 3.4605 | 3.7025 | 3.216
10 | SH-16-CH | 10-SH-16-CH | 4430.1269 | 3232.4244 | 2966.7614 | 2940.3644 | 3544.6769 | 2218.7461 | 2085.3352 | 2337.5901 | 2436.245 | 2198.6907 | 3.4703 | 3.1262 | 3.5155 | 3.7676 | 3.3574
10 | SH-16-CL | 10-SH-16-CL | 4329.0687 | 3205.7455 | 2967.3852 | 2945.0578 | 3501.4318 | 2281.1108 | 2140.0672 | 2379.0002 | 2474.8906 | 2252.3744 | 3.5356 | 3.2443 | 3.8043 | 4.0784 | 3.5014
10 | SH-16-LH | 10-SH-16-LH | 4325.5926 | 3078.5736 | 2820.7652 | 2804.0143 | 3409.4282 | 1999.1369 | 1904.1252 | 2155.3269 | 2266.2805 | 2006.7044 | 3.2636 | 2.9692 | 3.1576 | 3.4888 | 3.1481
10 | SH-16-LL | 10-SH-16-LL | 4208.1522 | 3050.205 | 2844.1965 | 2819.5144 | 3364.0325 | 2078.9797 | 1976.0758 | 2237.0377 | 2332.6181 | 2081.451 | 3.5011 | 3.1744 | 3.3606 | 3.7041 | 3.3646
10 | SH-16-LM | 10-SH-16-LM | 4432.3923 | 3153.519 | 2896.373 | 2877.1677 | 3494.2533 | 2045.7877 | 1976.9983 | 2234.2742 | 2343.1677 | 2072.4642 | 3.1265 | 3.0775 | 3.2554 | 3.5986 | 3.1782
10 | SH-16-TH | 10-SH-16-TH | 4948.8488 | 3465.5823 | 3016.9276 | 2969.6836 | 3822.5765 | 2144.3305 | 2006.8764 | 2239.8333 | 2344.4132 | 2117.7709 | 3.5636 | 3.2198 | 3.6497 | 3.8916 | 3.4591
10 | SH-16-TL | 10-SH-16-TL | 5204.4966 | 3700.2133 | 3242.4955 | 3201.1888 | 4062.4796 | 2435.8857 | 2267.8958 | 2478.8404 | 2595.4056 | 2384.8206 | 3.8956 | 3.5595 | 3.7691 | 4.345 | 3.7878
10 | SH-16-TM | 10-SH-16-TM | 5204.991 | 3689.3541 | 3222.5913 | 3185.3823 | 4053.6165 | 2403.4717 | 2238.7226 | 2446.2309 | 2567.4297 | 2354.4179 | 3.8204 | 3.491 | 3.6957 | 4.2687 | 3.7156
10 | SH-17-CM | 10-SH-17-CM | 4416.0498 | 3167.8197 | 2863.9221 | 2831.15 | 3486.2827 | 2158.2141 | 2025.7271 | 2252.9576 | 2344.1165 | 2132.0096 | 3.3686 | 3.0913 | 3.6222 | 3.8846 | 3.3358
10 | SH-17-LM | 10-SH-17-LM | 4117.9181 | 2996.3351 | 2778.6832 | 2766.2994 | 3297.5627 | 2062.8291 | 1955.6444 | 2187.5344 | 2291.3053 | 2056.6478 | 3.3798 | 3.0793 | 3.2552 | 3.6405 | 3.2642
10 | SH-17-TH | 10-SH-17-TH | 4825.6725 | 3357.4591 | 2912.5588 | 2857.5648 | 3709.5936 | 2025.6139 | 1902.47 | 2137.1168 | 2233.6906 | 2008.2257 | 3.3233 | 3.0098 | 3.4395 | 3.6783 | 3.2391
10 | SH-17-TL | 10-SH-17-TL | 4835.4299 | 3365.8209 | 2913.8982 | 2858.493 | 3716.7082 | 2045.7688 | 1920.4712 | 2149.3089 | 2243.9149 | 2025.3022 | 3.4018 | 3.079 | 3.5114 | 3.746 | 3.3114
10 | SH-18-LH | 10-SH-18-LH | 4357.0309 | 3019.7231 | 2684.8051 | 2640.2325 | 3357.5321 | 1867.865 | 1793.3343 | 2026.9488 | 2116.0447 | 1882.5744 | 2.9213 | 2.8741 | 3.0383 | 3.3613 | 2.9684
10 | SH-18-LL | 10-SH-18-LL | 4146.2499 | 2932.0917 | 2709.1086 | 2679.875 | 3259.1021 | 1929.6317 | 1854.6752 | 2106.3057 | 2197.3777 | 1948.4951 | 2.999 | 2.955 | 3.1265 | 3.4602 | 3.0514
10 | SH-18-LM | 10-SH-18-LM | 4531.1996 | 3109.1722 | 2717.2312 | 2664.3514 | 3459.3476 | 1910.6644 | 1808.4252 | 2031.8843 | 2119.7607 | 1903.8782 | 3.2638 | 2.9431 | 3.0897 | 3.4068 | 3.1187
10 | SH-18-TM | 10-SH-18-TM | 4748.5 | 3336.1302 | 2864.093 | 2807.6826 | 3664.1683 | 1949.3077 | 1878.5377 | 2099.7173 | 2194.67 | 1964.4461 | 3.0225 | 2.9965 | 3.1776 | 3.511 | 3.0894
11 | SA-10-HH | 11-SA-10-HH | 3041.2074 | 2966.8645 | 2818.6046 | 2484.1905 | 2919.0383 | 3041.2074 | 2966.8645 | 2818.6046 | 2484.1905 | 2919.0383 | 4.1222 | 3.607 | 4.1072 | 3.7116 | 3.8879
11 | SA-10-HL | 11-SA-10-HL | 3198.7849 | 3123.2068 | 2937.0645 | 2585.666 | 3064.2821 | 3198.7849 | 3123.2068 | 2937.0645 | 2585.666 | 3064.2821 | 4.6184 | 4.0428 | 4.4588 | 4.0132 | 4.3201
11 | SA-10-HM | 11-SA-10-HM | 3113.6638 | 3039.3176 | 2862.0886 | 2520.1806 | 2983.283 | 3113.6638 | 3039.3176 | 2862.0886 | 2520.1806 | 2983.283 | 4.4144 | 3.8639 | 4.2651 | 3.8389 | 4.1299
11 | SA-10-LH | 11-SA-10-LH | 2998.0151 | 2920.4732 | 2787.9275 | 2455.2586 | 2878.0748 | 2998.0151 | 2920.4732 | 2787.9275 | 2455.2586 | 2878.0748 | 4.0088 | 3.5109 | 4.0386 | 3.6517 | 3.793
11 | SA-10-LL | 11-SA-10-LL | 3059.4397 | 2999.433 | 2816.2592 | 2478.6542 | 2936.8096 | 3059.4397 | 2999.433 | 2816.2592 | 2478.6542 | 2936.8096 | 4.2629 | 3.737 | 4.1422 | 3.727 | 3.9957
11 | SA-10-LM | 11-SA-10-LM | 3004.0686 | 2927.0168 | 2779.9924 | 2446.9399 | 2880.7193 | 3004.0686 | 2927.0168 | 2779.9924 | 2446.9399 | 2880.7193 | 4.0476 | 3.5411 | 4.0539 | 3.6663 | 3.8227
11 | SA-10-MH | 11-SA-10-MH | 2994.3971 | 2913.2865 | 2807.9654 | 2478.0458 | 2879.4902 | 2994.3971 | 2913.2865 | 2807.9654 | 2478.0458 | 2879.4902 | 3.9011 | 3.4174 | 3.9454 | 3.5719 | 3.6957
11 | SA-10-ML | 11-SA-10-ML | 3149.2325 | 3083.4679 | 2898.6044 | 2551.4458 | 3021.5391 | 3149.2325 | 3083.4679 | 2898.6044 | 2551.4458 | 3021.5391 | 4.3532 | 3.8073 | 4.2333 | 3.8143 | 4.0787
11 | SA-10-MM | 11-SA-10-MM | 3024.747 | 2949.0855 | 2790.7873 | 2475.1252 | 2901.4376 | 3024.747 | 2949.0855 | 2790.7873 | 2475.1252 | 2901.4376 | 4.0597 | 3.5354 | 3.8294 | 3.6637 | 3.7947
11 | SA-13-HH | 11-SA-13-HH | 2387.0841 | 2365.6428 | 2224.7439 | 1971.5227 | 2308.5962 | 2387.0841 | 2365.6428 | 2224.7439 | 1971.5227 | 2308.5962 | 3.4566 | 3.2679 | 3.4508 | 3.2035 | 3.3587
11 | SA-13-HL | 11-SA-13-HL | 2457.9611 | 2400.8649 | 2260.7329 | 1985.7679 | 2355.3577 | 2457.9611 | 2400.8649 | 2260.7329 | 1985.7679 | 2355.3577 | 3.6898 | 3.248 | 3.654 | 3.268 | 3.4776
11 | SA-13-HM | 11-SA-13-HM | 2383.3093 | 2356.5303 | 2195.1024 | 1934.1408 | 2295.4614 | 2383.3093 | 2356.5303 | 2195.1024 | 1934.1408 | 2295.4614 | 3.5491 | 3.3319 | 3.4042 | 3.1212 | 3.4016
11 | SA-13-LH | 11-SA-13-LH | 2294.2375 | 2235.0572 | 2133.434 | 1880.4753 | 2202.6912 | 2294.2375 | 2235.0572 | 2133.434 | 1880.4753 | 2202.6912 | 3.1561 | 2.7699 | 3.1515 | 2.8261 | 2.9788
11 | SA-13-LL | 11-SA-13-LL | 2406.9325 | 2354.469 | 2229.8071 | 1960.9383 | 2311.7859 | 2406.9325 | 2354.469 | 2229.8071 | 1960.9383 | 2311.7859 | 3.4122 | 2.9948 | 3.4091 | 3.0651 | 3.2219
11 | SA-13-LM | 11-SA-13-LM | 2402.2667 | 2346.2543 | 2225.873 | 1975.6106 | 2308.2245 | 2402.2667 | 2346.2543 | 2225.873 | 1975.6106 | 2308.2245 | 3.2842 | 2.8861 | 3.1641 | 3.0016 | 3.0925
11 | SA-13-MH | 11-SA-13-MH | 2349.948 | 2284.0871 | 2166.7363 | 1921.7054 | 2251.2784 | 2349.948 | 2284.0871 | 2166.7363 | 1921.7054 | 2251.2784 | 3.3481 | 2.9445 | 3.3253 | 3.0521 | 3.1661
11 | SA-13-ML | 11-SA-13-ML | 2405.8327 | 2349.7227 | 2204.0451 | 1936.7903 | 2303.3342 | 2405.8327 | 2349.7227 | 2204.0451 | 1936.7903 | 2303.3342 | 3.5008 | 3.0698 | 3.406 | 3.0374 | 3.2796
11 | SA-13-MM | 11-SA-13-MM | 2305.4261 | 2266.3882 | 2106.2492 | 1858.1274 | 2211.9337 | 2305.4261 | 2266.3882 | 2106.2492 | 1858.1274 | 2211.9337 | 3.3862 | 3.1695 | 3.28 | 2.9746 | 3.2461
11 | SA-14-HH | 11-SA-14-HH | 2341.5218 | 2282.2682 | 2154.7753 | 1895.7568 | 2242.6738 | 2341.5218 | 2282.2682 | 2154.7753 | 1895.7568 | 2242.6738 | 3.3497 | 2.9384 | 3.2819 | 2.9324 | 3.1446
11 | SA-14-HL | 11-SA-14-HL | 2248.2034 | 2213.1713 | 2057.8151 | 1813.7667 | 2158.8438 | 2248.2034 | 2213.1713 | 2057.8151 | 1813.7667 | 2158.8438 | 3.3509 | 3.1474 | 3.265 | 2.9532 | 3.2198
11 | SA-14-HM | 11-SA-14-HM | 2359.5504 | 2298.8119 | 2174.5556 | 1910.9062 | 2260.071 | 2359.5504 | 2298.8119 | 2174.5556 | 1910.9062 | 2260.071 | 3.4305 | 3.016 | 3.4 | 3.0412 | 3.2326
11 | SA-14-MH | 11-SA-14-MH | 2268.5226 | 2215.3544 | 2113.0351 | 1879.3986 | 2182.7392 | 2268.5226 | 2215.3544 | 2113.0351 | 1879.3986 | 2182.7392 | 3.0521 | 2.6841 | 2.956 | 2.8155 | 2.8798
11 | SA-14-ML | 11-SA-14-ML | 2280.7005 | 2227.7867 | 2107.0376 | 1852.4507 | 2187.9475 | 2280.7005 | 2227.7867 | 2107.0376 | 1852.4507 | 2187.9475 | 3.3155 | 2.92 | 3.3099 | 2.9678 | 3.1326
11 | SA-14-MM | 11-SA-14-MM | 2241.4939 | 2187.2204 | 2077.391 | 1845.8213 | 2153.379 | 2241.4939 | 2187.2204 | 2077.391 | 1845.8213 | 2153.379 | 3.085 | 2.7106 | 2.975 | 2.8297 | 2.9064
11 | SA-15-HH | 11-SA-15-HH | 2084.1975 | 2062.819 | 1932.6644 | 1713.1998 | 2012.4334 | 2084.1975 | 2062.819 | 1932.6644 | 1713.1998 | 2012.4334 | 3.0921 | 2.9112 | 2.9818 | 2.7396 | 2.9711
11 | SA-15-HL | 11-SA-15-HL | 2059.6849 | 2032.7752 | 1897.0415 | 1677.9585 | 1983.1794 | 2059.6849 | 2032.7752 | 1897.0415 | 1677.9585 | 1983.1794 | 3.1459 | 2.9617 | 3.0602 | 2.7683 | 3.0241
11 | SA-15-HM | 11-SA-15-HM | 2054.8501 | 2033.4493 | 1899.6386 | 1680.2501 | 1982.1564 | 2054.8501 | 2033.4493 | 1899.6386 | 1680.2501 | 1982.1564 | 3.0245 | 2.8382 | 2.8907 | 2.6432 | 2.895
11 | SA-15-MH | 11-SA-15-MH | 2184.8583 | 2126.5279 | 2027.917 | 1789.1969 | 2096.266 | 2184.8583 | 2126.5279 | 2027.917 | 1789.1969 | 2096.266 | 3.179 | 2.8013 | 3.1945 | 2.8667 | 3.0095
11 | SA-15-ML | 11-SA-15-ML | 2117.6677 | 2069.3649 | 1955.9735 | 1719.5783 | 2031.7275 | 2117.6677 | 2069.3649 | 1955.9735 | 1719.5783 | 2031.7275 | 3.0758 | 2.7018 | 3.0519 | 2.7316 | 2.8985
11 | SA-15-MM | 11-SA-15-MM | 2128.6411 | 2074.7622 | 1961.3476 | 1724.0918 | 2039.1917 | 2128.6411 | 2074.7622 | 1961.3476 | 1724.0918 | 2039.1917 | 3.1322 | 2.7535 | 3.0974 | 2.7674 | 2.9494
11 | SA-16-CH | 11-SA-16-CH | 2478.0657 | 2347.552 | 2109.1813 | 1854.43 | 2308.1902 | 2478.0657 | 2347.552 | 2109.1813 | 1854.43 | 2308.1902 | 3.308 | 2.8918 | 3.2275 | 2.9013 | 3.1007
11 | SA-16-CL | 11-SA-16-CL | 2321.4133 | 2227.5714 | 1968.1556 | 1735.8234 | 2171.2229 | 2321.4133 | 2227.5714 | 1968.1556 | 1735.8234 | 2171.2229 | 3.3449 | 3.0895 | 3.0247 | 2.7702 | 3.1428
11 | SA-16-CM | 11-SA-16-CM | 2395.0949 | 2303.6217 | 2043.7891 | 1805.3589 | 2245.5276 | 2395.0949 | 2303.6217 | 2043.7891 | 1805.3589 | 2245.5276 | 3.3285 | 3.1029 | 3.075 | 2.8321 | 3.1552
11 | SA-16-LH | 11-SA-16-LH | 2094.6759 | 2006.9557 | 1855.2196 | 1638.497 | 1977.2971 | 2094.6759 | 2006.9557 | 1855.2196 | 1638.497 | 1977.2971 | 3.1065 | 2.703 | 2.9242 | 2.5885 | 2.8768
11 | SA-16-LL | 11-SA-16-LL | 2229.0913 | 2133.9934 | 1939.7872 | 1707.9043 | 2094.6848 | 2229.0913 | 2133.9934 | 1939.7872 | 1707.9043 | 2094.6848 | 3.3329 | 2.8964 | 3.1226 | 2.7632 | 3.0816
11 | SA-16-LM | 11-SA-16-LM | 2215.037 | 2125.4648 | 1944.0046 | 1711.4999 | 2087.1535 | 2215.037 | 2125.4648 | 1944.0046 | 1711.4999 | 2087.1535 | 3.2155 | 2.7983 | 3.0441 | 2.7018 | 2.9829
11 | SA-16-NM | 11-SA-16-NM | 2005.7289 | 1934.6894 | 1727.497 | 1518.4383 | 1885.3982 | 2005.7289 | 1934.6894 | 1727.497 | 1518.4383 | 1885.3982 | 3.0344 | 2.6387 | 2.7762 | 2.4418 | 2.7885
11 | SA-16-TH | 11-SA-16-TH | 2591.4021 | 2420.24 | 2207.9619 | 1950.9269 | 2403.0585 | 2591.4021 | 2420.24 | 2207.9619 | 1950.9269 | 2403.0585 | 3.5951 | 3.1357 | 3.3853 | 3.023 | 3.3354
11 | SA-16-TL | 11-SA-16-TL | 2327.7586 | 2219.3683 | 1942.3846 | 1718.1973 | 2165.2044 | 2327.7586 | 2219.3683 | 1942.3846 | 1718.1973 | 2165.2044 | 3.5035 | 3.2455 | 3.2017 | 2.8767 | 3.2968
11 | SA-17-CH | 11-SA-17-CH | 2289.4938 | 2176.2233 | 1953.9101 | 1717.1699 | 2136.318 | 2289.4938 | 2176.2233 | 1953.9101 | 1717.1699 | 2136.318 | 3.1758 | 2.7747 | 3.0677 | 2.7508 | 2.968
11 | SA-17-CL | 11-SA-17-CL | 2278.4824 | 2166.5304 | 1933.4239 | 1698.9319 | 2123.6447 | 2278.4824 | 2166.5304 | 1933.4239 | 1698.9319 | 2123.6447 | 3.2155 | 2.8039 | 3.011 | 2.6977 | 2.9799
11 | SA-17-CM | 11-SA-17-CM | 2312.079 | 2192.7795 | 1957.8031 | 1721.4892 | 2152.0711 | 2312.079 | 2192.7795 | 1957.8031 | 1721.4892 | 2152.0711 | 3.2035 | 2.7957 | 3.0465 | 2.7972 | 2.9889
11 | SA-17-LH | 11-SA-17-LH | 2052.3118 | 1966.8832 | 1795.7592 | 1597.5124 | 1933.5975 | 2052.3118 | 1966.8832 | 1795.7592 | 1597.5124 | 1933.5975 | 3.0427 | 2.6479 | 2.7787 | 2.5473 | 2.8077
11 | SA-17-LL | 11-SA-17-LL | 2153.8497 | 2058.5268 | 1863.4696 | 1639.2656 | 2019.9931 | 2153.8497 | 2058.5268 | 1863.4696 | 1639.2656 | 2019.9931 | 3.2077 | 2.7865 | 3.0103 | 2.6664 | 2.9669
11 | SA-17-LM | 11-SA-17-LM | 2142.0656 | 2054.0305 | 1868.1918 | 1644.2705 | 2015.0209 | 2142.0656 | 2054.0305 | 1868.1918 | 1644.2705 | 2015.0209 | 3.1787 | 2.7629 | 2.9723 | 2.6326 | 2.9381
11 | SA-17-TH | 11-SA-17-TH | 2184.4973 | 2064.5553 | 1917.6158 | 1694.6151 | 2047.9346 | 2184.4973 | 2064.5553 | 1917.6158 | 1694.6151 | 2047.9346 | 3.0887 | 2.7011 | 2.9814 | 2.6703 | 2.8866
11 | SA-17-TL | 11-SA-17-TL | 2026.0899 | 1930.1727 | 1706.871 | 1506.3788 | 1887.5118 | 2026.0899 | 1930.1727 | 1706.871 | 1506.3788 | 1887.5118 | 3.3183 | 3.0094 | 2.9376 | 2.667 | 3.0798
11 | SA-17-TM | 11-SA-17-TM | 2395.2874 | 2278.1453 | 1965.649 | 1746.5237 | 2219.0041 | 2395.2874 | 2278.1453 | 1965.649 | 1746.5237 | 2219.0041 | 3.2286 | 3.0694 | 3.1133 | 2.8822 | 3.1154
11 | SA-18-LH | 11-SA-18-LH | 2004.8886 | 1917.5262 | 1750.4233 | 1541.828 | 1884.7955 | 2004.8886 | 1917.5262 | 1750.4233 | 1541.828 | 1884.7955 | 2.9638 | 2.5778 | 2.7811 | 2.4626 | 2.7423
11 | SA-18-LL | 11-SA-18-LL | 1961.2938 | 1880.9503 | 1710.4941 | 1504.7777 | 1844.9732 | 1961.2938 | 1880.9503 | 1710.4941 | 1504.7777 | 1844.9732 | 2.9801 | 2.5927 | 2.802 | 2.4811 | 2.759
11 | SA-18-TH | 11-SA-18-TH | 2091.9708 | 2023.0652 | 1827.6468 | 1635.9619 | 1977.9626 | 2091.9708 | 2023.0652 | 1827.6468 | 1635.9619 | 1977.9626 | 2.9477 | 2.7669 | 2.7962 | 2.5585 | 2.8168
11 | SA-18-TL | 11-SA-18-TL | 2298.6522 | 2150.9165 | 1956.9819 | 1738.1463 | 2133.7319 | 2298.6522 | 2150.9165 | 1956.9819 | 1738.1463 | 2133.7319 | 3.2489 | 2.8409 | 3.1833 | 2.9596 | 3.0603
11 | SA-18-TM | 11-SA-18-TM | 2160.6207 | 2041.7074 | 1888.5733 | 1668.0006 | 2023.4038 | 2160.6207 | 2041.7074 | 1888.5733 | 1668.0006 | 2023.4038 | 3.043 | 2.6579 | 2.9011 | 2.5974 | 2.8339
11 | SH-10-HH | 11-SH-10-HH | 8398.4911 | 6559.0508 | 5269.8396 | 4555.6001 | 6820.7439 | 2950.9303 | 2929.5479 | 2754.6925 | 2453.4512 | 2859.7182 | 4.1302 | 3.8937 | 4.0458 | 3.725 | 3.9806
11 | SH-10-HL | 11-SH-10-HL | 8525.969 | 6699.8153 | 5366.385 | 4619.8 | 6942.0584 | 3059.756 | 3031.3724 | 2835.7739 | 2511.0924 | 2956.257 | 4.3488 | 4.0921 | 4.2471 | 3.9098 | 4.1852
11 | SH-10-HM | 11-SH-10-HM | 8319.0775 | 6547.1117 | 5316.7163 | 4556.915 | 6793.9711 | 3046.3789 | 2967.4871 | 2817.2538 | 2481.4974 | 2920.6252 | 4.2336 | 3.7113 | 4.2091 | 3.7846 | 3.9756
11 | SH-10-LH | 11-SH-10-LH | 8731.0732 | 6709.2022 | 5391.8516 | 4623.6387 | 7023.5758 | 2942.2168 | 2867.9098 | 2770.7089 | 2445.283 | 2833.7619 | 3.8803 | 3.4027 | 3.9187 | 3.5432 | 3.6609
11 | SH-10-LL | 11-SH-10-LL | 8727.1714 | 6744.1716 | 5330.1245 | 4563.7896 | 7020.6719 | 2997.715 | 2926.0131 | 2760.4783 | 2430.848 | 2873.4417 | 4.146 | 3.6351 | 4.1025 | 3.6815 | 3.8881
11 | SH-10-LM | 11-SH-10-LM | 8458.9745 | 6572.8859 | 5265.2866 | 4512.9753 | 6842.523 | 2924.702 | 2853.2197 | 2712.1177 | 2391.8091 | 2807.7034 | 3.9741 | 3.4891 | 3.9413 | 3.5363 | 3.7308
11 | SH-10-MH | 11-SH-10-MH | 8744.0285 | 6733.4888 | 5382.3789 | 4611.8633 | 7035.1133 | 2984.9559 | 2906.8743 | 2785.5396 | 2455.1296 | 2867.5174 | 4.0477 | 3.5453 | 4.0645 | 3.67 | 3.8111
11 | SH-10-ML | 11-SH-10-ML | 8418.194 | 6594.1963 | 5251.8427 | 4498.7072 | 6832.7012 | 3076.3385 | 2999.5938 | 2814.4894 | 2475.8665 | 2942.954 | 4.3721 | 3.832 | 4.3142 | 3.8664 | 4.0962
11 | SH-10-MM | 11-SH-10-MM | 8584.2479 | 6697.9885 | 5371.6773 | 4599.8504 | 6960.8259 | 3058.9868 | 2981.389 | 2830.5865 | 2491.9511 | 2933.5937 | 4.1615 | 3.6389 | 4.1477 | 3.7455 | 3.9086
11 | SH-13-HH | 11-SH-13-HH | 7969.1895 | 5987.6943 | 4726.9801 | 4072.9214 | 6314.4972 | 2483.863 | 2459.0364 | 2305.3806 | 2047.3364 | 2400.6032 | 3.5968 | 3.3731 | 3.4689 | 3.2026 | 3.4475
11 | SH-13-HL | 11-SH-13-HL | 7107.3154 | 5416.393 | 4282.4901 | 3669.3108 | 5674.6051 | 2370.392 | 2338.6729 | 2181.7826 | 1923.3251 | 2281.8731 | 3.6046 | 3.4127 | 3.5848 | 3.286 | 3.491
11 | SH-13-HM | 11-SH-13-HM | 7253.3722 | 5551.658 | 4420.3287 | 3799.5644 | 5813.5455 | 2429.1224 | 2401.9131 | 2243.8608 | 1983.4934 | 2342.9823 | 3.5383 | 3.306 | 3.3921 | 3.1305 | 3.3817
11 | SH-13-LH | 11-SH-13-LH | 8565.3705 | 6260.9369 | 4655.0296 | 3981.4458 | 6616.0527 | 2344.9938 | 2285.2309 | 2194.0339 | 1933.7828 | 2254.6926 | 3.1907 | 2.803 | 3.2322 | 2.9157 | 3.0139
11 | SH-13-LL | 11-SH-13-LL | 7385.4617 | 5555.2051 | 4281.5382 | 3659.6422 | 5827.8832 | 2273.1455 | 2213.7662 | 2084.5019 | 1835.4278 | 2174.876 | 3.2952 | 2.896 | 3.272 | 2.9324 | 3.0952
11 | SH-13-LM | 11-SH-13-LM | 6665.9865 | 5197.3242 | 4161.0295 | 3587.7446 | 5404.1968 | 2439.6606 | 2383.339 | 2256.2491 | 2000.7816 | 2343.1657 | 3.3579 | 2.9526 | 3.2381 | 3.0691 | 3.1507
11 | SH-13-MH | 11-SH-13-MH | 7887.1327 | 5844.3698 | 4587.1063 | 3950.8808 | 6196.1367 | 2286.4267 | 2268.4844 | 2141.9519 | 1900.8694 | 2216.2356 | 3.2861 | 3.1079 | 3.2283 | 2.9603 | 3.1718
11 | SH-13-ML | 11-SH-13-ML | 7733.1116 | 5852.0195 | 4548.1536 | 3885.4832 | 6130.9062 | 2497.6227 | 2443.6243 | 2325.5223 | 2042.9885 | 2401.7943 | 3.6005 | 3.1677 | 3.6464 | 3.2947 | 3.4032
11 | SH-13-MM | 11-SH-13-MM | 7440.3112 | 5712.172 | 4510.1535 | 3854.1681 | 5962.0147 | 2418.902 | 2355.9203 | 2228.112 | 1960.45 | 2316.5926 | 3.5309 | 3.0995 | 3.4973 | 3.1274 | 3.3123
11 | SH-14-HH | 11-SH-14-HH | 7384.7194 | 5560.815 | 4393.8752 | 3774.4214 | 5858.0447 | 2350.222 | 2323.8536 | 2171.9061 | 1919.7086 | 2267.0617 | 3.4569 | 3.2308 | 3.3068 | 3.0512 | 3.3024
11 | SH-14-HL | 11-SH-14-HL | 7415.1993 | 5482.2281 | 4259.0986 | 3641.2014 | 5804.9733 | 2276.5023 | 2247.4928 | 2085.6046 | 1834.6589 | 2189.3201 | 3.4006 | 3.1745 | 3.234 | 2.9661 | 3.2406
11 | SH-14-HM | 11-SH-14-HM | 7298.2346 | 5440.7302 | 4260.789 | 3657.3393 | 5748.6459 | 2262.6031 | 2239.4695 | 2088.0064 | 1844.5738 | 2182.6215 | 3.2881 | 3.0638 | 3.123 | 2.8762 | 3.1315
11 | SH-14-MH | 11-SH-14-MH | 7822.1691 | 5748.2944 | 4306.079 | 3683.1502 | 6066.7429 | 2185.1946 | 2130.7726 | 2042.7735 | 1800.634 | 2101.1496 | 3 | 2.6366 | 3.0281 | 2.7225 | 2.8306
11 | SH-14-ML | 11-SH-14-ML | 8314.2946 | 5844.0666 | 4339.442 | 3706.0983 | 6288.718 | 2221.8672 | 2182.9101 | 2029.1624 | 1788.2529 | 2131.4838 | 3.2592 | 3.0615 | 3.1619 | 2.8586 | 3.1235
11 | SH-14-MM | 11-SH-14-MM | 7224.1408 | 5411.4485 | 4149.4956 | 3545.231 | 5682.7 | 2211.5655 | 2161.011 | 2045.5577 | 1798.5764 | 2122.613 | 3.1815 | 2.7957 | 3.1671 | 2.8356 | 2.9898
11 | SH-15-HH | 11-SH-15-HH | 8407.7442 | 5941.5265 | 4377.0491 | 3750.0496 | 6370.5499 | 2086.9187 | 2067.0327 | 1933.5023 | 1713.364 | 2016.1078 | 3.026 | 2.8315 | 2.8857 | 2.6507 | 2.8886
11 | SH-15-HL | 11-SH-15-HL | 6369.1966 | 4839.8701 | 3833.0202 | 3284.3547 | 5078.7257 | 2109.5014 | 2084.2993 | 1939.1606 | 1708.5922 | 2031.224 | 3.1446 | 2.9472 | 3.0463 | 2.7867 | 3.0138
11 | SH-15-HM | 11-SH-15-HM | 6558.0402 | 4888.709 | 3875.5937 | 3321.6141 | 5175.8867 | 2042.9872 | 2024.4872 | 1895.0504 | 1670.7701 | 1973.6138 | 3.0627 | 2.8797 | 2.9547 | 2.6839 | 2.9338
11 | SH-15-MH | 11-SH-15-MH | 7692.6084 | 5596.2504 | 4156.2514 | 3547.2234 | 5924.927 | 2157.1437 | 2098.764 | 1993.0793 | 1751.8174 | 2066.2649 | 3.1353 | 2.7551 | 3.0871 | 2.7584 | 2.9377
11 | SH-15-ML | 11-SH-15-ML | 7324.9225 | 5224.9785 | 3955.6337 | 3380.6646 | 5601.2728 | 2079.223 | 2042.2418 | 1895.8642 | 1670.1088 | 1993.6487 | 3.1034 | 2.9107 | 2.9962 | 2.7006 | 2.9681
11 | SH-15-MM | 11-SH-15-MM | 7453.7264 | 5382.6518 | 4105.1922 | 3511.9614 | 5744.4547 | 2033.5439 | 2011.251 | 1881.9575 | 1661.1099 | 1962.1685 | 3.0358 | 2.8626 | 2.9483 | 2.6858 | 2.9167
11 | SH-16-CH | 11-SH-16-CH | 8267.4296 | 6032.2594 | 4270.5946 | 3645.2894 | 6329.0815 | 2370.31 | 2288.1799 | 2031.4287 | 1795.5523 | 2227.2495 | 3.2603 | 3.0338 | 3.0185 | 2.784 | 3.0852
11 | SH-16-CL | 11-SH-16-CL | 7962.4002 | 5832.5105 | 4167.5295 | 3550.7481 | 6116.4002 | 2456.5729 | 2361.711 | 2074.5884 | 1824.9265 | 2296.2547 | 3.3478 | 3.2012 | 3.2684 | 3.0505 | 3.2462
11 | SH-16-LH | 11-SH-16-LH | 8318.8225 | 5983.0905 | 4224.0651 | 3620.387 | 6319.2713 | 2131.9261 | 2039.7435 | 1911.4921 | 1689.4157 | 2015.9819 | 3.1028 | 2.7023 | 2.9479 | 2.6185 | 2.8707
11 | SH-16-LL | 11-SH-16-LL | 8044.2223 | 5807.4737 | 4063.8038 | 3473.9163 | 6113.3433 | 2225.9438 | 2136.4438 | 1945.338 | 1711.2403 | 2094.7119 | 3.3002 | 2.8703 | 3.1301 | 2.7787 | 3.0503
11 | SH-16-LM | 11-SH-16-LM | 8506.7717 | 6120.9594 | 4286.9191 | 3664.174 | 6454.3722 | 2217.0788 | 2123.6363 | 1952.6731 | 1740.1008 | 2090.7704 | 3.2305 | 2.8129 | 2.9683 | 2.7387 | 2.9762
11 | SH-16-TH | 11-SH-16-TH | 9550.8745 | 6938.1747 | 4755.7244 | 4060.1361 | 7258.4461 | 2289.932 | 2200.7683 | 1964.0598 | 1751.7269 | 2150.0214 | 3.4038 | 3.1777 | 3.1738 | 2.8704 | 3.224
11 | SH-16-TL | 11-SH-16-TL | 9796.3733 | 7099.3602 | 4912.5968 | 4185.5589 | 7445.4078 | 2591.176 | 2427.783 | 2175.1527 | 1913.7352 | 2394.2955 | 3.6167 | 3.1576 | 3.4695 | 3.1002 | 3.3591
11 | SH-16-TM | 11-SH-16-TM | 9818.9874 | 7112.6343 | 4927.5488 | 4199.788 | 7462.3856 | 2555.0027 | 2393.7511 | 2149.4939 | 1891.937 | 2362.0116 | 3.5467 | 3.0957 | 3.401 | 3.0439 | 3.294
11 | SH-17-CM | 11-SH-17-CM | 8301.4357 | 5951.9524 | 4144.9189 | 3521.7775 | 6278.9437 | 2324.7937 | 2235.6986 | 1965.763 | 1729.5398 | 2173.9586 | 3.187 | 3.0456 | 3.1074 | 2.9006 | 3.0886
11 | SH-17-LM | 11-SH-17-LM | 7799.0557 | 5621.5358 | 3969.9021 | 3398.4748 | 5931.0431 | 2179.1493 | 2079.6645 | 1910.4947 | 1684.4004 | 2047.8968 | 3.1408 | 2.7346 | 3.0574 | 2.7476 | 2.9265
11 | SH-17-TH | 11-SH-17-TH | 9415.3166 | 6829.8169 | 4661.1051 | 3972.4812 | 7144.4868 | 2171.8667 | 2093.2072 | 1874.3863 | 1666.9255 | 2043.6755 | 3.1816 | 2.9855 | 3.015 | 2.7534 | 3.034
11 | SH-17-TL | 11-SH-17-TL | 9441.0035 | 6831.3892 | 4642.5212 | 3950.2117 | 7149.3208 | 2196.6908 | 2113.2471 | 1883.7533 | 1671.8031 | 2062.2769 | 3.2492 | 3.0457 | 3.0738 | 2.7925 | 3.0943
11 | SH-18-LH | 11-SH-18-LH | 8614.0403 | 6144.1168 | 4146.9033 | 3504.9381 | 6465.0708 | 2034.6872 | 1947.5287 | 1771.2229 | 1566.6584 | 1911.9713 | 3.0254 | 2.6326 | 2.783 | 2.5709 | 2.7877
11 | SH-18-LL | 11-SH-18-LL | 8028.1254 | 5751.8072 | 3978.1975 | 3376.8871 | 6063.2021 | 2104.4138 | 2018.7788 | 1837.2476 | 1623.5686 | 1980.3422 | 3.1285 | 2.7247 | 2.8828 | 2.6622 | 2.8847
11 | SH-18-LM | 11-SH-18-LM | 8974.2496 | 6386.5688 | 4208.758 | 3590.5284 | 6707.7089 | 2039.7567 | 1949.0735 | 1772.2137 | 1559.5097 | 1913.73 | 3.0634 | 2.6636 | 2.9031 | 2.576 | 2.8304
11 | SH-18-TM | 11-SH-18-TM | 9464.2961 | 6792.9596 | 4646.7837 | 3956.9121 | 7144.0486 | 2158.3203 | 2041.0664 | 1864.8021 | 1660.213 | 2016.3681 | 3.1437 | 2.7387 | 2.9159 | 2.7202 | 2.9067
12 | SA-10-HH | 12-SA-10-HH | 2229.347 | 2210.0627 | 2072.0646 | 1804.8081 | 2164.4964 | 2229.347 | 2210.0627 | 2072.0646 | 1804.8081 | 2164.4964 | 4.0834 | 3.5814 | 3.9516 | 3.5711 | 3.8377
12 | SA-10-HL | 12-SA-10-HL | 2342.2219 | 2325.539 | 2172.2182 | 1887.0925 | 2273.9904 | 2342.2219 | 2325.539 | 2172.2182 | 1887.0925 | 2273.9904 | 4.5442 | 3.977 | 4.3675 | 3.9255 | 4.2597
12 | SA-10-HM | 12-SA-10-HM | 2275.1898 | 2258.6831 | 2113.3738 | 1837.7622 | 2209.6213 | 2275.1898 | 2258.6831 | 2113.3738 | 1837.7622 | 2209.6213 | 4.221 | 3.672 | 4.0197 | 3.6252 | 3.9424
12 | SA-10-LH | 12-SA-10-LH | 2130.5474 | 2115.4724 | 2014.3732 | 1751.1654 | 2076.1813 | 2130.5474 | 2115.4724 | 2014.3732 | 1751.1654 | 2076.1813 | 3.9166 | 3.4358 | 3.8525 | 3.4807 | 3.6935
12 | SA-10-LL | 12-SA-10-LL | 2258.8945 | 2254.2739 | 2105.8108 | 1830.3093 | 2199.4806 | 2258.8945 | 2254.2739 | 2105.8108 | 1830.3093 | 2199.4806 | 4.2074 | 3.6908 | 4.0567 | 3.6465 | 3.9497
12 | SA-10-LM | 12-SA-10-LM | 2145.9062 | 2131.2924 | 2016.8669 | 1752.8145 | 2088.9453 | 2145.9062 | 2131.2924 | 2016.8669 | 1752.8145 | 2088.9453 | 3.9675 | 3.4766 | 3.8769 | 3.5022 | 3.735
12 | SA-10-MH | 12-SA-10-MH | 2143.4285 | 2124.9866 | 2038.0293 | 1776.247 | 2090.2188 | 2143.4285 | 2124.9866 | 2038.0293 | 1776.247 | 2090.2188 | 3.8154 | 3.3477 | 3.771 | 3.4098 | 3.6022
12 | SA-10-ML | 12-SA-10-ML | 2325.2908 | 2315.9393 | 2161.9234 | 1878.7276 | 2261.2907 | 2325.2908 | 2315.9393 | 2161.9234 | 1878.7276 | 2261.2907 | 4.2839 | 3.7562 | 4.1765 | 3.7538 | 4.03
12 | SA-10-MM | 12-SA-10-MM | 2137.4259 | 2120.8835 | 2005.7442 | 1753.8343 | 2080.3497 | 2137.4259 | 2120.8835 | 2005.7442 | 1753.8343 | 2080.3497 | 4.0115 | 3.5148 | 3.7174 | 3.5151 | 3.7506
12 | SA-13-HH | 12-SA-13-HH | 1739.4426 | 1748.6717 | 1638.7375 | 1430.8633 | 1702.3248 | 1739.4426 | 1748.6717 | 1638.7375 | 1430.8633 | 1702.3248 | 3.3984 | 3.2114 | 3.3196 | 3.0761 | 3.2911
12 | SA-13-HL | 12-SA-13-HL | 1727.23 | 1715.061 | 1617.0543 | 1402.6282 | 1679.7408 | 1727.23 | 1715.061 | 1617.0543 | 1402.6282 | 1679.7408 | 3.5559 | 3.151 | 3.4664 | 3.1775 | 3.3629
12 | SA-13-HM | 12-SA-13-HM | 1738.6286 | 1746.8716 | 1628.0585 | 1415.9685 | 1698.6997 | 1738.6286 | 1746.8716 | 1628.0585 | 1415.9685 | 1698.6997 | 3.4787 | 3.2683 | 3.3224 | 3.0641 | 3.3454
12 | SA-13-LH | 12-SA-13-LH | 1639.5642 | 1627.3867 | 1551.6569 | 1355.5118 | 1598.4288 | 1639.5642 | 1627.3867 | 1551.6569 | 1355.5118 | 1598.4288 | 3.0663 | 2.7051 | 3.0149 | 2.7905 | 2.9032
12 | SA-13-LL | 12-SA-13-LL | 1724.1827 | 1716.4506 | 1616.8211 | 1402.0835 | 1678.865 | 1724.1827 | 1716.4506 | 1616.8211 | 1402.0835 | 1678.865 | 3.3194 | 2.9325 | 3.2474 | 2.9303 | 3.134
12 | SA-13-LM | 12-SA-13-LM | 1705.161 | 1696.5179 | 1616.4301 | 1404.7814 | 1663.6872 | 1705.161 | 1696.5179 | 1616.4301 | 1404.7814 | 1663.6872 | 3.1914 | 2.8179 | 3.1636 | 2.857 | 3.0211
12 | SA-13-MH | 12-SA-13-MH | 1681.55 | 1686.0214 | 1574.8469 | 1374.7093 | 1642.1754 | 1681.55 | 1686.0214 | 1574.8469 | 1374.7093 | 1642.1754 | 3.2168 | 3.0363 | 3.1537 | 2.9244 | 3.1165
12 | SA-13-ML | 12-SA-13-ML | 1703.7782 | 1695.3676 | 1587.5906 | 1378.4697 | 1656.8988 | 1703.7782 | 1695.3676 | 1587.5906 | 1378.4697 | 1656.8988 | 3.4168 | 3.0195 | 3.2947 | 2.9562 | 3.2151
12 | SA-13-MM | 12-SA-13-MM | 1669.646 | 1669.0052 | 1544.0208 | 1344.9251 | 1624.563 | 1669.646 | 1669.0052 | 1544.0208 | 1344.9251 | 1624.563 | 3.3126 | 3.1027 | 3.202 | 2.9236 | 3.1871
12 | SA-14-HH | 12-SA-14-HH | 1662.5257 | 1651.7784 | 1557.3579 | 1353.646 | 1617.6016 | 1662.5257 | 1651.7784 | 1557.3579 | 1353.646 | 1617.6016 | 3.2606 | 2.8799 | 3.1668 | 2.8485 | 3.0728
12 | SA-14-HL | 12-SA-14-HL | 1606.2978 | 1605.0885 | 1500.1559 | 1302.4212 | 1565.1993 | 1606.2978 | 1605.0885 | 1500.1559 | 1302.4212 | 1565.1993 | 3.2666 | 3.0484 | 3.1213 | 2.8607 | 3.1325
12 | SA-14-HM | 12-SA-14-HM | 1644.1701 | 1629.7075 | 1544.5516 | 1339.7401 | 1598.9492 | 1644.1701 | 1629.7075 | 1544.5516 | 1339.7401 | 1598.9492 | 3.3054 | 2.9176 | 3.2242 | 2.8999 | 3.1171
12 | SA-14-MH | 12-SA-14-MH | 1621.0042 | 1612.2632 | 1526.1298 | 1338.9077 | 1580.5012 | 1621.0042 | 1612.2632 | 1526.1298 | 1338.9077 | 1580.5012 | 2.9671 | 2.6176 | 2.8234 | 2.6741 | 2.796
12 | SA-14-ML | 12-SA-14-ML | 1604.2929 | 1595.1064 | 1509.9786 | 1310.942 | 1562.6382 | 1604.2929 | 1595.1064 | 1509.9786 | 1310.942 | 1562.6382 | 3.1926 | 2.8277 | 3.1296 | 2.8127 | 3.0171
12 | SA-14-MM | 12-SA-14-MM | 1588.784 | 1580.2338 | 1495.3758 | 1310.115 | 1548.8399 | 1588.784 | 1580.2338 | 1495.3758 | 1310.115 | 1548.8399 | 2.9941 | 2.6453 | 2.8414 | 2.6874 | 2.821
12 | SA-15-HH | 12-SA-15-HH | 1516.7625 | 1523.7891 | 1426.7104 | 1246.3091 | 1483.6388 | 1516.7625 | 1523.7891 | 1426.7104 | 1246.3091 | 1483.6388 | 3.0237 | 2.8453 | 2.8932 | 2.6769 | 2.9114
12 | SA-15-HL | 12-SA-15-HL | 1479.7758 | 1481.5085 | 1387.1414 | 1205.1397 | 1444.0382 | 1479.7758 | 1481.5085 | 1387.1414 | 1205.1397 | 1444.0382 | 3.0442 | 2.8479 | 2.9225 | 2.6828 | 2.925
12 | SA-15-HM | 12-SA-15-HM | 1504.7804 | 1508.7299 | 1408.2922 | 1227.5335 | 1469.1616 | 1504.7804 | 1508.7299 | 1408.2922 | 1227.5335 | 1469.1616 | 2.933 | 2.7534 | 2.7955 | 2.5803 | 2.8189
12 | SA-15-MH | 12-SA-15-MH | 1529.7234 | 1513.9684 | 1443.8634 | 1251.5991 | 1488.0774 | 1529.7234 | 1513.9684 | 1443.8634 | 1251.5991 | 1488.0774 | 3.0535 | 2.6995 | 3.0151 | 2.7114 | 2.8883
12 | SA-15-ML | 12-SA-15-ML | 1510.4481 | 1502.3072 | 1412.7896 | 1221.0163 | 1469.1564 | 1510.4481 | 1502.3072 | 1412.7896 | 1221.0163 | 1469.1564 | 2.9871 | 2.6404 | 2.9122 | 2.6156 | 2.8176
12 | SA-15-MM | 12-SA-15-MM | 1498.5996 | 1486.4865 | 1405.6973 | 1217.6505 | 1457.2043 | 1498.5996 | 1486.4865 | 1405.6973 | 1217.6505 | 1457.2043 | 3.0139 | 2.6665 | 2.9386 | 2.6333 | 2.8433
12 | SA-16-CH | 12-SA-16-CH | 1844.7116 | 1775.573 | 1593.6928 | 1386.2828 | 1747.7829 | 1844.7116 | 1775.573 | 1593.6928 | 1386.2828 | 1747.7829 | 3.2164 | 2.816 | 3.1464 | 2.9469 | 3.0375
12 | SA-16-CL | 12-SA-16-CL | 1736.9332 | 1692.1099 | 1494.2849 | 1301.1579 | 1651.9316 | 1736.9332 | 1692.1099 | 1494.2849 | 1301.1579 | 1651.9316 | 3.2655 | 3.0219 | 2.9725 | 2.7416 | 3.0941
12 | SA-16-CM | 12-SA-16-CM | 1791.683 | 1753.0484 | 1550.9619 | 1351.2835 | 1708.7205 | 1791.683 | 1753.0484 | 1550.9619 | 1351.2835 | 1708.7205 | 3.2818 | 3.0843 | 3.0772 | 2.8542 | 3.1464
12 | SA-16-LH | 12-SA-16-LH | 1570.8967 | 1527.2007 | 1407.6048 | 1225.4773 | 1503.8874 | 1570.8967 | 1527.2007 | 1407.6048 | 1225.4773 | 1503.8874 | 3.027 | 2.6326 | 2.8199 | 2.5275 | 2.813
12 | SA-16-LL | 12-SA-16-LL | 1670.3725 | 1624.7526 | 1468.6152 | 1275.6304 | 1593.6235 | 1670.3725 | 1624.7526 | 1468.6152 | 1275.6304 | 1593.6235 | 3.2735 | 2.8492 | 3.0195 | 2.6986 | 3.0361
12 | SA-16-LM | 12-SA-16-LM | 1650.2929 | 1607.4464 | 1464.3054 | 1271.2998 | 1577.8398 | 1650.2929 | 1607.4464 | 1464.3054 | 1271.2998 | 1577.8398 | 3.1536 | 2.7452 | 2.9323 | 2.6265 | 2.9303
12 | SA-16-NM | 12-SA-16-NM | 1514.3261 | 1480.7612 | 1326.0709 | 1149.1029 | 1446.2778 | 1514.3261 | 1480.7612 | 1326.0709 | 1149.1029 | 1446.2778 | 2.9637 | 2.5644 | 2.6605 | 2.3764 | 2.7286
12 | SA-16-TH | 12-SA-16-TH | 1941.9003 | 1839.1465 | 1656.4714 | 1444.1166 | 1825.1055 | 1941.9003 | 1839.1465 | 1656.4714 | 1444.1166 | 1825.1055 | 3.4784 | 3.0333 | 3.2688 | 2.9327 | 3.2413
12 | SA-16-TL | 12-SA-16-TL | 1773.1952 | 1714.7367 | 1485.5394 | 1301.969 | 1674.7419 | 1773.1952 | 1714.7367 | 1485.5394 | 1301.969 | 1674.7419 | 3.3061 | 3.0577 | 3.0311 | 2.778 | 3.1347
12 | SA-17-CH | 12-SA-17-CH | 1705.0386 | 1665.4913 | 1474.5073 | 1281.3172 | 1624.4773 | 1705.0386 | 1665.4913 | 1474.5073 | 1281.3172 | 1624.4773 | 3.0965 | 2.954 | 3.0023 | 2.8024 | 3.0063
12 | SA-17-CL | 12-SA-17-CL | 1705.127 | 1661.6995 | 1465.244 | 1272.1129 | 1621.2094 | 1705.127 | 1661.6995 | 1465.244 | 1272.1129 | 1621.2094 | 3.1536 | 2.9802 | 2.9925 | 2.7763 | 3.0367
12 | SA-17-CM | 12-SA-17-CM | 1730.3237 | 1689.6255 | 1482.96 | 1288.9726 | 1645.7582 | 1730.3237 | 1689.6255 | 1482.96 | 1288.9726 | 1645.7582 | 3.14 | 2.98 | 3.0036 | 2.7934 | 3.0337
12 | SA-17-LH | 12-SA-17-LH | 1521.4493 | 1481.3016 | 1345.1615 | 1178.8173 | 1454.498 | 1521.4493 | 1481.3016 | 1345.1615 | 1178.8173 | 1454.498 | 2.9631 | 2.5726 | 2.6495 | 2.4569 | 2.7376
12 | SA-17-LL | 12-SA-17-LL | 1605.0315 | 1559.1576 | 1403.9231 | 1218.4414 | 1529.0282 | 1605.0315 | 1559.1576 | 1403.9231 | 1218.4414 | 1529.0282 | 3.1449 | 2.7375 | 2.9154 | 2.6068 | 2.92
12 | SA-17-LM | 12-SA-17-LM | 1593.7968 | 1555.9914 | 1408.6922 | 1222.9017 | 1524.0371 | 1593.7968 | 1555.9914 | 1408.6922 | 1222.9017 | 1524.0371 | 3.0808 | 2.682 | 2.8638 | 2.5624 | 2.8623
12 | SA-17-TH | 12-SA-17-TH | 1609.0738 | 1543.2084 | 1422.0844 | 1239.9259 | 1529.0558 | 1609.0738 | 1543.2084 | 1422.0844 | 1239.9259 | 1529.0558 | 2.9773 | 2.5976 | 2.8372 | 2.5534 | 2.7834
12 | SA-17-TL | 12-SA-17-TL | 1516.6378 | 1470.9489 | 1297.2896 | 1133.3915 | 1438.9188 | 1516.6378 | 1470.9489 | 1297.2896 | 1133.3915 | 1438.9188 | 3.0195 | 2.7843 | 2.7787 | 2.5535 | 2.8626
12 | SA-17-TM | 12-SA-17-TM | 1835.5066 | 1764.9065 | 1503.9469 | 1321.234 | 1723.5604 | 1835.5066 | 1764.9065 | 1503.9469 | 1321.234 | 1723.5604 | 3.1704 | 3.0351 | 3.0849 | 2.8869 | 3.0848
12 | SA-18-LH | 12-SA-18-LH | 1500.7712 | 1458.2821 | 1322.3595 | 1149.2794 | 1431.8945 | 1500.7712 | 1458.2821 | 1322.3595 | 1149.2794 | 1431.8945 | 2.9059 | 2.5305 | 2.6976 | 2.4134 | 2.6993
12 | SA-18-LL | 12-SA-18-LL | 1450.5818 | 1412.8874 | 1284.0173 | 1114.1408 | 1386.22 | 1450.5818 | 1412.8874 | 1284.0173 | 1114.1408 | 1386.22 | 2.8852 | 2.5104 | 2.6843 | 2.4026 | 2.6806
12 | SA-18-TH | 12-SA-18-TH | 1556.1975 | 1527.3014 | 1366.3444 | 1210.9468 | 1491.5342 | 1556.1975 | 1527.3014 | 1366.3444 | 1210.9468 | 1491.5342 | 2.8321 | 2.6505 | 2.6637 | 2.4691 | 2.7127
12 | SA-18-TL | 12-SA-18-TL | 1710.4819 | 1659.5165 | 1458.3538 | 1280.9787 | 1622.7444 | 1710.4819 | 1659.5165 | 1458.3538 | 1280.9787 | 1622.7444 | 3.154 | 3.0243 | 3.0836 | 2.8831 | 3.0734
12 | SA-18-TM | 12-SA-18-TM | 1589.7357 | 1523.6255 | 1400.6985 | 1220.9069 | 1509.4232 | 1589.7357 | 1523.6255 | 1400.6985 | 1220.9069 | 1509.4232 | 2.9153 | 2.5371 | 2.7516 | 2.4743 | 2.7176
12 | SH-10-HH | 12-SH-10-HH | 7016.0521 | 5362.9389 | 4224.3449 | 3607.121 | 5916.0701 | 2157.9161 | 2174.076 | 2047.5563 | 1790.2628 | 2122.4792 | 4.0602 | 3.819 | 3.9169 | 3.6206 | 3.9301
12 | SH-10-HL | 12-SH-10-HL | 7128.6964 | 5473.9658 | 4293.0215 | 3654.7453 | 6018.5856 | 2241.7367 | 2253.1041 | 2104.981 | 1834.1376 | 2198.8731 | 4.2025 | 3.9548 | 4.0416 | 3.7518 | 4.0676
12 | SH-10-HM | 12-SH-10-HM | 6904.6858 | 5308.9648 | 4219.1774 | 3582.3657 | 5841.1943 | 2198.549 | 2179.2968 | 2059.1167 | 1791.4485 | 2145.2804 | 4.1789 | 3.6699 | 4.0898 | 3.6857 | 3.9605
12 | SH-10-LH | 12-SH-10-LH | 7257.3051 | 5456.9658 | 4289.6163 | 3643.322 | 6074.478 | 2111.9871 | 2097.4295 | 2012.9076 | 1753.2917 | 2068.1597 | 3.7855 | 3.3365 | 3.7465 | 3.3875 | 3.5997
12 | SH-10-LL | 12-SH-10-LL | 7242.2849 | 5477.7949 | 4255.2003 | 3609.9546 | 6067.999 | 2178.9804 | 2164.5032 | 2044.3446 | 1777.3123 | 2128.2106 | 4.0313 | 3.5266 | 3.9228 | 3.5261 | 3.8115
12 | SH-10-LM | 12-SH-10-LM | 7052.0154 | 5361.4538 | 4215.9316 | 3598.9819 | 5931.6579 | 2135.9032 | 2119.4942 | 2013.837 | 1761.0157 | 2087.9034 | 3.9125 | 3.4429 | 3.8271 | 3.5543 | 3.7187
12 | SH-10-MH | 12-SH-10-MH | 7249.5598 | 5457.5734 | 4264.4538 | 3619.4316 | 6066.4992 | 2134.1377 | 2117.2595 | 2017.3991 | 1755.3348 | 2086.1782 | 3.9584 | 3.4828 | 3.891 | 3.5158 | 3.7574
12 | SH-10-ML | 12-SH-10-ML | 6941.8871 | 5315.3203 | 4156.0178 | 3533.0965 | 5851.3143 | 2217.3735 | 2200.1647 | 2066.8192 | 1796.4981 | 2162.5774 | 4.2463 | 3.7258 | 4.131 | 3.8117 | 4.0264
12 | SH-10-MM | 12-SH-10-MM | 7134.8372 | 5436.5954 | 4251.9527 | 3608.5039 | 6001.3812 | 2207.0669 | 2189.1996 | 2057.5616 | 1789.3782 | 2152.4145 | 4.0994 | 3.5974 | 4.0145 | 3.6191 | 3.8849
12 | SH-13-HH | 12-SH-13-HH | 6621.9954 | 4900.833 | 3788.7747 | 3229.1788 | 5496.6663 | 1805.2678 | 1815.028 | 1693.8302 | 1479.5513 | 1771.031 | 3.4824 | 3.2861 | 3.3517 | 3.1162 | 3.3744
12 | SH-13-HL | 12-SH-13-HL | 5892.7879 | 4398.2764 | 3406.7512 | 2890.7359 | 4908.5466 | 1715.6639 | 1716.3047 | 1600.0721 | 1390.5023 | 1678.0356 | 3.5086 | 3.2968 | 3.4636 | 3.1965 | 3.4082
12 | SH-13-HM | 12-SH-13-HM | 6033.5762 | 4535.9046 | 3535.0947 | 3008.982 | 5045.2302 | 1775.2955 | 1782.5814 | 1657.3834 | 1444.2399 | 1739.17 | 3.4427 | 3.2434 | 3.2981 | 3.0591 | 3.331
12 | SH-13-LH | 12-SH-13-LH | 7030.3175 | 5039.0516 | 3708.6286 | 3143.2915 | 5727.2641 | 1662.4288 | 1651.0345 | 1580.9844 | 1375.4177 | 1627.2345 | 3.0926 | 2.7302 | 3.0682 | 2.7712 | 2.9433
12 | SH-13-LL | 12-SH-13-LL | 6121.9811 | 4515.1204 | 3426.6655 | 2911.5018 | 5062.9891 | 1645.9885 | 1630.3332 | 1531.661 | 1334.8605 | 1604.2108 | 3.2373 | 2.86 | 3.1863 | 2.9478 | 3.0831
12 | SH-13-LM | 12-SH-13-LM | 5489.0686 | 4174.6642 | 3270.3047 | 2790.3365 | 4615.5165 | 1724.7955 | 1716.8254 | 1622.9975 | 1419.6404 | 1687.2795 | 3.2564 | 2.8776 | 3.089 | 2.9172 | 3.0864
12 | SH-13-MH | 12-SH-13-MH | 6559.7002 | 4784.3793 | 3684.0395 | 3144.0772 | 5410.3684 | 1647.5888 | 1656.3052 | 1567.2894 | 1371.8396 | 1620.1178 | 3.2225 | 3.0483 | 3.1613 | 2.9339 | 3.135
12 | SH-13-ML | 12-SH-13-ML | 6351.0421 | 4690.8623 | 3568.5907 | 3020.4958 | 5256.0255 | 1752.2108 | 1743.7881 | 1653.4747 | 1434.4489 | 1713.8091 | 3.4684 | 3.0716 | 3.4329 | 3.0981 | 3.3026
12 | SH-13-MM | 12-SH-13-MM | 6170.2212 | 4625.2676 | 3576.8768 | 3024.734 | 5147.0413 | 1722.085 | 1707.9238 | 1608.7348 | 1393.5051 | 1679.4703 | 3.4534 | 3.0544 | 3.3714 | 3.0328 | 3.2783
12 | SH-14-HH | 12-SH-14-HH | 6123.3329 | 4539.6324 | 3510.9343 | 2988.6178 | 5086.296 | 1708.0264 | 1714.7965 | 1593.9032 | 1390.2377 | 1673.1833 | 3.3301 | 3.1332 | 3.1907 | 2.9571 | 3.2206
12 | SH-14-HL | 12-SH-14-HL | 6135.0238 | 4473.78 | 3410.0272 | 2889.4526 | 5052.1867 | 1662.6409 | 1667.3166 | 1541.2935 | 1337.9075 | 1625.8314 | 3.2843 | 3.0782 | 3.1155 | 2.8731 | 3.1657
12 | SH-14-HM | 12-SH-14-HM | 6047.5122 | 4445.7623 | 3415.789 | 2904.9603 | 5001.9538 | 1657.3079 | 1663.5281 | 1547.0935 | 1347.7998 | 1623.3393 | 3.1676 | 2.9667 | 3.0192 | 2.794 | 3.0558
12 | SH-14-MH | 12-SH-14-MH | 6409.8936 | 4621.851 | 3425.5147 | 2904.6429 | 5238.4401 | 1554.0518 | 1543.6169 | 1476.0191 | 1284.2349 | 1520.9156 | 2.9082 | 2.5689 | 2.8797 | 2.595 | 2.7669
12 | SH-14-ML | 12-SH-14-ML | 6800.2888 | 4716.2656 | 3450.9074 | 2920.6364 | 5464.2944 | 1572.1933 | 1567.2991 | 1466.394 | 1273.3041 | 1535.8252 | 3.1889 | 2.9937 | 3.0913 | 2.8437 | 3.0862
12 | SH-14-MM | 12-SH-14-MM | 5934.4841 | 4356.5552 | 3288.9781 | 2784.8607 | 4894.9335 | 1570.7054 | 1564.5252 | 1479.5491 | 1284.6641 | 1536.3826 | 3.073 | 2.7199 | 3.0158 | 2.7076 | 2.9201
12 | SH-15-HH | 12-SH-15-HH | 6965.1856 | 4856.9789 | 3542.8473 | 3008.1033 | 5607.726 | 1527.6977 | 1531.6485 | 1429.6221 | 1248.0745 | 1496.599 | 2.9248 | 2.7403 | 2.7854 | 2.5775 | 2.8215
12 | SH-15-HL | 12-SH-15-HL | 5282.9397 | 3945.1566 | 3064.8197 | 2602.395 | 4403.1619 | 1540.2773 | 1546.6352 | 1437.0792 | 1249.7724 | 1508.5913 | 3.0877 | 2.9021 | 2.9755 | 2.743 | 2.9869
12 | SH-15-HM | 12-SH-15-HM | 5406.278 | 3971.792 | 3096.7716 | 2629.1576 | 4477.5541 | 1472.3793 | 1480.1907 | 1391.8128 | 1210.0476 | 1445.68 | 2.9714 | 2.7816 | 2.8403 | 2.6068 | 2.8657
12 | SH-15-MH | 12-SH-15-MH | 6287.4115 | 4476.6903 | 3282.5616 | 2773.7883 | 5105.7414 | 1505.8404 | 1489.5134 | 1417.2383 | 1227.184 | 1468.9946 | 3.0256 | 2.6665 | 2.9346 | 2.6512 | 2.8666
12 | SH-15-ML | 12-SH-15-ML | 5989.8092 | 4212.977 | 3136.2536 | 2654.4065 | 4848.6881 | 1472.594 | 1466.8899 | 1370.8446 | 1189.588 | 1437.65 | 3.0194 | 2.8318 | 2.924 | 2.677 | 2.9197
12 | SH-15-MM | 12-SH-15-MM | 6152.4655 | 4383.4794 | 3290.5648 | 2788.6228 | 5010.8161 | 1468.907 | 1472.564 | 1381.4442 | 1201.0331 | 1439.7026 | 2.954 | 2.7645 | 2.837 | 2.6109 | 2.8515
12 | SH-16-CH | 12-SH-16-CH | 6857.5442 | 4906.2687 | 3433.14 | 2910.2798 | 5552.8935 | 1779.633 | 1742.7581 | 1541.2819 | 1346.6707 | 1708.7843 | 3.1834 | 2.9734 | 2.9612 | 2.7454 | 3.0561
12 | SH-16-CL | 12-SH-16-CL | 6560.996 | 4716.3684 | 3334.5346 | 2820.6575 | 5327.9762 | 1823.4901 | 1784.1138 | 1568.2784 | 1363.4922 | 1747.9594 | 3.2507 | 3.1328 | 3.2041 | 3.0165 | 3.1878
12 | SH-16-LH | 12-SH-16-LH | 6907.3424 | 4866.7491 | 3437.1254 | 2920.3965 | 5565.2836 | 1583.2147 | 1537.695 | 1436.3373 | 1251.9932 | 1526.698 | 3.0186 | 2.6279 | 2.837 | 2.5459 | 2.8323
12 | SH-16-LL | 12-SH-16-LL | 6618.9014 | 4688.3647 | 3276.1323 | 2775.9209 | 5337.6109 | 1643.8566 | 1606.9229 | 1459.6575 | 1266.5253 | 1582.7987 | 3.2305 | 2.8086 | 2.9974 | 2.6842 | 3.0228
12 | SH-16-LM | 12-SH-16-LM | 7035.7637 | 4959.9884 | 3464.4414 | 2945.6644 | 5663.7429 | 1640.8232 | 1597.6569 | 1461.082 | 1285.1614 | 1579.8988 | 3.1384 | 2.7305 | 2.8183 | 2.6235 | 2.9295
12 | SH-16-TH | 12-SH-16-TH | 7975.5832 | 5665.8645 | 3836.8048 | 3263.0591 | 6419.7035 | 1705.6697 | 1667.298 | 1477.3046 | 1306.3048 | 1638.0431 | 3.2943 | 3.059 | 3.0325 | 2.7881 | 3.1492
12 | SH-16-TL | 12-SH-16-TL | 8192.332 | 5801.4066 | 3933.3576 | 3324.0283 | 6585.0178 | 1940.0151 | 1843.31 | 1631.1275 | 1414.145 | 1834.8104 | 3.5467 | 3.101 | 3.392 | 3.0504 | 3.3428
12 | SH-16-TM | 12-SH-16-TM | 8223.5814 | 5823.7798 | 3955.3761 | 3344.0132 | 6611.4963 | 1914.6831 | 1820.2003 | 1613.6244 | 1400.0554 | 1811.898 | 3.4804 | 3.043 | 3.3347 | 2.9988 | 3.2813
12 | SH-17-CM | 12-SH-17-CM | 6914.4589 | 4852.0108 | 3335.3722 | 2814.7294 | 5545.3295 | 1724.7352 | 1687.6647 | 1484.5886 | 1290.8764 | 1653.5738 | 3.0945 | 2.9823 | 3.0496 | 2.8705 | 3.0345
12 | SH-17-LM | 12-SH-17-LM | 6452.1285 | 4569.3213 | 3215.4305 | 2728.0671 | 5206.7469 | 1643.4377 | 1592.5904 | 1448.8638 | 1259.2583 | 1576.1837 | 3.0709 | 2.6878 | 3.0069 | 2.7045 | 2.9073
12 | SH-17-TH | 12-SH-17-TH | 7854.4943 | 5573.6109 | 3752.3243 | 3183.5216 | 6315.1621 | 1602.8412 | 1572.7248 | 1398.8711 | 1232.3456 | 1542.6921 | 3.0771 | 2.8776 | 2.8767 | 2.6589 | 2.957
12 | SH-17-TL | 12-SH-17-TL | 7870.408 | 5565.2681 | 3730.5827 | 3159.7082 | 6316.0993 | 1621.5526 | 1585.8406 | 1405.0996 | 1235.9254 | 1557.0916 | 3.148 | 2.9358 | 2.9283 | 2.6997 | 3.0194
12 | SH-18-LH | 12-SH-18-LH | 7120.7097 | 4949.2467 | 3314.4291 | 2789.972 | 5674.3514 | 1479.5476 | 1439.7387 | 1305.0144 | 1140.9699 | 1421.6444 | 2.9368 | 2.5552 | 2.638 | 2.4543 | 2.7414
12 | SH-18-LL | 12-SH-18-LL | 6583.1076 | 4613.1808 | 3176.0897 | 2681.6126 | 5277.687 | 1529.1352 | 1492.0929 | 1353.4384 | 1181.5714 | 1471.3037 | 3.0175 | 2.6271 | 2.7182 | 2.5301 | 2.8187
12 | SH-18-LM | 12-SH-18-LM | 7451.627 | 5169.5771 | 3396.9405 | 2872.2075 | 5924.0111 | 1503.5054 | 1460.5653 | 1322.9544 | 1148.685 | 1442.6466 | 2.9846 | 2.5928 | 2.7521 | 2.4665 | 2.7893
12 | SH-18-TM | 12-SH-18-TM | 7837.6387 | 5487.37 | 3674.4275 | 3109.0088 | 6264.5795 | 1551.381 | 1490.7938 | 1344.4356 | 1181.8013 | 1480.8816 | 3.0356 | 2.6557 | 2.764 | 2.5746 | 2.8451
13 | SA-10-HH | 13-SA-10-HH | 4345.8121 | 4140.4283 | 3945.9124 | 3512.9423 | 4128.9268 | 4345.8121 | 4140.4283 | 3945.9124 | 3512.9423 | 4128.9268 | 4.4359 | 3.86 | 4.4803 | 4.0568 | 4.2063
13 | SA-10-HL | 13-SA-10-HL | 4619.9632 | 4413.155 | 4186.7716 | 3721.6257 | 4390.9427 | 4619.9632 | 4413.155 | 4186.7716 | 3721.6257 | 4390.9427 | 4.9516 | 4.3112 | 4.9138 | 4.4393 | 4.6727
13 | SA-10-HM | 13-SA-10-HM | 4458.7109 | 4252.7857 | 4042.4002 | 3593.6687 | 4235.9095 | 4458.7109 | 4252.7857 | 4042.4002 | 3593.6687 | 4235.9095 | 4.6215 | 4.0142 | 4.5528 | 4.1205 | 4.3498
13 | SA-10-LH | 13-SA-10-LH | 4178.9342 | 3985.5665 | 3857.7415 | 3428.6875 | 3987.7016 | 4178.9342 | 3985.5665 | 3857.7415 | 3428.6875 | 3987.7016 | 4.1875 | 3.6558 | 4.3279 | 3.918 | 4.0005
13 | SA-10-LL | 13-SA-10-LL | 4406.1378 | 4226.4857 | 4005.665 | 3559.7999 | 4197.186 | 4406.1378 | 4226.4857 | 4005.665 | 3559.7999 | 4197.186 | 4.5175 | 3.9354 | 4.5105 | 4.0721 | 4.2707
13 | SA-10-LM | 13-SA-10-LM | 4207.772 | 4014.8182 | 3860.6086 | 3430.3886 | 4009.6479 | 4207.772 | 4014.8182 | 3860.6086 | 3430.3886 | 4009.6479 | 4.2442 | 3.6984 | 4.3617 | 3.9461 | 4.0456
13 | SA-10-MH | 13-SA-10-MH | 4163.8221 | 3969.567 | 3830.6382 | 3453.2861 | 3973.4556 | 4163.8221 | 3969.567 | 3830.6382 | 3453.2861 | 3973.4556 | 4.0744 | 3.556 | 3.9433 | 3.8249 | 3.8444
13 | SA-10-ML | 13-SA-10-ML | 4535.2546 | 4346.296 | 4124.9842 | 3666.8224 | 4319.3206 | 4535.2546 | 4346.296 | 4124.9842 | 3666.8224 | 4319.3206 | 4.5876 | 4.0033 | 4.6721 | 4.2199 | 4.3634
13 | SA-10-MM | 13-SA-10-MM | 4208.7007 | 3992.1755 | 3843.0608 | 3442.5358 | 3999.7488 | 4208.7007 | 3992.1755 | 3843.0608 | 3442.5358 | 3999.7488 | 4.3066 | 3.5934 | 4.054 | 3.9381 | 3.9748
13 | SA-13-HH | 13-SA-13-HH | 3419.4945 | 3270.164 | 3140.3098 | 2793.189 | 3262.1523 | 3419.4945 | 3270.164 | 3140.3098 | 2793.189 | 3262.1523 | 3.7011 | 3.2313 | 3.7499 | 3.3904 | 3.516
13 | SA-13-HL | 13-SA-13-HL | 3452.6165 | 3300.6548 | 3148.5002 | 2793.6379 | 3287.0161 | 3452.6165 | 3300.6548 | 3148.5002 | 2793.6379 | 3287.0161 | 3.9904 | 3.4992 | 4.0542 | 3.6687 | 3.7995
13 | SA-13-HM | 13-SA-13-HM | 3428.9974 | 3330.4928 | 3130.1896 | 2792.983 | 3285.3867 | 3428.9974 | 3330.4928 | 3130.1896 | 2792.983 | 3285.3867 | 3.8321 | 3.664 | 3.7632 | 3.5636 | 3.7368
13 | SA-13-LH | 13-SA-13-LH | 3207.5498 | 3063.2693 | 2963.4533 | 2635.6746 | 3063.0275 | 3207.5498 | 3063.2693 | 2963.4533 | 2635.6746 | 3063.0275 | 3.3609 | 2.947 | 3.4482 | 3.1212 | 3.2088
13 | SA-13-LL | 13-SA-13-LL | 3394.2199 | 3251.1734 | 3111.4987 | 2761.8254 | 3237.9581 | 3394.2199 | 3251.1734 | 3111.4987 | 2761.8254 | 3237.9581 | 3.6736 | 3.2134 | 3.7311 | 3.3813 | 3.4951
13 | SA-13-LM | 13-SA-13-LM | 3342.2604 | 3197.6878 | 3072.7139 | 2755.9257 | 3191.7653 | 3342.2604 | 3197.6878 | 3072.7139 | 2755.9257 | 3191.7653 | 3.4883 | 3.0525 | 3.3774 | 3.2628 | 3.2934
13 | SA-13-MH | 13-SA-13-MH | 3329.1576 | 3165.128 | 3041.4665 | 2704.8556 | 3165.1896 | 3329.1576 | 3165.128 | 3041.4665 | 2704.8556 | 3165.1896 | 3.5497 | 3.0945 | 3.5623 | 3.222 | 3.3618
13 | SA-13-ML | 13-SA-13-ML | 3395.7632 | 3245.4708 | 3068.6282 | 2724.0509 | 3225.4797 | 3395.7632 | 3245.4708 | 3068.6282 | 2724.0509 | 3225.4797 | 3.7695 | 3.306 | 3.8309 | 3.4455 | 3.5878
13 | SA-13-MM | 13-SA-13-MM | 3299.3187 | 3180.779 | 2976.5003 | 2659.6941 | 3143.8743 | 3299.3187 | 3180.779 | 2976.5003 | 2659.6941 | 3143.8743 | 3.6817 | 3.5305 | 3.6812 | 3.4534 | 3.6083
13 | SA-14-HH | 13-SA-14-HH | 3298.8608 | 3150.0192 | 3006.6728 | 2672.4048 | 3139.3088 | 3298.8608 | 3150.0192 | 3006.6728 | 2672.4048 | 3139.3088 | 3.6006 | 3.1497 | 3.6499 | 3.2837 | 3.4219
13 | SA-14-HL | 13-SA-14-HL | 3201.7376 | 3090.5116 | 2906.2799 | 2590.7423 | 3056.322 | 3201.7376 | 3090.5116 | 2906.2799 | 2590.7423 | 3056.322 | 3.6212 | 3.444 | 3.5838 | 3.373 | 3.5301
13 | SA-14-HM | 13-SA-14-HM | 3285.8898 | 3135.3034 | 3010.3372 | 2669.9917 | 3129.6451 | 3285.8898 | 3135.3034 | 3010.3372 | 2669.9917 | 3129.6451 | 3.6452 | 3.1951 | 3.7265 | 3.3674 | 3.4759
13 | SA-14-MH | 13-SA-14-MH | 3159.3729 | 3022.5274 | 2915.7045 | 2621.1956 | 3020.4408 | 3159.3729 | 3022.5274 | 2915.7045 | 2621.1956 | 3020.4408 | 3.2357 | 2.8323 | 3.149 | 3.046 | 3.0598
13 | SA-14-ML | 13-SA-14-ML | 3183.224 | 3047.198 | 2925.9975 | 2596.0331 | 3037.9525 | 3183.224 | 3047.198 | 2925.9975 | 2596.0331 | 3037.9525 | 3.5497 | 3.1162 | 3.6358 | 3.2912 | 3.3888
13 | SA-14-MM | 13-SA-14-MM | 3116.3629 | 2981.2904 | 2870.0688 | 2577.3213 | 2977.5112 | 3116.3629 | 2981.2904 | 2870.0688 | 2577.3213 | 2977.5112 | 3.276 | 2.8656 | 3.1773 | 3.0717 | 3.0943
13 | SA-15-HH | 13-SA-15-HH | 2993.2167 | 2908.0529 | 2749.2804 | 2463.2128 | 2873.3688 | 2993.2167 | 2908.0529 | 2749.2804 | 2463.2128 | 2873.3688 | 3.3424 | 3.2083 | 3.309 | 3.1401 | 3.2713
13 | SA-15-HL | 13-SA-15-HL | 2950.2192 | 2853.652 | 2692.1628 | 2400.7579 | 2822.0764 | 2950.2192 | 2853.652 | 2692.1628 | 2400.7579 | 2822.0764 | 3.3971 | 3.2472 | 3.3799 | 3.1842 | 3.3224
13 | SA-15-HM | 13-SA-15-HM | 2958.325 | 2868.2985 | 2697.837 | 2412.9217 | 2832.4168 | 2958.325 | 2868.2985 | 2697.837 | 2412.9217 | 2832.4168 | 3.242 | 3.104 | 3.1953 | 3.026 | 3.1659
13 | SA-15-MH | 13-SA-15-MH | 3043.4697 | 2900.6226 | 2808.951 | 2496.8044 | 2903.3448 | 3043.4697 | 2900.6226 | 2808.951 | 2496.8044 | 2903.3448 | 3.3995 | 2.9859 | 3.4932 | 3.167 | 3.2493
13 | SA-15-ML | 13-SA-15-ML | 2990.1093 | 2860.761 | 2732.9043 | 2424.8276 | 2849.0834 | 2990.1093 | 2860.761 | 2732.9043 | 2424.8276 | 2849.0834 | 3.3325 | 2.9217 | 3.3639 | 3.0418 | 3.167
13 | SA-15-MM | 13-SA-15-MM | 2982.7469 | 2846.066 | 2727.2114 | 2421.8538 | 2839.7817 | 2982.7469 | 2846.066 | 2727.2114 | 2421.8538 | 2839.7817 | 3.3613 | 2.9469 | 3.4265 | 3.0955 | 3.2028
13 | SA-16-CH | 13-SA-16-CH | 3589.507 | 3337.8521 | 3073.4166 | 2736.6244 | 3333.2239 | 3589.507 | 3337.8521 | 3073.4166 | 2736.6244 | 3333.2239 | 3.4268 | 2.9977 | 3.5224 | 3.1756 | 3.2698
13 | SA-16-CL | 13-SA-16-CL | 3414.1286 | 3229.5882 | 2879.1905 | 2569.4738 | 3179.052 | 3414.1286 | 3229.5882 | 2879.1905 | 2569.4738 | 3179.052 | 3.5605 | 3.3854 | 3.3593 | 3.163 | 3.4276
13 | SA-16-CM | 13-SA-16-CM | 3505.9479 | 3331.8318 | 2991.6862 | 2678.5787 | 3279.8283 | 3505.9479 | 3331.8318 | 2991.6862 | 2678.5787 | 3279.8283 | 3.5395 | 3.4045 | 3.4494 | 3.2575 | 3.451
13 | SA-16-LH | 13-SA-16-LH | 3082.2003 | 2889.3177 | 2693.4139 | 2401.3917 | 2884.7054 | 3082.2003 | 2889.3177 | 2693.4139 | 2401.3917 | 2884.7054 | 3.3165 | 2.8853 | 3.257 | 2.929 | 3.1189
13 | SA-16-LL | 13-SA-16-LL | 3296.727 | 3090.1264 | 2828.7581 | 2520.6183 | 3071.8098 | 3296.727 | 3090.1264 | 2828.7581 | 2520.6183 | 3071.8098 | 3.6033 | 3.1401 | 3.5194 | 3.1652 | 3.3856
13 | SA-16-LM | 13-SA-16-LM | 3248.0638 | 3047.7367 | 2807.9701 | 2501.0397 | 3032.9367 | 3248.0638 | 3047.7367 | 2807.9701 | 2501.0397 | 3032.9367 | 3.4618 | 3.0164 | 3.3872 | 3.0518 | 3.2545
13 | SA-16-NM | 13-SA-16-NM | 2971.5751 | 2792.5844 | 2513.855 | 2233.6423 | 2761.6174 | 2971.5751 | 2792.5844 | 2513.855 | 2233.6423 | 2761.6174 | 3.2935 | 2.857 | 3.0963 | 2.7763 | 3.0579
13 | SA-16-TH | 13-SA-16-TH | 3745.5674 | 3445.611 | 3190.5404 | 2847.3293 | 3461.101 | 3745.5674 | 3445.611 | 3190.5404 | 2847.3293 | 3461.101 | 3.7428 | 3.2658 | 3.6847 | 3.3109 | 3.5254
13 | SA-16-TL | 13-SA-16-TL | 3443.8671 | 3241.3902 | 2864.4663 | 2570.9961 | 3191.8876 | 3443.8671 | 3241.3902 | 2864.4663 | 2570.9961 | 3191.8876 | 3.6336 | 3.4545 | 3.4848 | 3.2774 | 3.5123
13 | SA-17-CH | 13-SA-17-CH | 3345.9983 | 3114.4698 | 2858.3854 | 2541.2592 | 3106.175 | 3345.9983 | 3114.4698 | 2858.3854 | 2541.2592 | 3106.175 | 3.3232 | 2.9056 | 3.4057 | 3.0586 | 3.1668
13 | SA-17-CL | 13-SA-17-CL | 3350.5839 | 3118.3806 | 2836.4386 | 2520.2717 | 3103.5109 | 3350.5839 | 3118.3806 | 2836.4386 | 2520.2717 | 3103.5109 | 3.393 | 2.9666 | 3.3971 | 3.0529 | 3.2128
13 | SA-17-CM | 13-SA-17-CM | 3384.0443 | 3144.5011 | 2866.6319 | 2550.4781 | 3133.4805 | 3384.0443 | 3144.5011 | 2866.6319 | 2550.4781 | 3133.4805 | 3.3738 | 2.9507 | 3.3952 | 3.0641 | 3.2005
13 | SA-17-LH | 13-SA-17-LH | 3004.961 | 2816.5764 | 2588.397 | 2321.4738 | 2803.7776 | 3004.961 | 2816.5764 | 2588.397 | 2321.4738 | 2803.7776 | 3.2449 | 2.8221 | 2.9958 | 2.8657 | 3.0165
13 | SA-17-LL | 13-SA-17-LL | 3180.0008 | 2975.1316 | 2714.9964 | 2417.911 | 2957.4315 | 3180.0008 | 2975.1316 | 2714.9964 | 2417.911 | 2957.4315 | 3.4557 | 3.0117 | 3.3927 | 3.0514 | 3.2515
13 | SA-17-LM | 13-SA-17-LM | 3139.5795 | 2947.6986 | 2708.0374 | 2412.8751 | 2930.7498 | 3139.5795 | 2947.6986 | 2708.0374 | 2412.8751 | 2930.7498 | 3.4109 | 2.9701 | 3.3315 | 2.9912 | 3.2035
13 | SA-17-TH | 13-SA-17-TH | 3125.6167 | 2907.0272 | 2744.4783 | 2451.3896 | 2920.9031 | 3125.6167 | 2907.0272 | 2744.4783 | 2451.3896 | 2920.9031 | 3.2411 | 2.8332 | 3.258 | 2.9355 | 3.0727
13 | SA-17-TL | 13-SA-17-TL | 2995.7333 | 2788.4935 | 2533.2396 | 2248.6443 | 2774.049 | 2995.7333 | 2788.4935 | 2533.2396 | 2248.6443 | 2774.049 | 3.3325 | 2.8718 | 3.1693 | 2.8506 | 3.0975
13 | SA-17-TM | 13-SA-17-TM | 3530.5789 | 3338.5976 | 2925.5287 | 2638.6705 | 3276.0508 | 3530.5789 | 3338.5976 | 2925.5287 | 2638.6705 | 3276.0508 | 3.4089 | 3.3169 | 3.4748 | 3.337 | 3.382
13 | SA-18-LH | 13-SA-18-LH | 2962.4971 | 2769.9409 | 2546.4048 | 2270.021 | 2759.1486 | 2962.4971 | 2769.9409 | 2546.4048 | 2270.021 | 2759.1486 | 3.2053 | 2.7958 | 3.1431 | 2.8292 | 3.016
13 | SA-18-LL | 13-SA-18-LL | 2873.7754 | 2698.6374 | 2482.218 | 2206.8656 | 2683.2856 | 2873.7754 | 2698.6374 | 2482.218 | 2206.8656 | 2683.2856 | 3.1714 | 2.7596 | 3.1192 | 2.8 | 2.9834
13 | SA-18-TH | 13-SA-18-TH | 3002.198 | 2783.5607 | 2622.9593 | 2381.5727 | 2802.3623 | 3002.198 | 2783.5607 | 2622.9593 | 2381.5727 | 2802.3623 | 3.0886 | 2.6945 | 3.0652 | 2.9018 | 2.9279
13 | SA-18-TL | 13-SA-18-TL | 3342.1356 | 3078.706 | 2858.0808 | 2548.3491 | 3092.5086 | 3342.1356 | 3078.706 | 2858.0808 | 2548.3491 | 3092.5086 | 3.4128 | 2.9948 | 3.5292 | 3.1759 | 3.2648
13 | SA-18-TM | 13-SA-18-TM | 3082.1847 | 2863.2648 | 2694.7475 | 2406.3882 | 2876.0713 | 3082.1847 | 2863.2648 | 2694.7475 | 2406.3882 | 2876.0713 | 3.1819 | 2.7821 | 3.1683 | 2.8505 | 3.0087
13 | SH-10-HH | 13-SH-10-HH | 8069.2958 | 6617.8251 | 5539.9939 | 4867.2335 | 6989.4888 | 4209.6881 | 4100.3383 | 3898.9147 | 3498.8837 | 4074.8837 | 4.4313 | 4.2509 | 4.3799 | 4.1718 | 4.3466
13 | SH-10-HL | 13-SH-10-HL | 8276.7657 | 6809.1698 | 5670.9428 | 4966.7849 | 7172.3 | 4391.2446 | 4263.9739 | 4021.2076 | 3596.0822 | 4235.5539 | 4.5875 | 4.4109 | 4.561 | 4.3519 | 4.5094
13 | SH-10-HM | 13-SH-10-HM | 8059.0291 | 6583.4678 | 5581.288 | 4862.9627 | 6979.6405 | 4315.7355 | 4113.4739 | 3952.0793 | 3514.1129 | 4136.6201 | 4.5829 | 3.9898 | 4.6027 | 4.1569 | 4.3646
13 | SH-10-LH | 13-SH-10-LH | 8193.1879 | 6550.5772 | 5539.5738 | 4826.2878 | 7021.5954 | 4096.6672 | 3911.2781 | 3826.5338 | 3406.3803 | 3945.2253 | 4.1223 | 3.5999 | 4.2329 | 3.8366 | 3.9506
13 | SH-10-LL | 13-SH-10-LL | 8310.6666 | 6692.4817 | 5569.8787 | 4848.4749 | 7126.7093 | 4275.9311 | 4077.0531 | 3896.4138 | 3462.8796 | 4094.677 | 4.3915 | 3.8204 | 4.3936 | 3.974 | 4.1783
13 | SH-10-LM | 13-SH-10-LM | 8065.1197 | 6519.5699 | 5483.7647 | 4777.2812 | 6941.1357 | 4151.7666 | 3962.6857 | 3818.278 | 3398.2074 | 3984.9644 | 4.2543 | 3.7017 | 4.2249 | 3.8206 | 4.041
13 | SH-10-MH | 13-SH-10-MH | 8242.226 | 6609.4553 | 5557.6872 | 4838.3799 | 7066.3828 | 4174.1685 | 3982.1827 | 3862.9895 | 3435.2729 | 4010.8579 | 4.3084 | 3.7594 | 4.4142 | 3.999 | 4.1258
13 | SH-10-ML | 13-SH-10-ML | 8141.3104 | 6637.9787 | 5555.1937 | 4837.903 | 7028.8824 | 4376.5756 | 4173.3344 | 3969.7806 | 3525.616 | 4187.015 | 4.6262 | 4.0283 | 4.6303 | 4.182 | 4.4027
13 | SH-10-MM | 13-SH-10-MM | 8245.8818 | 6686.9742 | 5565.6193 | 4879.5313 | 7097.0385 | 4326.0805 | 4126.4779 | 3917.1199 | 3509.4637 | 4139.9654 | 4.456 | 3.8815 | 4.2732 | 4.1305 | 4.2213
13 | SH-13-HH | 13-SH-13-HH | 7412.1906 | 5859.2163 | 4842.829 | 4244.3984 | 6296.7332 | 3550.862 | 3389.2223 | 3262.2926 | 2926.3438 | 3409.2466 | 3.8234 | 3.3377 | 3.793 | 3.6156 | 3.6485
13 | SH-13-HL | 13-SH-13-HL | 6720.6669 | 5403.6497 | 4444.9521 | 3878.1813 | 5748.5221 | 3398.6619 | 3280.9891 | 3078.2809 | 2745.366 | 3264.1514 | 3.9155 | 3.7733 | 3.9763 | 3.7684 | 3.8681
13 | SH-13-HM | 13-SH-13-HM | 6884.1624 | 5532.0558 | 4607.8743 | 4035.5297 | 5900.2927 | 3493.2399 | 3338.0221 | 3189.0278 | 2854.5937 | 3350.2805 | 3.758 | 3.2762 | 3.7084 | 3.5309 | 3.58
13 | SH-13-LH | 13-SH-13-LH | 7618.6865 | 5800.4779 | 4634.231 | 4025.4213 | 6325.0067 | 3255.2976 | 3109.3724 | 3030.8044 | 2695.5656 | 3133.0925 | 3.3717 | 2.9537 | 3.4996 | 3.1702 | 3.2422
13 | SH-13-LL | 13-SH-13-LL | 6819.8982 | 5365.4167 | 4383.8538 | 3809.4454 | 5767.4892 | 3241.0495 | 3090.6879 | 2952.2297 | 2624.4763 | 3103.5915 | 3.5689 | 3.1286 | 3.6197 | 3.2731 | 3.4138
13 | SH-13-LM | 13-SH-13-LM | 6370.3732 | 5176.839 | 4354.7297 | 3821.1823 | 5498.3247 | 3387.9697 | 3243.0158 | 3113.5689 | 2790.1176 | 3255.79 | 3.5583 | 3.1166 | 3.4551 | 3.3366 | 3.3855
13 | SH-13-MH | 13-SH-13-MH | 7179.1894 | 5613.5845 | 4612.4274 | 4045.5045 | 6062.6848 | 3241.6382 | 3151.7419 | 3014.9438 | 2709.5677 | 3139.0484 | 3.5523 | 3.4158 | 3.5406 | 3.3602 | 3.4925
13 | SH-13-ML | 13-SH-13-ML | 7146.4656 | 5655.6401 | 4662.6217 | 4048.5762 | 6068.7675 | 3477.4725 | 3332.0995 | 3215.8416 | 2852.3515 | 3344.9796 | 3.846 | 3.3686 | 3.9697 | 3.5924 | 3.6931
13 | SH-13-MM | 13-SH-13-MM | 6964.7377 | 5566.185 | 4610.5017 | 4004.4785 | 5946.0616 | 3422.2167 | 3263.594 | 3123.505 | 2773.7767 | 3278.2439 | 3.8466 | 3.3657 | 3.8646 | 3.4836 | 3.6686
13 | SH-14-HH | 13-SH-14-HH | 6900.1148 | 5480.982 | 4526.0001 | 3960.5453 | 5873.5132 | 3367.1168 | 3215.8704 | 3077.1822 | 2754.0931 | 3229.4815 | 3.6653 | 3.1974 | 3.6149 | 3.4397 | 3.4917
13 | SH-14-HL | 13-SH-14-HL | 6873.2824 | 5391.8528 | 4384.1497 | 3817.0438 | 5800.9556 | 3284.7125 | 3177.2016 | 2970.0373 | 2645.1739 | 3155.3271 | 3.6141 | 3.4546 | 3.5406 | 3.3563 | 3.5329
13 | SH-14-HM | 13-SH-14-HM | 6770.0687 | 5347.2501 | 4377.8064 | 3826.6792 | 5739.3165 | 3248.5745 | 3151.2346 | 2961.7739 | 2648.0016 | 3129.5137 | 3.4902 | 3.3292 | 3.4175 | 3.2445 | 3.4095
13 | SH-14-MH | 13-SH-14-MH | 6980.9207 | 5353.2392 | 4302.3566 | 3737.616 | 5819.7725 | 3040.9868 | 2907.2785 | 2827.729 | 2514.3169 | 2926.8457 | 3.195 | 2.8018 | 3.2987 | 2.9907 | 3.0696
13 | SH-14-ML | 13-SH-14-ML | 7376.5369 | 5494.3651 | 4336.9984 | 3773.9567 | 6053.6268 | 3131.476 | 3017.8501 | 2835.9741 | 2529.2322 | 3005.8141 | 3.5168 | 3.3845 | 3.5534 | 3.3603 | 3.4682
13 | SH-14-MM | 13-SH-14-MM | 6598.9926 | 5175.5632 | 4220.7397 | 3664.8005 | 5570.8185 | 3103.0862 | 2970.7255 | 2850.6213 | 2530.7284 | 2980.1001 | 3.4092 | 2.9909 | 3.4885 | 3.1546 | 3.2684
13 | SH-15-HH | 13-SH-15-HH | 7451.639 | 5528.1724 | 4329.0916 | 3776.6366 | 6097.7902 | 2995.285 | 2904.2609 | 2737.6494 | 2451.6385 | 2886.8759 | 3.2309 | 3.0915 | 3.172 | 3.0087 | 3.1609
13 | SH-15-HL | 13-SH-15-HL | 6016.8114 | 4849.2861 | 3999.3381 | 3491.9063 | 5154.6179 | 3037.3958 | 2947.9776 | 2766.5305 | 2468.7768 | 2925.6431 | 3.3717 | 3.2232 | 3.3409 | 3.1607 | 3.3038
13 | SH-15-HM | 13-SH-15-HM | 6067.5914 | 4803.3869 | 3973.7015 | 3470.2134 | 5157.7957 | 2918.5388 | 2834.152 | 2683.7504 | 2397.5151 | 2817.3437 | 3.2923 | 3.1491 | 3.2545 | 3.0704 | 3.2242
13 | SH-15-MH | 13-SH-15-MH | 6866.364 | 5223.9393 | 4167.4647 | 3616.5526 | 5697.0163 | 3006.717 | 2862.4164 | 2757.1476 | 2449.4847 | 2881.5062 | 3.359 | 2.946 | 3.3971 | 3.0762 | 3.2116
13 | SH-15-ML | 13-SH-15-ML | 6577.315 | 4995.0297 | 3995.0024 | 3479.1153 | 5455.8909 | 2938.3531 | 2830.1855 | 2655.054 | 2368.0845 | 2818.6639 | 3.3667 | 3.2366 | 3.3968 | 3.1861 | 3.316
13 | SH-15-MM | 13-SH-15-MM | 6697.7326 | 5117.0148 | 4115.4582 | 3585.3815 | 5575.7388 | 2911.747 | 2821.7988 | 2668.2579 | 2382.9057 | 2806.8992 | 3.2587 | 3.1172 | 3.228 | 3.0582 | 3.1939
13 | SH-16-CH | 13-SH-16-CH | 7693.2369 | 5846.6872 | 4402.1018 | 3831.3481 | 6324.7285 | 3454.8222 | 3216.2694 | 2951.8823 | 2630.4821 | 3241.8033 | 3.4403 | 2.9867 | 3.3012 | 2.9834 | 3.2405
13 | SH-16-CL | 13-SH-16-CL | 7515.4176 | 5757.7634 | 4401.3473 | 3832.7694 | 6215.0419 | 3568.8538 | 3315.2129 | 3046.9219 | 2712.6085 | 3345.796 | 3.4699 | 3.0372 | 3.577 | 3.2373 | 3.3303
13 | SH-16-LH | 13-SH-16-LH | 7540.7962 | 5612.3592 | 4256.9548 | 3709.1258 | 6149.5874 | 3099.2465 | 2902.8015 | 2751.7526 | 2456.3845 | 2936.4309 | 3.3171 | 2.8925 | 3.2839 | 2.9538 | 3.1494
13 | SH-16-LL | 13-SH-16-LL | 7390.7898 | 5561.9282 | 4179.6956 | 3642.4353 | 6048.3854 | 3252.3115 | 3057.3359 | 2797.4265 | 2503.1325 | 3065.9907 | 3.5423 | 3.0844 | 3.2879 | 3.1435 | 3.3285
13 | SH-16-LM | 13-SH-16-LM | 7722.9046 | 5756.2354 | 4305.5784 | 3766.5714 | 6290.2922 | 3216.7505 | 3016.3916 | 2797.6389 | 2520.2831 | 3038.0146 | 3.4354 | 2.9845 | 3.1918 | 3.0618 | 3.2274
13 | SH-16-TH | 13-SH-16-TH | 8584.0698 | 6467.6504 | 4664.8012 | 4072.1606 | 6987.2701 | 3333.2152 | 3163.6915 | 2853.633 | 2580.8875 | 3151.103 | 3.6131 | 3.4669 | 3.5402 | 3.3254 | 3.5339
13 | SH-16-TL | 13-SH-16-TL | 8967.6758 | 6732.5692 | 4956.8002 | 4299.9087 | 7307.6856 | 3775.8429 | 3483.7806 | 3181.0556 | 2830.771 | 3523.0191 | 3.8096 | 3.3323 | 3.8081 | 3.4256 | 3.6282
13 | SH-16-TM | 13-SH-16-TM | 8961.9504 | 6718.0792 | 4950.5153 | 4294.5911 | 7299.1175 | 3722.9508 | 3434.9937 | 3146.8511 | 2801.0422 | 3475.9599 | 3.7362 | 3.2688 | 3.7371 | 3.3631 | 3.5592
13 | SH-17-CM | 13-SH-17-CM | 7688.6678 | 5758.8875 | 4298.5668 | 3735.0104 | 6272.0358 | 3378.7641 | 3139.1767 | 2888.0021 | 2570.8604 | 3168.4669 | 3.3084 | 2.8968 | 3.4092 | 3.0853 | 3.1753
13 | SH-17-LM | 13-SH-17-LM | 7223.8562 | 5434.4845 | 4149.0626 | 3618.5256 | 5925.067 | 3225.5227 | 3016.9068 | 2811.7401 | 2508.8314 | 3043.411 | 3.3433 | 2.9138 | 3.4156 | 3.0988 | 3.1987
13 | SH-17-TH | 13-SH-17-TH | 8379.28 | 6216.3791 | 4520.0898 | 3938.6668 | 6781.9883 | 3143.3853 | 2916.5625 | 2711.9688 | 2448.5602 | 2954.5255 | 3.3608 | 2.9297 | 3.3295 | 3.1476 | 3.2027
13 | SH-17-TL | 13-SH-17-TL | 8415.489 | 6242.6809 | 4517.7501 | 3928.9945 | 6805.8513 | 3184.5626 | 2954.7885 | 2729.8631 | 2458.2968 | 2988.9284 | 3.4423 | 3.0004 | 3.4074 | 3.214 | 3.2791
13 | SH-18-LH | 13-SH-18-LH | 7675.3862 | 5649.211 | 4064.0461 | 3518.067 | 6179.8388 | 2944.18 | 2759.9688 | 2535.7812 | 2272.7519 | 2774.0732 | 3.2259 | 2.8056 | 3.0019 | 2.8795 | 3.0326
13 | SH-18-LL | 13-SH-18-LL | 7259.5549 | 5402.7318 | 4002.9918 | 3480.1497 | 5899.157 | 3038.7596 | 2856.0152 | 2624.9872 | 2348.4233 | 2866.8886 | 3.3075 | 2.8762 | 3.0829 | 2.9591 | 3.1105
13 | SH-18-LM | 13-SH-18-LM | 7979.5473 | 5856.2331 | 4153.3944 | 3584.9161 | 6403.2439 | 2988.6212 | 2795.638 | 2548.6354 | 2282.3681 | 2808.4002 | 3.2827 | 2.8464 | 3.0263 | 2.8981 | 3.0766
13 | SH-18-TM | 13-SH-18-TM | 8333.6597 | 6161.6859 | 4430.1708 | 3853.1907 | 6723.8938 | 3060.8653 | 2845.2469 | 2620.2056 | 2363.3023 | 2873.9967 | 3.3138 | 2.8932 | 3.1358 | 3.01 | 3.1304
14 | SA-10-HH | 14-SA-10-HH | 4866.475 | 3621.3719 | 3022.8835 | 3644.3896 | 3662.6463 | 4866.475 | 3621.3719 | 3022.8835 | 3644.3896 | 3662.6463 | 5.0762 | 4.0055 | 3.9349 | 4.5135 | 4.1125
14 | SA-10-HL | 14-SA-10-HL | 5005.6654 | 3744.5943 | 3046.0952 | 3694.5666 | 3772.575 | 5005.6654 | 3744.5943 | 3046.0952 | 3694.5666 | 3772.575 | 5.8371 | 5.0218 | 4.4057 | 5.3214 | 5.0326
14 | SA-10-HM | 14-SA-10-HM | 4886.845 | 3662.1302 | 2985.0288 | 3623.5525 | 3689.8303 | 4886.845 | 3662.1302 | 2985.0288 | 3623.5525 | 3689.8303 | 5.5445 | 4.7679 | 4.1881 | 5.0531 | 4.779
14 | SA-10-LH | 14-SA-10-LH | 4836.8609 | 3595.4286 | 2992.8901 | 3608.472 | 3635.5127 | 4836.8609 | 3595.4286 | 2992.8901 | 3608.472 | 3635.5127 | 4.8867 | 3.8809 | 3.8426 | 4.4104 | 3.9867
14 | SA-10-LL | 14-SA-10-LL | 4777.6806 | 3567.0259 | 2905.0219 | 3527.7698 | 3595.2445 | 4777.6806 | 3567.0259 | 2905.0219 | 3527.7698 | 3595.2445 | 5.199 | 4.4921 | 3.9558 | 4.7995 | 4.503
14 | SA-10-LM | 14-SA-10-LM | 4828.3666 | 3585.7385 | 2973.7109 | 3587.8155 | 3624.3813 | 4828.3666 | 3585.7385 | 2973.7109 | 3587.8155 | 3624.3813 | 4.9137 | 3.8981 | 3.8657 | 4.4378 | 4.0059
14 | SA-10-MH | 14-SA-10-MH | 4825.602 | 3599.6048 | 3029.233 | 3642.1118 | 3643.2601 | 4825.602 | 3599.6048 | 3029.233 | 3642.1118 | 3643.2601 | 4.7566 | 3.7796 | 3.7746 | 4.3246 | 3.8875
14 | SA-10-ML | 14-SA-10-ML | 4914.9267 | 3637.0093 | 2993.3984 | 3619.0738 | 3674.2939 | 4914.9267 | 3637.0093 | 2993.3984 | 3619.0738 | 3674.2939 | 5.2801 | 4.1866 | 4.0373 | 4.6605 | 4.285
14 | SA-10-MM | 14-SA-10-MM | 4824.8194 | 3677.528 | 3030.859 | 3693.5859 | 3703.9488 | 4824.8194 | 3677.528 | 3030.859 | 3693.5859 | 3703.9488 | 4.2006 | 3.6968 | 3.3418 | 4.259 | 3.7207
14 | SA-13-HH | 14-SA-13-HH | 3797.2805 | 2837.2017 | 2349.9193 | 2848.9877 | 2865.71 | 3797.2805 | 2837.2017 | 2349.9193 | 2848.9877 | 2865.71 | 4.7502 | 3.8335 | 3.4016 | 4.1538 | 3.8763
14 | SA-13-HL | 14-SA-13-HL | 4005.9128 | 2993.1116 | 2432.8911 | 2951.8322 | 3015.634 | 4005.9128 | 2993.1116 | 2432.8911 | 2951.8322 | 3015.634 | 4.802 | 4.1302 | 3.6159 | 4.3363 | 4.1368
14 | SA-13-HM | 14-SA-13-HM | 3735.1004 | 2768.6569 | 2256.5932 | 2736.5909 | 2793.1233 | 3735.1004 | 2768.6569 | 2256.5932 | 2736.5909 | 2793.1233 | 4.833 | 3.8492 | 3.3685 | 4.0059 | 3.8861
14 | SA-13-LH | 14-SA-13-LH | 3728.2761 | 2776.891 | 2275.1232 | 2765.801 | 2802.0213 | 3728.2761 | 2776.891 | 2275.1232 | 2765.801 | 2802.0213 | 4.4111 | 3.5267 | 3.1157 | 3.7262 | 3.5646
14 | SA-13-LL | 14-SA-13-LL | 3885.1354 | 2883.4163 | 2385.43 | 2881.5036 | 2913.8797 | 3885.1354 | 2883.4163 | 2385.43 | 2881.5036 | 2913.8797 | 4.3296 | 3.432 | 3.3068 | 3.8071 | 3.5119
14 | SA-13-LM | 14-SA-13-LM | 3942.0644 | 2938.3959 | 2423.064 | 2955.3378 | 2967.661 | 3942.0644 | 2938.3959 | 2423.064 | 2955.3378 | 2967.661 | 4.1385 | 3.2907 | 2.9927 | 3.76 | 3.349
14 | SA-13-MH | 14-SA-13-MH | 3737.8355 | 2779.5286 | 2263.1131 | 2744.5265 | 2802.6298 | 3737.8355 | 2779.5286 | 2263.1131 | 2744.5265 | 2802.6298 | 4.6533 | 3.7032 | 3.2461 | 3.8701 | 3.7403
14 | SA-13-ML | 14-SA-13-ML | 3919.6642 | 2898.5514 | 2368.4539 | 2866.3527 | 2925.776 | 3919.6642 | 2898.5514 | 2368.4539 | 2866.3527 | 2925.776 | 4.523 | 3.5819 | 3.403 | 3.9329 | 3.6584
14 | SA-13-MM | 14-SA-13-MM | 3591.2618 | 2659.5777 | 2155.5023 | 2613.6047 | 2681.349 | 3591.2618 | 2659.5777 | 2155.5023 | 2613.6047 | 2681.349 | 4.6454 | 3.6827 | 3.1685 | 3.7452 | 3.7101
14 | SA-14-HH | 14-SA-14-HH | 3809.0311 | 2822.2672 | 2320.2466 | 2801.3966 | 2850.1888 | 3809.0311 | 2822.2672 | 2320.2466 | 2801.3966 | 2850.1888 | 4.3173 | 3.4222 | 3.2712 | 3.7763 | 3.498
14 | SA-14-HL | 14-SA-14-HL | 3569.9335 | 2640.3584 | 2142.432 | 2598.9679 | 2662.8489 | 3569.9335 | 2640.3584 | 2142.432 | 2598.9679 | 2662.8489 | 4.614 | 3.6581 | 3.1784 | 3.7511 | 3.6902
14 | SA-14-HM | 14-SA-14-HM | 3836.9882 | 2866.8479 | 2329.0781 | 2825.8307 | 2888.2288 | 3836.9882 | 2866.8479 | 2329.0781 | 2825.8307 | 2888.2288 | 4.3945 | 3.7962 | 3.3223 | 3.9896 | 3.8005
14 | SA-14-MH | 14-SA-14-MH | 3717.353 | 2775.5726 | 2302.2243 | 2808.8521 | 2804.9087 | 3717.353 | 2775.5726 | 2302.2243 | 2808.8521 | 2804.9087 | 3.8514 | 3.0654 | 2.7948 | 3.5115 | 3.1205
14 | SA-14-ML | 14-SA-14-ML | 3721.1242 | 2788.1731 | 2271.4446 | 2756.7652 | 2809.0866 | 3721.1242 | 2788.1731 | 2271.4446 | 2756.7652 | 2809.0866 | 4.2791 | 3.7092 | 3.251 | 3.9297 | 3.7139
14 | SA-14-MM | 14-SA-14-MM | 3700.6993 | 2760.9494 | 2277.6779 | 2776.6618 | 2788.2541 | 3700.6993 | 2760.9494 | 2277.6779 | 2776.6618 | 2788.2541 | 3.8563 | 3.0577 | 2.7843 | 3.5344 | 3.1147
14 | SA-15-HH | 14-SA-15-HH | 3274.8203 | 2441.8824 | 2000.3506 | 2425.3652 | 2463.361 | 3274.8203 | 2441.8824 | 2000.3506 | 2425.3652 | 2463.361 | 4.258 | 3.4118 | 2.9614 | 3.5428 | 3.4389
14 | SA-15-HL | 14-SA-15-HL | 3250.5409 | 2412.2064 | 1958.025 | 2372.7991 | 2431.7963 | 3250.5409 | 2412.2064 | 1958.025 | 2372.7991 | 2431.7963 | 4.3658 | 3.5037 | 3.0027 | 3.5819 | 3.5243
14 | SA-15-HM | 14-SA-15-HM | 3234.6016 | 2404.0794 | 1974.6488 | 2394.7651 | 2427.0616 | 3234.6016 | 2404.0794 | 1974.6488 | 2394.7651 | 2427.0616 | 4.1191 | 3.2876 | 2.8657 | 3.406 | 3.3164
14 | SA-15-MH | 14-SA-15-MH | 3588.7052 | 2709.0448 | 2212.5128 | 2665.2689 | 2727.1153 | 3588.7052 | 2709.0448 | 2212.5128 | 2665.2689 | 2727.1153 | 4.1219 | 3.5792 | 3.1583 | 3.6294 | 3.5795
14 | SA-15-ML | 14-SA-15-ML | 3405.2676 | 2522.7741 | 2080.8033 | 2512.1878 | 2548.8877 | 3405.2676 | 2522.7741 | 2080.8033 | 2512.1878 | 2548.8877 | 3.9549 | 3.1276 | 2.9715 | 3.427 | 3.1946
14 | SA-15-MM | 14-SA-15-MM | 3445.4472 | 2579.6273 | 2098.8241 | 2547.1136 | 2598.7592 | 3445.4472 | 2579.6273 | 2098.8241 | 2547.1136 | 2598.7592 | 4.038 | 3.4625 | 3.0328 | 3.6162 | 3.4686
14 | SA-16-CH | 14-SA-16-CH | 3783.2079 | 2753.8305 | 2104.5368 | 2552.0944 | 2761.1507 | 3783.2079 | 2753.8305 | 2104.5368 | 2552.0944 | 2761.1507 | 4.4935 | 3.584 | 2.9136 | 3.5592 | 3.5846
14 | SA-16-CL | 14-SA-16-CL | 3511.9598 | 2543.2221 | 1962.2541 | 2380.9618 | 2554.7523 | 3511.9598 | 2543.2221 | 1962.2541 | 2380.9618 | 2554.7523 | 4.6273 | 3.5905 | 2.8753 | 3.4973 | 3.5946
14 | SA-16-CM | 14-SA-16-CM | 3637.7578 | 2644.2687 | 2041.5666 | 2476.2528 | 2655.2068 | 3637.7578 | 2644.2687 | 2041.5666 | 2476.2528 | 2655.2068 | 4.5816 | 3.5674 | 2.8892 | 3.5167 | 3.5756
14 | SA-16-LH | 14-SA-16-LH | 3170.6888 | 2321.486 | 1870.8183 | 2249.0416 | 2341.2389 | 3170.6888 | 2321.486 | 1870.8183 | 2249.0416 | 2341.2389 | 3.8111 | 3.0025 | 2.8367 | 3.2988 | 3.0666
14 | SA-16-LL | 14-SA-16-LL | 3425.3836 | 2496.2897 | 1972.1912 | 2380.5196 | 2512.8107 | 3425.3836 | 2496.2897 | 1972.1912 | 2380.5196 | 2512.8107 | 4.1027 | 3.2361 | 3.0767 | 3.5787 | 3.3079
14 | SA-16-LM | 14-SA-16-LM | 3444.5093 | 2518.8264 | 2001.658 | 2417.0795 | 2536.3967 | 3444.5093 | 2518.8264 | 2001.658 | 2417.0795 | 2536.3967 | 3.9558 | 3.1227 | 2.999 | 3.4766 | 3.1962
14 | SA-16-NM | 14-SA-16-NM | 3127.0829 | 2257.6905 | 1757.8472 | 2135.8253 | 2271.5127 | 3127.0829 | 2257.6905 | 1757.8472 | 2135.8253 | 2271.5127 | 3.7972 | 3.0059 | 2.7766 | 3.2463 | 3.0587
14 | SA-16-TH | 14-SA-16-TH | 3892.5735 | 2914.2244 | 2257 | 2702.6722 | 2915.6274 | 3892.5735 | 2914.2244 | 2257 | 2702.6722 | 2915.6274 | 4.6328 | 4.0946 | 3.4467 | 4.0218 | 4.0627
14 | SA-16-TL | 14-SA-16-TL | 3451.8121 | 2487.6398 | 1900.1984 | 2300.0185 | 2497.032 | 3451.8121 | 2487.6398 | 1900.1984 | 2300.0185 | 2497.032 | 4.8032 | 3.7498 | 3.143 | 3.7053 | 3.7703
14 | SA-17-CH | 14-SA-17-CH | 3510.7449 | 2553.6618 | 1960.283 | 2375.9446 | 2562.0741 | 3510.7449 | 2553.6618 | 1960.283 | 2375.9446 | 2562.0741 | 4.3559 | 3.4615 | 2.8305 | 3.4532 | 3.4661
14 | SA-17-CL | 14-SA-17-CL | 3477.1736 | 2521.8704 | 1937.5094 | 2349.998 | 2531.4229 | 3477.1736 | 2521.8704 | 1937.5094 | 2349.998 | 2531.4229 | 4.3796 | 3.4322 | 2.8007 | 3.4008 | 3.4407
14 | SA-17-CM | 14-SA-17-CM | 3526.3365 | 2561.6166 | 1956.8704 | 2374.0434 | 2568.9843 | 3526.3365 | 2561.6166 | 1956.8704 | 2374.0434 | 2568.9843 | 4.3644 | 3.4332 | 2.8234 | 3.4319 | 3.4439
14 | SA-17-LH | 14-SA-17-LH | 3199.9053 | 2338.1848 | 1851.5654 | 2249.9823 | 2354.1631 | 3199.9053 | 2338.1848 | 1851.5654 | 2249.9823 | 2354.1631 | 3.6925 | 2.9053 | 2.5855 | 3.2844 | 2.9521
14 | SA-17-LL | 14-SA-17-LL | 3349.6496 | 2434.4555 | 1913.6375 | 2312.2087 | 2449.8748 | 3349.6496 | 2434.4555 | 1913.6375 | 2312.2087 | 2449.8748 | 3.9439 | 3.1117 | 2.9879 | 3.4687 | 3.1852
14 | SA-17-LM | 14-SA-17-LM | 3343.878 | 2434.8581 | 1924.4403 | 2323.6429 | 2451.3818 | 3343.878 | 2434.8581 | 1924.4403 | 2323.6429 | 2451.3818 | 3.9681 | 3.1362 | 2.9778 | 3.4511 | 3.2039
14 | SA-17-TH | 14-SA-17-TH | 3331.8385 | 2508.0846 | 1968.6999 | 2355.3093 | 2511.8934 | 3331.8385 | 2508.0846 | 1968.6999 | 2355.3093 | 2511.8934 | 3.9216 | 3.463 | 2.9773 | 3.4545 | 3.4457
14 | SA-17-TL | 14-SA-17-TL | 2999.0527 | 2154.8177 | 1654.2653 | 2004.4143 | 2165.2186 | 2999.0527 | 2154.8177 | 1654.2653 | 2004.4143 | 2165.2186 | 4.4525 | 3.4623 | 2.8792 | 3.4323 | 3.4804
14 | SA-17-TM | 14-SA-17-TM | 3536.253 | 2562.7748 | 1916.3911 | 2322.4166 | 2563.9598 | 3536.253 | 2562.7748 | 1916.3911 | 2322.4166 | 2563.9598 | 4.3975 | 3.5047 | 2.9409 | 3.5351 | 3.5187
14 | SA-18-LH | 14-SA-18-LH | 3094.1071 | 2255.8959 | 1792.3074 | 2161.2724 | 2272.2775 | 3094.1071 | 2255.8959 | 1792.3074 | 2161.2724 | 2272.2775 | 3.6854 | 2.9106 | 2.7634 | 3.2074 | 2.9739
14 | SA-18-LL | 14-SA-18-LL | 3047.3482 | 2221.428 | 1750.0967 | 2114.4215 | 2235.3094 | 3047.3482 | 2221.428 | 1750.0967 | 2114.4215 | 2235.3094 | 3.6763 | 2.9002 | 2.7629 | 3.2102 | 2.9653
14 | SA-18-TH | 14-SA-18-TH | 3224.5025 | 2378.8494 | 1856.7257 | 2251.8397 | 2387.6673 | 3224.5025 | 2378.8494 | 1856.7257 | 2251.8397 | 2387.6673 | 4.1681 | 3.3125 | 2.7745 | 3.3694 | 3.3272
14 | SA-18-TL | 14-SA-18-TL | 3531.1618 | 2592.3165 | 1983.526 | 2402.6697 | 2596.7899 | 3531.1618 | 2592.3165 | 1983.526 | 2402.6697 | 2596.7899 | 4.5565 | 3.6806 | 3.0533 | 3.7155 | 3.6856
14 | SA-18-TM | 14-SA-18-TM | 3347.3695 | 2457.6663 | 1965.0153 | 2354.2184 | 2474.8714 | 3347.3695 | 2457.6663 | 1965.0153 | 2354.2184 | 2474.8714 | 3.897 | 3.0938 | 2.9455 | 3.4231 | 3.1608
14 | SH-10-HH | 14-SH-10-HH | 10196.4236 | 6778.256 | 4633.354 | 5277.4875 | 7115.028 | 4659.6936 | 3470.7754 | 2849.1651 | 3459.7875 | 3617.1907 | 5.5841 | 4.4516 | 3.9216 | 4.6958 | 4.6057
14 | SH-10-HL | 14-SH-10-HL | 10233.6975 | 6855.4454 | 4695.26 | 5347.6215 | 7183.8181 | 4816.5899 | 3576.4068 | 2919.9015 | 3544.5279 | 3727.6878 | 5.8858 | 4.6752 | 4.1266 | 4.9432 | 4.8417
14 | SH-10-HM | 14-SH-10-HM | 10202.4339 | 6829.7892 | 4724.5585 | 5355.2987 | 7163.289 | 4811.2484 | 3614.7196 | 2951.2518 | 3561.0582 | 3757.182 | 5.3374 | 4.5947 | 4.0207 | 4.6292 | 4.6711
14 | SH-10-LH | 14-SH-10-LH | 10733.4336 | 7076.7173 | 4845.229 | 5474.9441 | 7442.7442 | 4758.6575 | 3551.7275 | 3000.1036 | 3607.5039 | 3709.8151 | 4.8219 | 3.8211 | 3.7792 | 4.3272 | 4.0056
14 | SH-10-LL | 14-SH-10-LL | 10751.1601 | 7067.2608 | 4742.8724 | 5390.5209 | 7426.9676 | 4741.3009 | 3514.9045 | 2861.2068 | 3475.9574 | 3663.8395 | 5.5883 | 4.4367 | 3.8606 | 4.6434 | 4.5886
14 | SH-10-LM | 14-SH-10-LM | 10363.0593 | 6879.7345 | 4672.7257 | 5316.1567 | 7219.8185 | 4627.3179 | 3441.8049 | 2817.8268 | 3424.4451 | 3587.2034 | 5.3397 | 4.2425 | 3.707 | 4.4346 | 4.3882
14 | SH-10-MH | 14-SH-10-MH | 10858.0514 | 7140.3446 | 4848.0005 | 5485.0358 | 7509.4166 | 4808.6669 | 3578.6214 | 2993.0045 | 3604.9579 | 3736.5641 | 5.0432 | 3.9986 | 3.9294 | 4.5052 | 4.1881
14 | SH-10-ML | 14-SH-10-ML | 10622.3219 | 7030.2116 | 4745.2568 | 5403.6174 | 7379.6082 | 4858.4931 | 3595.8189 | 2916.5822 | 3540.9336 | 3748.0807 | 5.9371 | 4.71 | 4.1016 | 4.898 | 4.8712
14 | SH-10-MM | 14-SH-10-MM | 10523.723 | 6980.7308 | 4780.9803 | 5421.3409 | 7331.7559 | 4873.4514 | 3618.9048 | 2995.9168 | 3615.5958 | 3776.6301 | 5.1509 | 4.0763 | 3.9566 | 4.553 | 4.2653
14 | SH-13-HH | 14-SH-13-HH | 9532.4271 | 6229.8001 | 4143.7287 | 4687.1176 | 6550.6721 | 3951.6259 | 2943.4667 | 2408.9602 | 2921.6062 | 3066.5155 | 4.9977 | 3.9809 | 3.5142 | 4.1755 | 4.1192
14 | SH-13-HL | 14-SH-13-HL | 8646.0802 | 5648.2453 | 3781.7079 | 4286.3342 | 5943.2779 | 3747.6869 | 2781.778 | 2268.5371 | 2751.01 | 2899.2192 | 4.9646 | 3.9898 | 3.4364 | 4.1278 | 4.1112
14 | SH-13-HM | 14-SH-13-HM | 8820.3189 | 5791.2615 | 3897.9494 | 4421.5862 | 6088.9423 | 3841.9301 | 2855.0995 | 2332.5331 | 2829.4826 | 2975.4512 | 4.8498 | 3.8597 | 3.3941 | 4.021 | 3.9924
14 | SH-13-LH | 14-SH-13-LH | 10531.0379 | 6648.9977 | 4201.4299 | 4717.0152 | 7022.3377 | 3833.323 | 2857.4409 | 2392.6836 | 2880.9732 | 2982.829 | 4.0372 | 3.2187 | 3.1926 | 3.6567 | 3.3711
14 | SH-13-LL | 14-SH-13-LL | 8826.3403 | 5686.4071 | 3728.7283 | 4211.5864 | 5993.4649 | 3573.3882 | 2652.8341 | 2158.1558 | 2616.912 | 2764.0328 | 4.5108 | 3.5823 | 3.1288 | 3.7149 | 3.7045
14 | SH-13-LM | 14-SH-13-LM | 8408.9913 | 5547.3304 | 3792.6705 | 4351.4395 | 5835.0829 | 4023.8937 | 2995.3028 | 2465.0461 | 3005.8149 | 3123.357 | 4.2485 | 3.3834 | 3.0823 | 3.8733 | 3.5211
14 | SH-13-MH | 14-SH-13-MH | 9329.0118 | 6047.1435 | 3985.3195 | 4495.4434 | 6366.3239 | 3632.1442 | 2715.5572 | 2224.423 | 2698.5 | 2827.0687 | 4.5632 | 3.6675 | 3.1395 | 3.7813 | 3.7768
14 | SH-13-ML | 14-SH-13-ML | 9658.3081 | 6250.6745 | 4139.041 | 4689.059 | 6586.451 | 4144.0595 | 3081.4814 | 2551.7423 | 3080.9086 | 3214.966 | 4.5718 | 3.6303 | 3.5449 | 4.0774 | 3.7987
14 | SH-13-MM | 14-SH-13-MM | 9007.6861 | 5886.3803 | 3964.3421 | 4486.7932 | 6196.1236 | 3828.5136 | 2869.8826 | 2338.447 | 2835.0396 | 2984.3209 | 4.5597 | 3.8905 | 3.4068 | 4.0415 | 3.9666
14 | SH-14-HH | 14-SH-14-HH | 8886.2575 | 5799.4849 | 3860.7629 | 4367.9797 | 6100.734 | 3726.8446 | 2770.3537 | 2261.5256 | 2741.9315 | 2886.67 | 4.7984 | 3.8206 | 3.3682 | 3.9958 | 3.9528
14 | SH-14-HL | 14-SH-14-HL | 8879.6685 | 5701.6692 | 3721.5252 | 4199.2039 | 6012.2148 | 3575.1087 | 2645.8626 | 2147.3642 | 2604.3267 | 2757.9991 | 4.6455 | 3.69 | 3.2408 | 3.8324 | 3.8176
14 | SH-14-HM | 14-SH-14-HM | 8841.7447 | 5704.4282 | 3745.1165 | 4229.4003 | 6010.8883 | 3539.6568 | 2629.062 | 2147.3366 | 2604.6497 | 2740.1305 | 4.4758 | 3.566 | 3.1276 | 3.709 | 3.6868
14 | SH-14-MH | 14-SH-14-MH | 9766.6271 | 6187.2139 | 3916.969 | 4397.8142 | 6529.9638 | 3558.494 | 2650.3823 | 2217.4285 | 2669.9905 | 2766.9392 | 3.853 | 3.0751 | 3.0088 | 3.4579 | 3.2151
14 | SH-14-ML | 14-SH-14-ML | 10048.0967 | 6217.6755 | 3843.309 | 4317.3354 | 6589.8836 | 3553.3495 | 2627.5206 | 2129.7909 | 2584.8005 | 2739.1024 | 4.5232 | 3.5888 | 3.1226 | 3.7033 | 3.7102
14 | SH-14-MM | 14-SH-14-MM | 9014.4583 | 5694.962 | 3735.1415 | 4213.4441 | 6032.1229 | 3589.9722 | 2693.127 | 2198.5285 | 2655.2682 | 2800.2324 | 4.1283 | 3.5852 | 3.1691 | 3.6442 | 3.6426
14 | SH-15-HH | 14-SH-15-HH | 9734.4732 | 6064.883 | 3760.7058 | 4201.8546 | 6417.3228 | 3277.2643 | 2442.9676 | 2008.1169 | 2434.7154 | 2545.8122 | 4.1303 | 3.3059 | 2.8776 | 3.4205 | 3.412
14 | SH-15-HL | 14-SH-15-HL | 7723.8256 | 5040.334 | 3376.0072 | 3823.6366 | 5305.0942 | 3327.0359 | 2466.0921 | 2005.9688 | 2432.7187 | 2570.3226 | 4.2833 | 3.4074 | 2.9972 | 3.5414 | 3.5246
14 | SH-15-HM | 14-SH-15-HM | 7826.9116 | 5080.5518 | 3380.6337 | 3816.562 | 5351.1485 | 3213.084 | 2389.8258 | 1944.4086 | 2357.6121 | 2488.9993 | 4.2148 | 3.373 | 2.8363 | 3.4065 | 3.4695
14 | SH-15-MH | 14-SH-15-MH | 9434.0251 | 5789.0351 | 3686.7164 | 4163.8045 | 6163.7351 | 3497.2584 | 2622.838 | 2136.6459 | 2593.0444 | 2727.1662 | 4.0457 | 3.4736 | 3.0435 | 3.6236 | 3.5379
14 | SH-15-ML | 14-SH-15-ML | 8947.2895 | 5574.7943 | 3512.0059 | 3956.9026 | 5906.9416 | 3319.2737 | 2452.9649 | 1986.101 | 2409.6891 | 2557.1548 | 4.3069 | 3.4143 | 2.9575 | 3.4953 | 3.5283
14 | SH-15-MM | 14-SH-15-MM | 8918.5295 | 5659.5907 | 3584.1836 | 4014.4437 | 5970.335 | 3190.058 | 2371.6635 | 1928.7698 | 2336.3473 | 2470.1242 | 4.1221 | 3.3051 | 2.7983 | 3.3729 | 3.4013
14 | SH-16-CH | 14-SH-16-CH | 9918.9836 | 6238.152 | 3780.651 | 4249.977 | 6574.3935 | 3600.0676 | 2624.209 | 2030.7885 | 2465.5837 | 2731.6492 | 4.4968 | 3.5365 | 2.9109 | 3.5389 | 3.6441
14 | SH-16-CL | 14-SH-16-CL | 9577.1433 | 6053.5478 | 3683.6192 | 4147.6894 | 6373.7829 | 3705.2688 | 2687.6942 | 2045.6897 | 2480.3278 | 2796.1656 | 4.5408 | 3.5903 | 2.949 | 3.6014 | 3.6952
14 | SH-16-LH | 14-SH-16-LH | 9845.7567 | 6089.3042 | 3673.3092 | 4092.3839 | 6441.7887 | 3288.0099 | 2419.7705 | 1969.5965 | 2361.0638 | 2525.2254 | 3.8726 | 3.0577 | 2.9233 | 3.3896 | 3.1961
14 | SH-16-LL | 14-SH-16-LL | 9709.8687 | 6005.1593 | 3609.2846 | 4033.1867 | 6351.5256 | 3474.0883 | 2535.7921 | 1993.4347 | 2419.0882 | 2642.8852 | 4.0166 | 3.1675 | 2.8137 | 3.5511 | 3.294
14 | SH-16-LM | 14-SH-16-LM | 10198.9725 | 6289.8975 | 3759.678 | 4198.774 | 6654.8073 | 3467.5865 | 2543.1694 | 2025.4667 | 2465.4241 | 2651.4853 | 3.9429 | 3.1063 | 2.7766 | 3.5387 | 3.2346
14 | SH-16-TH | 14-SH-16-TH | 11545.9262 | 7174.7122 | 4172.0621 | 4645.9322 | 7560.5486 | 3494.4131 | 2552.7073 | 1968.7326 | 2387.5164 | 2654.9475 | 4.7632 | 3.7553 | 3.0571 | 3.7121 | 3.863
14 | SH-16-TL | 14-SH-16-TL | 11600.8467 | 7325.1027 | 4326.7689 | 4831.3387 | 7696.3369 | 3882.7553 | 2885.2836 | 2204.0508 | 2656.592 | 2986.0842 | 4.5368 | 4.0027 | 3.3573 | 3.9273 | 4.0333
14 | SH-16-TM | 14-SH-16-TM | 11575.3985 | 7311.9816 | 4317.732 | 4831.6564 | 7681.962 | 3811.3276 | 2837.7098 | 2170.3264 | 2630.2938 | 2936.4452 | 4.4513 | 3.9148 | 3.2703 | 3.9781 | 3.9509
14 | SH-17-CM | 14-SH-17-CM | 9452.8932 | 5869.2195 | 3527.441 | 3960.4734 | 6202.074 | 3509.4595 | 2547.7594 | 1940.5783 | 2353.2037 | 2650.2872 | 4.3325 | 3.4211 | 2.8077 | 3.4313 | 3.5218
14 | SH-17-LM | 14-SH-17-LM | 9307.8283 | 5769.0479 | 3488.9523 | 3912.3376 | 6101.6146 | 3323.5471 | 2440.505 | 1954.3327 | 2351.8294 | 2544.2041 | 3.8835 | 3.0677 | 3.0016 | 3.4711 | 3.2149
14 | SH-17-TH | 14-SH-17-TH | 11393.5344 | 7065.711 | 4106.9165 | 4568.1924 | 7449.1878 | 3357.7148 | 2456.0619 | 1903.2028 | 2304.8378 | 2554.7598 | 4.439 | 3.5228 | 2.9378 | 3.5739 | 3.6283
14 | SH-17-TL | 14-SH-17-TL | 11453.1647 | 7090.2702 | 4099.1923 | 4558.0473 | 7475.5998 | 3394.436 | 2479.8563 | 1907.8176 | 2309.7482 | 2578.3719 | 4.536 | 3.6083 | 2.999 | 3.6438 | 3.7131
14 | SH-18-LH | 14-SH-18-LH | 10418.3069 | 6366.7067 | 3675.0873 | 4072.5585 | 6734.249 | 3251.6505 | 2375.95 | 1867.0868 | 2267.8225 | 2475.6875 | 3.7289 | 2.9445 | 2.6344 | 3.3448 | 3.0645
14 | SH-18-LL | 14-SH-18-LL | 9767.2809 | 6001.932 | 3563.1693 | 3972.8676 | 6352.7572 | 3378.6272 | 2469.3761 | 1943.5419 | 2359.5978 | 2573.2484 | 3.8742 | 3.0609 | 2.7434 | 3.4874 | 3.1861
14 | SH-18-LM | 14-SH-18-LM | 10782.3281 | 6557.0044 | 3681.3191 | 4093.9299 | 6931.6798 | 3182.7442 | 2320.0739 | 1830.3577 | 2207.2841 | 2419.1348 | 3.7787 | 2.9829 | 2.8891 | 3.3502 | 3.1229
14 | SH-18-TM | 14-SH-18-TM | 11648.8461 | 7237.3629 | 4209.4788 | 4700.1251 | 7627.4983 | 3456.7975 | 2546.5533 | 1992.6602 | 2421.7717 | 2647.5616 | 3.8464 | 3.0375 | 2.733 | 3.4836 | 3.1638
15 | SA-10-HH | 15-SA-10-HH | 10330.5189 | 8166.3556 | 6617.3179 | 8002.7345 | 8615.01 | 10330.5189 | 8166.3556 | 6617.3179 | 8002.7345 | 8615.01 | 5.4089 | 4.2618 | 3.9016 | 4.9534 | 4.5998
15 | SA-10-HL | 15-SA-10-HL | 11114.1175 | 8785.9432 | 7113.9586 | 8503.0824 | 9263.2799 | 11114.1175 | 8785.9432 | 7113.9586 | 8503.0824 | 9263.2799 | 6.1579 | 4.8798 | 5.0485 | 5.7014 | 5.342
15 | SA-10-HM | 15-SA-10-HM | 10640.5426 | 8401.4732 | 6833.7573 | 8164.6012 | 8867.9185 | 10640.5426 | 8401.4732 | 6833.7573 | 8164.6012 | 8867.9185 | 5.814 | 4.6074 | 4.7629 | 5.3795 | 5.0431
15 | SA-10-LH | 15-SA-10-LH | 9972.6196 | 7904.0832 | 6452.9588 | 7806.1398 | 8339.6905 | 9972.6196 | 7904.0832 | 6452.9588 | 7806.1398 | 8339.6905 | 4.9983 | 3.9593 | 3.6645 | 4.647 | 4.2727
15 | SA-10-LL | 15-SA-10-LL | 10340.0977 | 8180.1226 | 6625.5756 | 7932.3893 | 8623.1028 | 10340.0977 | 8180.1226 | 6625.5756 | 7932.3893 | 8623.1028 | 5.3412 | 4.2273 | 4.3865 | 4.9435 | 4.6319
15 | SA-10-LM | 15-SA-10-LM | 10035.6754 | 7948.5107 | 6467.6304 | 7819.4045 | 8384.3216 | 10035.6754 | 7948.5107 | 6467.6304 | 7819.4045 | 8384.3216 | 5.0516 | 3.9948 | 3.6916 | 4.6772 | 4.3124
15 | SA-10-MH | 15-SA-10-MH | 9535.0433 | 7849.6457 | 6459.4931 | 7835.9895 | 8176.9475 | 9535.0433 | 7849.6457 | 6459.4931 | 7835.9895 | 8176.9475 | 4.3152 | 3.8498 | 3.5706 | 4.5236 | 3.9841
15 | SA-10-ML | 15-SA-10-ML | 10617.4794 | 8413.282 | 6785.4157 | 8184.6344 | 8860.2784 | 10617.4794 | 8413.282 | 6785.4157 | 8184.6344 | 8860.2784 | 5.4481 | 4.3097 | 3.9707 | 5.0443 | 4.6499
15 | SA-10-MM | 15-SA-10-MM | 9834.6717 | 8021.503 | 6530.3447 | 7829.1544 | 8366.7661 | 9834.6717 | 8021.503 | 6530.3447 | 7829.1544 | 8366.7661 | 4.5852 | 3.9676 | 3.446 | 4.0443 | 4.0892
15 | SA-13-HH | 15-SA-13-HH | 8279.4081 | 6552.9735 | 5391.6855 | 6431.8616 | 6922.1725 | 8279.4081 | 6552.9735 | 5391.6855 | 6431.8616 | 6922.1725 | 4.6827 | 3.7105 | 3.8339 | 4.3307 | 4.0612
15 | SA-13-HL | 15-SA-13-HL | 8613.6436 | 6793.7062 | 5520.638 | 6596.493 | 7172.8137 | 8613.6436 | 6793.7062 | 5520.638 | 6596.493 | 7172.8137 | 5.0417 | 4.0072 | 4.137 | 4.6828 | 4.3808
15 | SA-13-HM | 15-SA-13-HM | 8299.8083 | 6639.482 | 5314.2375 | 6381.7827 | 6958.0859 | 8299.8083 | 6639.482 | 5314.2375 | 6381.7827 | 6958.0859 | 4.7988 | 4.3089 | 3.9118 | 4.7331 | 4.4231
15 | SA-13-LH | 15-SA-13-LH | 7718.3586 | 6112.0561 | 5061.7287 | 6030.4723 | 6461.2893 | 7718.3586 | 6112.0561 | 5061.7287 | 6030.4723 | 6461.2893 | 4.1903 | 3.3466 | 3.5006 | 3.9551 | 3.6608
15 | SA-13-LL | 15-SA-13-LL | 8222.6102 | 6506.3575 | 5276.661 | 6363.2654 | 6861.4086 | 8222.6102 | 6506.3575 | 5276.661 | 6363.2654 | 6861.4086 | 4.5638 | 3.6127 | 3.3211 | 4.2143 | 3.8952
15 | SA-13-LM | 15-SA-13-LM | 7858.4606 | 6433.6001 | 5276.672 | 6382.9009 | 6711.3367 | 7858.4606 | 6433.6001 | 5276.672 | 6382.9009 | 6711.3367 | 3.8164 | 3.4142 | 3.1731 | 4.0229 | 3.5314
15 | SA-13-MH | 15-SA-13-MH | 8071.0331 | 6484.5302 | 5211.4924 | 6212.6657 | 6786.9041 | 8071.0331 | 6484.5302 | 5211.4924 | 6212.6657 | 6786.9041 | 4.523 | 4.0785 | 3.6914 | 4.1835 | 4.1664
15 | SA-13-ML | 15-SA-13-ML | 8371.0212 | 6596.118 | 5298.2379 | 6346.7956 | 6955.1997 | 8371.0212 | 6596.118 | 5298.2379 | 6346.7956 | 6955.1997 | 4.7496 | 3.7674 | 3.8693 | 4.3851 | 4.118
15 | SA-13-MM | 15-SA-13-MM | 8093.9444 | 6357.2617 | 5078.1358 | 6099.554 | 6706.6854 | 8093.9444 | 6357.2617 | 5078.1358 | 6099.554 | 6706.6854 | 5.1703 | 4.1665 | 3.7259 | 4.4915 | 4.4322
15 | SA-14-HH | 15-SA-14-HH | 8091.2606 | 6389.3535 | 5192.511 | 6206.1011 | 6742.9962 | 8091.2606 | 6389.3535 | 5192.511 | 6206.1011 | 6742.9962 | 4.5259 | 3.5922 | 3.7022 | 4.1902 | 3.9279
15 | SA-14-HL | 15-SA-14-HL | 7825.8552 | 6222.4098 | 4961.8946 | 5955.6113 | 6532.171 | 7825.8552 | 6222.4098 | 4961.8946 | 5955.6113 | 6532.171 | 4.6023 | 4.1236 | 3.6964 | 4.4496 | 4.2257
15 | SA-14-HM | 15-SA-14-HM | 8086.0777 | 6371.6192 | 5189.7429 | 6199.6644 | 6731.8854 | 8086.0777 | 6371.6192 | 5189.7429 | 6199.6644 | 6731.8854 | 4.5488 | 3.6203 | 3.7412 | 4.2361 | 3.9567
15 | SA-14-MH | 15-SA-14-MH | 7373.1981 | 6056.8838 | 4993.8679 | 6045.9112 | 6315.8205 | 7373.1981 | 6056.8838 | 4993.8679 | 6045.9112 | 6315.8205 | 3.5476 | 3.1805 | 2.9627 | 3.7564 | 3.2886
15 | SA-14-ML | 15-SA-14-ML | 7844.1834 | 6206.5403 | 5085.0122 | 6071.6226 | 6552.9843 | 7844.1834 | 6206.5403 | 5085.0122 | 6071.6226 | 6552.9843 | 4.4568 | 3.5479 | 3.6821 | 4.163 | 3.88
15 | SA-14-MM | 15-SA-14-MM | 7356.5774 | 5817.1412 | 4946.4151 | 5929.5777 | 6179.7615 | 7356.5774 | 5817.1412 | 4946.4151 | 5929.5777 | 6179.7615 | 3.5788 | 2.757 | 2.843 | 3.3344 | 3.053
15 | SA-15-HH | 15-SA-15-HH | 7290.5965 | 5866.0895 | 4724.2247 | 5675.8163 | 6140.0322 | 7290.5965 | 5866.0895 | 4724.2247 | 5675.8163 | 6140.0322 | 4.26 | 3.8276 | 3.481 | 4.2177 | 3.9296
15 | SA-15-HL | 15-SA-15-HL | 7354.2224 | 5778.3489 | 4623.4672 | 5548.8922 | 6096.4518 | 7354.2224 | 5778.3489 | 4623.4672 | 5548.8922 | 6096.4518 | 4.8938 | 3.9447 | 3.569 | 4.3 | 4.2039
15 | SA-15-HM | 15-SA-15-HM | 7126.9495 | 5710.7526 | 4585.2482 | 5508.4932 | 5983.9642 | 7126.9495 | 5710.7526 | 4585.2482 | 5508.4932 | 5983.9642 | 4.1249 | 3.6942 | 3.3462 | 4.043 | 3.7938
15 | SA-15-MH | 15-SA-15-MH | 7527.9767 | 5949.9438 | 4908.9797 | 5847.6837 | 6290.7633 | 7527.9767 | 5949.9438 | 4908.9797 | 5847.6837 | 6290.7633 | 4.2537 | 3.3851 | 3.4955 | 3.9576 | 3.6992
15 | SA-15-ML | 15-SA-15-ML | 7289.034 | 5752.0048 | 4685.2658 | 5597.7348 | 6073.9324 | 7289.034 | 5752.0048 | 4685.2658 | 5597.7348 | 6073.9324 | 4.1872 | 3.3193 | 3.3786 | 3.8376 | 3.6235
15 | SA-15-MM | 15-SA-15-MM | 7328.4725 | 5776.6332 | 4707.4554 | 5622.0585 | 6102.8598 | 7328.4725 | 5776.6332 | 4707.4554 | 5622.0585 | 6102.8598 | 4.2232 | 3.358 | 3.4439 | 3.9074 | 3.6665
15 | SA-16-CH | 15-SA-16-CH | 8290.6106 | 6484.1106 | 5176.707 | 6186.4167 | 6849.7192 | 8290.6106 | 6484.1106 | 5176.707 | 6186.4167 | 6849.7192 | 4.1267 | 3.2891 | 3.4372 | 3.8751 | 3.5995
15 | SA-16-CL | 15-SA-16-CL | 8067.9879 | 6363.9731 | 4834.3303 | 5820.0054 | 6654.3635 | 8067.9879 | 6363.9731 | 4834.3303 | 5820.0054 | 6654.3635 | 4.3762 | 3.9505 | 3.5433 | 4.3054 | 4.04
15 | SA-16-CM | 15-SA-16-CM | 8204.3736 | 6550.7287 | 5016.8458 | 6043.3914 | 6826.1646 | 8204.3736 | 6550.7287 | 5016.8458 | 6043.3914 | 6826.1646 | 4.3255 | 3.9068 | 3.5138 | 4.2746 | 3.9968
15 | SA-16-LH | 15-SA-16-LH | 7443.8513 | 5779.9633 | 4529.8734 | 5468.8427 | 6108.4351 | 7443.8513 | 5779.9633 | 4529.8734 | 5468.8427 | 6108.4351 | 4.1531 | 3.273 | 2.9884 | 3.7998 | 3.531
15 | SA-16-LL | 15-SA-16-LL | 7969.8012 | 6188.2659 | 4790.1046 | 5768.342 | 6527.5675 | 7969.8012 | 6188.2659 | 4790.1046 | 5768.342 | 6527.5675 | 4.4421 | 3.5035 | 3.2033 | 4.075 | 3.7795
15 | SA-16-LM | 15-SA-16-LM | 7817.0168 | 6087.2439 | 4745.44 | 5721.4114 | 6420.7565 | 7817.0168 | 6087.2439 | 4745.44 | 5721.4114 | 6420.7565 | 4.2496 | 3.3525 | 3.0688 | 3.9006 | 3.6169
15 | SA-16-NM | 15-SA-16-NM | 7189.4514 | 5532.6813 | 4195.7451 | 5038.4265 | 5838.4759 | 7189.4514 | 5532.6813 | 4195.7451 | 5038.4265 | 5838.4759 | 4.0087 | 3.1661 | 2.8949 | 3.6781 | 3.4137
15 | SA-16-TH | 15-SA-16-TH | 8889.6744 | 6882.844 | 5438.2922 | 6467.7662 | 7286.5846 | 8889.6744 | 6882.844 | 5438.2922 | 6467.7662 | 7286.5846 | 4.8364 | 3.8509 | 4.0006 | 4.5219 | 4.2118
15 | SA-16-TL | 15-SA-16-TL | 8411.3439 | 6441.8587 | 4847.1214 | 5836.9194 | 6803.84 | 8411.3439 | 6441.8587 | 4847.1214 | 5836.9194 | 6803.84 | 5.1707 | 4.1793 | 3.7463 | 4.531 | 4.4433
15 | SA-17-CH | 15-SA-17-CH | 7824.6824 | 6105.4881 | 4842.0059 | 5792.1702 | 6449.3425 | 7824.6824 | 6105.4881 | 4842.0059 | 5792.1702 | 6449.3425 | 4.0525 | 3.2197 | 3.3381 | 3.7737 | 3.5229
15 | SA-17-CL | 15-SA-17-CL | 7836.6186 | 6088.1944 | 4755.1222 | 5698.5335 | 6427.8596 | 7836.6186 | 6088.1944 | 4755.1222 | 5698.5335 | 6427.8596 | 4.1409 | 3.2878 | 3.3676 | 3.8151 | 3.5907
15 | SA-17-CM | 15-SA-17-CM | 7889.8169 | 6137.1009 | 4816.0772 | 5763.8717 | 6480.5753 | 7889.8169 | 6137.1009 | 4816.0772 | 5763.8717 | 6480.5753 | 4.1152 | 3.2674 | 3.3588 | 3.8008 | 3.5706
15 | SA-17-LH | 15-SA-17-LH | 7081.6171 | 5684.0545 | 4432.2674 | 5301.7624 | 5925.318 | 7081.6171 | 5684.0545 | 4432.2674 | 5301.7624 | 5925.318 | 3.6065 | 3.1854 | 2.9093 | 3.3118 | 3.2831
15 | SA-17-LL | 15-SA-17-LL | 7712.194 | 5992.6096 | 4629.9898 | 5574.7246 | 6317.6686 | 7712.194 | 5992.6096 | 4629.9898 | 5574.7246 | 6317.6686 | 4.2527 | 3.3536 | 3.0688 | 3.9037 | 3.6185
15 | SA-17-LM | 15-SA-17-LM | 7615.4136 | 5909.6126 | 4597.2832 | 5539.2772 | 6239.6916 | 7615.4136 | 5909.6126 | 4597.2832 | 5539.2772 | 6239.6916 | 4.2532 | 3.3614 | 3.0773 | 3.9086 | 3.624
15 | SA-17-TH | 15-SA-17-TH | 7547.8309 | 5892.2287 | 4757.4237 | 5646.1436 | 6237.7026 | 7547.8309 | 5892.2287 | 4757.4237 | 5646.1436 | 6237.7026 | 4.1192 | 3.2736 | 3.4085 | 3.8403 | 3.5838
15 | SA-17-TL | 15-SA-17-TL | 7329.2214 | 5718.6921 | 4317.8992 | 5169.1103 | 5998.2309 | 7329.2214 | 5718.6921 | 4317.8992 | 5169.1103 | 5998.2309 | 4.4002 | 3.9331 | 3.5057 | 3.9923 | 4.0203
15 | SA-17-TM | 15-SA-17-TM | 8531.4606 | 6635.6233 | 5007.8873 | 6028.9557 | 6969.4853 | 8531.4606 | 6635.6233 | 5007.8873 | 6028.9557 | 6969.4853 | 4.7119 | 3.8109 | 3.4593 | 4.2166 | 4.0606
15 | SA-18-LH | 15-SA-18-LH | 7153.9982 | 5559.4975 | 4318.6058 | 5206.7721 | 5865.6865 | 7153.9982 | 5559.4975 | 4318.6058 | 5206.7721 | 5865.6865 | 3.9631 | 3.1294 | 2.8642 | 3.641 | 3.375
15 | SA-18-LL | 15-SA-18-LL | 7042.9454 | 5462.926 | 4243.1191 | 5108.1303 | 5767.5481 | 7042.9454 | 5462.926 | 4243.1191 | 5108.1303 | 5767.5481 | 3.9783 | 3.1382 | 2.8697 | 3.6492 | 3.3853
15 | SA-18-TH | 15-SA-18-TH | 7204.427 | 5803.6555 | 4518.1168 | 5454.1335 | 6042.3734 | 7204.427 | 5803.6555 | 4518.1168 | 5454.1335 | 6042.3734 | 3.9574 | 3.5795 | 3.2624 | 3.9716 | 3.6688
15 | SA-18-TL | 15-SA-18-TL | 7953.6625 | 6211.0118 | 4967.8658 | 5911.9601 | 6565.8385 | 7953.6625 | 6211.0118 | 4967.8658 | 5911.9601 | 6565.8385 | 4.2954 | 3.4248 | 3.582 | 4.0473 | 3.7485
15 | SA-18-TM | 15-SA-18-TM | 7464.4849 | 5816.1363 | 4677.2792 | 5555.4296 | 6158.1138 | 7464.4849 | 5816.1363 | 4677.2792 | 5555.4296 | 6158.1138 | 4.0789 | 3.2461 | 3.3803 | 3.8118 | 3.5521
15 | SH-10-HH | 15-SH-10-HH | 11142.3732 | 8528.0303 | 6621.088 | 7911.4126 | 9034.0536 | 10000.8891 | 8077.4597 | 6533.9503 | 7859.852 | 8438.6487 | 5.472 | 4.9157 | 4.469 | 5.4145 | 5.0434
15 | SH-10-HL | 15-SH-10-HL | 11618.6815 | 8858.5157 | 6831.3925 | 8155.834 | 9388.5716 | 10468.0609 | 8408.0859 | 6744.6616 | 8104.421 | 8790.4556 | 5.742 | 5.1638 | 4.6969 | 5.6937 | 5.2966
15 | SH-10-HM | 15-SH-10-HM | 11489.0051 | 8636.9442 | 6811.0084 | 8074.1505 | 9231.3268 | 10382.832 | 8201.3948 | 6725.4088 | 8023.8272 | 8654.6933 | 5.6359 | 4.4562 | 4.5714 | 5.175 | 4.8708
15 | SH-10-LH | 15-SH-10-LH | 10956.1899 | 8221.775 | 6479.416 | 7799.825 | 8797.7377 | 9754.0089 | 7751.7737 | 6388.3354 | 7746.2235 | 8173.0608 | 5.0366 | 3.9842 | 3.6714 | 4.6596 | 4.2937
15 | SH-10-LL | 15-SH-10-LL | 11320.0957 | 8462.1459 | 6600.4595 | 7835.2644 | 9050.3986 | 10160.8586 | 8008.4698 | 6512.5391 | 7782.6997 | 8447.7547 | 5.3504 | 4.2335 | 4.3583 | 4.9303 | 4.629
15 | SH-10-LM | 15-SH-10-LM | 10954.4341 | 8203.8641 | 6459.6257 | 7651.9304 | 8779.2002 | 9808.6866 | 7752.335 | 6371.0998 | 7599.8363 | 8181.7604 | 5.1497 | 4.075 | 4.1801 | 4.7333 | 4.4529
15 | SH-10-MH | 15-SH-10-MH | 11226.2199 | 8417.7128 | 6595.1062 | 7926.789 | 9001.9908 | 10037.8398 | 7953.7736 | 6505.4625 | 7873.7551 | 8384.8735 | 5.2827 | 4.1799 | 3.8532 | 4.8923 | 4.5046
15 | SH-10-ML | 15-SH-10-ML | 11591.0407 | 8821.727 | 6776.5497 | 8052.4287 | 9349.1933 | 10507.9053 | 8394.6912 | 6693.081 | 8003.5274 | 8784.3585 | 5.6975 | 5.129 | 4.6477 | 5.2621 | 5.2402
15 | SH-10-MM | 15-SH-10-MM | 11510.8208 | 8635.7788 | 6719.6301 | 8062.3981 | 9223.4831 | 10358.6243 | 8186.4686 | 6633.0618 | 8011.1393 | 8625.4643 | 5.451 | 4.3026 | 3.9448 | 5.0065 | 4.6365
15 | SH-13-HH | 15-SH-13-HH | 9710.8095 | 7247.1237 | 5691.3632 | 6731.3411 | 7762.5392 | 8620.6468 | 6819.6279 | 5607.5065 | 6682.1455 | 7195.215 | 4.9835 | 3.9579 | 4.0662 | 4.6065 | 4.3205
15 | SH-13-HL | 15-SH-13-HL | 9360.0705 | 6982.7632 | 5366.7871 | 6404.5901 | 7459.7251 | 8413.058 | 6613.2825 | 5295.6636 | 6362.4054 | 6968.1123 | 5.542 | 4.471 | 4.0689 | 4.9196 | 4.7637
15 | SH-13-HM | 15-SH-13-HM | 9406.7908 | 7157.099 | 5515.7211 | 6536.9862 | 7588.7732 | 8433.6124 | 6772.839 | 5440.8465 | 6492.9467 | 7081.0057 | 4.8403 | 4.3382 | 3.9315 | 4.4586 | 4.4393
15 | SH-13-LH | 15-SH-13-LH | 9031.7146 | 6698.569 | 5222.7793 | 6272.1008 | 7188.8759 | 7870.7885 | 6251.8997 | 5137.2028 | 6221.024 | 6589.6071 | 4.1579 | 3.3121 | 3.0892 | 3.9218 | 3.5679
15 | SH-13-LL | 15-SH-13-LL | 8813.6315 | 6557.5671 | 5114.3616 | 6057.5497 | 7025.6436 | 7813.6124 | 6168.1785 | 5038.8796 | 6013.4439 | 6506.8613 | 4.4081 | 3.4942 | 3.5773 | 4.0561 | 3.8147
15 | SH-13-LM | 15-SH-13-LM | 8875.7141 | 6890.3003 | 5430.62 | 6526.8863 | 7277.2259 | 8001.5296 | 6549.7449 | 5365.2157 | 6488.355 | 6823.7283 | 3.8935 | 3.4939 | 3.2595 | 4.1325 | 3.6101
15 | SH-13-MH | 15-SH-13-MH | 9138.2733 | 6785.2955 | 5237.9503 | 6249.1326 | 7266.6103 | 8018.3245 | 6344.2989 | 5152.0237 | 6198.0628 | 6682.889 | 5.0328 | 4.0601 | 3.6949 | 4.4666 | 4.3259
15 | SH-13-ML | 15-SH-13-ML | 9634.2732 | 7216.7116 | 5629.7401 | 6741.2705 | 7714.784 | 8602.4453 | 6819.9531 | 5553.9219 | 6696.6856 | 7182.3447 | 4.7876 | 3.7996 | 3.51 | 4.4562 | 4.0917
15 | SH-13-MM | 15-SH-13-MM | 9384.1732 | 6991.1965 | 5459.6378 | 6468.7813 | 7487.8934 | 8360.1829 | 6590.9232 | 5381.6509 | 6422.4872 | 6955.7526 | 4.8349 | 3.8334 | 3.906 | 4.4364 | 4.1813
15 | SH-14-HH | 15-SH-14-HH | 9184.4667 | 6861.4695 | 5362.9997 | 6352.3526 | 7341.821 | 8190.3688 | 6472.2151 | 5286.6863 | 6307.4996 | 6824.7967 | 4.8019 | 3.8143 | 3.9111 | 4.4347 | 4.1622
15 | SH-14-HL | 15-SH-14-HL | 8920.634 | 6706.9109 | 5112.5611 | 6090.2984 | 7134.5059 | 7940.588 | 6325.056 | 5038.7135 | 6046.7159 | 6625.9678 | 4.6378 | 4.1557 | 3.7624 | 4.5427 | 4.2636
15 | SH-14-HM | 15-SH-14-HM | 8753.7774 | 6619.9611 | 5081.0431 | 6057.9557 | 7033.1465 | 7779.717 | 6236.3633 | 5005.812 | 6013.7118 | 6525.3726 | 4.4872 | 4.0143 | 3.6321 | 4.3842 | 4.1202
15 | SH-14-MH | 15-SH-14-MH | 8409.2028 | 6250.9535 | 4872.6647 | 5850.3436 | 6702.3029 | 7361.7556 | 5844.6303 | 4793.951 | 5803.4488 | 6159.703 | 3.9822 | 3.1761 | 2.9632 | 3.7644 | 3.4201
15 | SH-14-ML | 15-SH-14-ML | 8754.8927 | 6509.7063 | 4944.4774 | 5889.4504 | 6951.2838 | 7649.392 | 6090.2767 | 4864.6407 | 5842.3683 | 6383.8831 | 4.4252 | 3.9874 | 3.5897 | 4.3336 | 4.0791
15 | SH-14-MM | 15-SH-14-MM | 8531.9315 | 6363.4342 | 4994.2605 | 5917.5274 | 6817.4563 | 7572.5504 | 5990.8144 | 4922.2769 | 5874.7277 | 6320.2708 | 4.2645 | 3.4018 | 3.5635 | 4.0206 | 3.7203
15 | SH-15-HH | 15-SH-15-HH | 8341.5693 | 6208.5158 | 4728.015 | 5629.2056 | 6629.4259 | 7181.3365 | 5767.166 | 4643.2274 | 5579.4928 | 6033.1978 | 4.1396 | 3.7038 | 3.3543 | 4.0497 | 3.802
15 | SH-15-HL | 15-SH-15-HL | 8194.2948 | 6204.8693 | 4764.0395 | 5681.6047 | 6589.2264 | 7351.385 | 5873.5126 | 4699.9408 | 5643.2557 | 6150.2624 | 4.2958 | 3.8414 | 3.4752 | 4.1921 | 3.9432
15 | SH-15-HM | 15-SH-15-HM | 8068.0819 | 6012.7718 | 4619.3464 | 5507.1547 | 6425.4384 | 7197.5804 | 5669.3769 | 4552.1851 | 5466.9304 | 5971.3426 | 4.6839 | 3.7724 | 3.4108 | 4.1012 | 4.0164
15 | SH-15-MH | 15-SH-15-MH | 8428.6737 | 6220.2455 | 4840.074 | 5729.4142 | 6683.2195 | 7400.3423 | 5828.1895 | 4765.696 | 5685.5971 | 6154.4592 | 4.2213 | 3.3575 | 3.4424 | 3.9066 | 3.6621
15 | SH-15-ML | 15-SH-15-ML | 8162.5653 | 6086.9731 | 4633.4231 | 5519.6134 | 6494.4719 | 7199.3047 | 5716.9981 | 4562.8028 | 5477.9397 | 5997.6443 | 4.26 | 3.8266 | 3.4323 | 4.138 | 3.916
15 | SH-15-MM | 15-SH-15-MM | 8179.959 | 6038.999 | 4602.9678 | 5479.7786 | 6469.8124 | 7170.0544 | 5645.0927 | 4526.4741 | 5434.5825 | 5945.502 | 4.5087 | 3.6363 | 3.3032 | 3.9954 | 3.8736
15 | SH-16-CH | 15-SH-16-CH | 9166.2595 | 6677.5755 | 5019.3078 | 5948.8732 | 7176.7359 | 8071.5461 | 6266.3313 | 4943.1081 | 5903.6379 | 6617.3934 | 4.2314 | 3.3603 | 3.4657 | 3.9176 | 3.6705
15 | SH-16-CL | 15-SH-16-CL | 9343.0904 | 6889.9194 | 5269.899 | 6249.8311 | 7387.3627 | 8330.3755 | 6507.9915 | 5199.5646 | 6208.1589 | 6869.2066 | 4.2361 | 3.3694 | 3.4857 | 3.9303 | 3.68
15 | SH-16-LH | 15-SH-16-LH | 8696.3588 | 6312.8276 | 4741.862 | 5692.1179 | 6796.6552 | 7538.9638 | 5877.3958 | 4660.005 | 5643.0179 | 6204.7215 | 4.1826 | 3.3043 | 3.0292 | 3.8526 | 3.5599
15 | SH-16-LL | 15-SH-16-LL | 8726.0401 | 6549.2254 | 4865.306 | 5817.6384 | 6947.2476 | 7659.9467 | 6156.4687 | 4792.8751 | 5774.4029 | 6406.6813 | 3.8728 | 3.4285 | 3.1377 | 3.9872 | 3.5469
15 | SH-16-LM | 15-SH-16-LM | 8739.317 | 6546.6496 | 4874.171 | 5791.0706 | 6950.3192 | 7567.6664 | 6111.6524 | 4793.3358 | 5742.9769 | 6354.3521 | 3.8288 | 3.3903 | 3.0112 | 3.5306 | 3.4764
15 | SH-16-TH | 15-SH-16-TH | 9501.8025 | 6969.2256 | 5024.1314 | 6002.6451 | 7429.6023 | 8099.8181 | 6442.2605 | 4927.3624 | 5945.0672 | 6713.2517 | 4.5449 | 4.0996 | 3.7114 | 4.5183 | 4.198
15 | SH-16-TL | 15-SH-16-TL | 10273.1913 | 7404.1544 | 5480.4993 | 6488.7643 | 7974.7086 | 8880.3528 | 6892.1002 | 5389.1478 | 6433.8766 | 7269.5555 | 4.7434 | 3.767 | 3.9027 | 4.4082 | 4.1181
15 | SH-16-TM | 15-SH-16-TM | 10146.6953 | 7304.0204 | 5423.2362 | 6413.5311 | 7873.7582 | 8732.6613 | 6783.7027 | 5330.2985 | 6357.694 | 7157.6058 | 4.6521 | 3.6948 | 3.8227 | 4.3175 | 4.038
15 | SH-17-CM | 15-SH-17-CM | 9035.8539 | 6591.6963 | 5015.7939 | 5943.467 | 7092.5477 | 7908.7567 | 6180.4003 | 4943.2076 | 5900.9018 | 6523.7329 | 4.0505 | 3.2227 | 3.3302 | 3.7555 | 3.5188
15 | SH-17-LM | 15-SH-17-LM | 8708.6008 | 6420.1748 | 4903.1116 | 5904.8744 | 6886.7322 | 7687.9406 | 6038.131 | 4832.3125 | 5862.4404 | 6365.9412 | 4.1499 | 3.279 | 3.0145 | 3.8238 | 3.5337
15 | SH-17-TH | 15-SH-17-TH | 9041.3423 | 6635.8528 | 4802.5265 | 5656.9403 | 7072.7119 | 7638.9694 | 6111.3679 | 4706.9914 | 5599.2155 | 6357.6534 | 4.2242 | 3.8103 | 3.4692 | 3.918 | 3.8931
15 | SH-17-TL | 15-SH-17-TL | 9157.2554 | 6709.1971 | 4834.1141 | 5701.6504 | 7151.935 | 7763.4021 | 6190.0948 | 4740.2173 | 5645.245 | 6442.5124 | 4.3181 | 3.8953 | 3.5474 | 4.0073 | 3.98
15 | SH-18-LH | 15-SH-18-LH | 8249.7732 | 6111.8322 | 4511.4203 | 5394.6875 | 6510.7425 | 7032.7055 | 5674.5366 | 4433.0594 | 5348.1212 | 5899.9047 | 3.5847 | 3.1827 | 2.9205 | 3.7094 | 3.2909
15 | SH-18-LL | 15-SH-18-LL | 8339.6414 | 6251.0678 | 4654.452 | 5526.6729 | 6634.8543 | 7265.3024 | 5859.7928 | 4583.1667 | 5484.3231 | 6092.6632 | 3.7061 | 3.2935 | 3.0268 | 3.442 | 3.3886
15 | SH-18-LM | 15-SH-18-LM | 8378.0138 | 6157.075 | 4496.3259 | 5367.6361 | 6569.897 | 7084.2621 | 5695.9814 | 4414.4956 | 5319.3304 | 5922.7107 | 3.6385 | 3.2291 | 2.9616 | 3.7625 | 3.339
15 | SH-18-TM | 15-SH-18-TM | 8714.9522 | 6455.6154 | 4733.2989 | 5671.8779 | 6871.4949 | 7297.1172 | 5933.7676 | 4638.9494 | 5614.2616 | 6153.1117 | 3.6386 | 3.2402 | 2.9855 | 3.7842 | 3.3491
16 | SA-10-HH | 16-SA-10-HH | 939.9697 | 573.3603 | 1256.8617 | 1224.5932 | 851.9299 | 939.9697 | 573.3603 | 1256.8617 | 1224.5932 | 851.9299 | 3.2188 | 2.4246 | 3.3575 | 3.3524 | 2.9643
16 | SA-10-HL | 16-SA-10-HL | 947.6509 | 578.9741 | 1258.5691 | 1225.9953 | 858.2016 | 947.6509 | 578.9741 | 1258.5691 | 1225.9953 | 858.2016 | 3.4251 | 2.5682 | 3.6354 | 3.6297 | 3.1577
16 | SA-10-HM | 16-SA-10-HM | 948.2805 | 579.7443 | 1260.4607 | 1228.5486 | 859.0337 | 948.2805 | 579.7443 | 1260.4607 | 1228.5486 | 859.0337 | 3.3589 | 2.5066 | 3.5161 | 3.509 | 3.0868
16 | SA-10-LH | 16-SA-10-LH | 931.8929 | 565.6068 | 1249.4581 | 1214.4973 | 844.0169 | 931.8929 | 565.6068 | 1249.4581 | 1214.4973 | 844.0169 | 3.2355 | 2.4323 | 3.3819 | 3.3772 | 2.9789
16 | SA-10-LL | 16-SA-10-LL | 937.7874 | 569.6315 | 1254.4041 | 1218.4751 | 849.1535 | 937.7874 | 569.6315 | 1254.4041 | 1218.4751 | 849.1535 | 3.343 | 2.504 | 3.58 | 3.572 | 3.0848
16 | SA-10-LM | 16-SA-10-LM | 930.675 | 564.0834 | 1246.6085 | 1211.6202 | 842.5029 | 930.675 | 564.0834 | 1246.6085 | 1211.6202 | 842.5029 | 3.2477 | 2.4372 | 3.383 | 3.3786 | 2.9873
16 | SA-10-MH | 16-SA-10-MH | 940.0151 | 575.8551 | 1253.5228 | 1220.0738 | 852.4014 | 940.0151 | 575.8551 | 1253.5228 | 1220.0738 | 852.4014 | 3.1609 | 2.3995 | 3.2915 | 3.2872 | 2.9166
16 | SA-10-ML | 16-SA-10-ML | 959.8222 | 583.7347 | 1281.3662 | 1248.3892 | 869.0915 | 959.8222 | 583.7347 | 1281.3662 | 1248.3892 | 869.0915 | 3.3983 | 2.5458 | 3.5915 | 3.5852 | 3.1303
16 | SA-10-MM | 16-SA-10-MM | 938.6973 | 569.4785 | 1260.3802 | 1226.8676 | 850.3192 | 938.6973 | 569.4785 | 1260.3802 | 1226.8676 | 850.3192 | 3.2419 | 2.4848 | 3.3155 | 3.3101 | 2.9924
16 | SA-13-HH | 16-SA-13-HH | 722.1741 | 442.565 | 964.2353 | 955.3622 | 655.2195 | 722.1741 | 442.565 | 964.2353 | 955.3622 | 655.2195 | 2.5841 | 1.9676 | 2.7231 | 2.8738 | 2.3917
16 | SA-13-HL | 16-SA-13-HL | 737.3092 | 444.6627 | 991.7248 | 961.1406 | 667.1567 | 737.3092 | 444.6627 | 991.7248 | 961.1406 | 667.1567 | 2.7101 | 2.0001 | 2.9021 | 2.8973 | 2.4906
16 | SA-13-HM | 16-SA-13-HM | 709.503 | 431.9282 | 941.8388 | 925.242 | 642.0262 | 709.503 | 431.9282 | 941.8388 | 925.242 | 642.0262 | 2.5779 | 1.9339 | 2.795 | 2.8786 | 2.3847
16 | SA-13-LH | 16-SA-13-LH | 712.2048 | 433.6661 | 950.4643 | 924.4775 | 645.0066 | 712.2048 | 433.6661 | 950.4643 | 924.4775 | 645.0066 | 2.4504 | 1.8344 | 2.5721 | 2.5684 | 2.2547
16 | SA-13-LL | 16-SA-13-LL | 734.2384 | 444.4496 | 989.3693 | 963.3823 | 665.1875 | 734.2384 | 444.4496 | 989.3693 | 963.3823 | 665.1875 | 2.6187 | 1.9495 | 2.7626 | 2.7576 | 2.4074
16 | SA-13-LM | 16-SA-13-LM | 747.0544 | 454.1313 | 1005.2087 | 977.9515 | 677.2784 | 747.0544 | 454.1313 | 1005.2087 | 977.9515 | 677.2784 | 2.6014 | 1.964 | 2.7313 | 2.727 | 2.3993
16 | SA-13-MH | 16-SA-13-MH | 700.298 | 429.084 | 920.3343 | 894.6635 | 633.4585 | 700.298 | 429.084 | 920.3343 | 894.6635 | 633.4585 | 2.4843 | 1.8645 | 2.6444 | 2.6403 | 2.2918
16 | SA-13-ML | 16-SA-13-ML | 727.7397 | 439.9743 | 976.6126 | 946.9317 | 658.6084 | 727.7397 | 439.9743 | 976.6126 | 946.9317 | 658.6084 | 2.6327 | 1.9448 | 2.7965 | 2.7927 | 2.4175
16 | SA-13-MM | 16-SA-13-MM | 680.7269 | 415.3673 | 891.9896 | 866.4644 | 614.8536 | 680.7269 | 415.3673 | 891.9896 | 866.4644 | 614.8536 | 2.4292 | 1.803 | 2.575 | 2.5565 | 2.2327
16 | SA-14-HH | 16-SA-14-HH | 704.9839 | 429.1 | 941.6902 | 913.0674 | 638.4832 | 704.9839 | 429.1 | 941.6902 | 913.0674 | 638.4832 | 2.5218 | 1.8734 | 2.6627 | 2.6601 | 2.3173
16 | SA-14-HL | 16-SA-14-HL | 673.0341 | 407.9318 | 895.8685 | 868.7823 | 608.5932 | 673.0341 | 407.9318 | 895.8685 | 868.7823 | 608.5932 | 2.4272 | 1.8041 | 2.6404 | 2.6269 | 2.2397
16 | SA-14-HM | 16-SA-14-HM | 706.0253 | 427.257 | 950.0374 | 921.2749 | 639.3984 | 706.0253 | 427.257 | 950.0374 | 921.2749 | 639.3984 | 2.6129 | 1.9319 | 2.7733 | 2.7694 | 2.3996
16 | SA-14-MH | 16-SA-14-MH | 706.6149 | 431.0795 | 950.4295 | 925.6457 | 641.1044 | 706.6149 | 431.0795 | 950.4295 | 925.6457 | 641.1044 | 2.4287 | 1.8452 | 2.5436 | 2.5419 | 2.2433
16 | SA-14-ML | 16-SA-14-ML | 692.426 | 418.9158 | 928.638 | 900.4938 | 626.6808 | 692.426 | 418.9158 | 928.638 | 900.4938 | 626.6808 | 2.5083 | 1.8601 | 2.6595 | 2.6555 | 2.3051
16 | SA-14-MM | 16-SA-14-MM | 690.6199 | 420.8924 | 926.7099 | 901.4526 | 626.1771 | 690.6199 | 420.8924 | 926.7099 | 901.4526 | 626.1771 | 2.4191 | 1.8333 | 2.5398 | 2.5358 | 2.2336
16 | SA-15-HH | 16-SA-15-HH | 613.7304 | 378.2503 | 812.6217 | 801.7304 | 556.727 | 613.7304 | 378.2503 | 812.6217 | 801.7304 | 556.727 | 2.2147 | 1.6807 | 2.3637 | 2.4569 | 2.051
16 | SA-15-HL | 16-SA-15-HL | 608.6096 | 371.1575 | 813.0159 | 801.471 | 551.5758 | 608.6096 | 371.1575 | 813.0159 | 801.471 | 551.5758 | 2.254 | 1.6773 | 2.4002 | 2.4615 | 2.0752
16 | SA-15-HM | 16-SA-15-HM | 620.0425 | 378.3369 | 822.5435 | 810.0399 | 561.3259 | 620.0425 | 378.3369 | 822.5435 | 810.0399 | 561.3259 | 2.2233 | 1.664 | 2.3921 | 2.4713 | 2.0532
16 | SA-15-MH | 16-SA-15-MH | 655.2167 | 400.3349 | 874.6792 | 848.5816 | 593.8729 | 655.2167 | 400.3349 | 874.6792 | 848.5816 | 593.8729 | 2.3576 | 1.7652 | 2.5057 | 2.5024 | 2.1731
16 | SA-15-ML | 16-SA-15-ML | 636.0672 | 385.1961 | 855.2681 | 829.7695 | 576.0654 | 636.0672 | 385.1961 | 855.2681 | 829.7695 | 576.0654 | 2.303 | 1.7072 | 2.4503 | 2.4451 | 2.1172
16 | SA-15-MM | 16-SA-15-MM | 640.0751 | 387.4086 | 858.1497 | 831.8516 | 579.3214 | 640.0751 | 387.4086 | 858.1497 | 831.8516 | 579.3214 | 2.3268 | 1.7243 | 2.4765 | 2.4724 | 2.139
16 | SA-16-CH | 16-SA-16-CH | 765.6214 | 462.218 | 930.5788 | 904.5223 | 681.3348 | 765.6214 | 462.218 | 930.5788 | 904.5223 | 681.3348 | 2.6454 | 1.9546 | 2.5293 | 2.5293 | 2.3963
16 | SA-16-CL | 16-SA-16-CL | 730.8245 | 441.4281 | 885.0667 | 864.5022 | 650.1055 | 730.8245 | 441.4281 | 885.0667 | 864.5022 | 650.1055 | 2.569 | 1.8456 | 2.4348 | 2.5181 | 2.3074
16 | SA-16-CM | 16-SA-16-CM | 749.6221 | 453.1301 | 907.2213 | 888.8457 | 666.8996 | 749.6221 | 453.1301 | 907.2213 | 888.8457 | 666.8996 | 2.6087 | 1.8953 | 2.432 | 2.5379 | 2.3458
16 | SA-16-LH | 16-SA-16-LH | 652.2258 | 403.714 | 810.5784 | 788.1563 | 585.9084 | 652.2258 | 403.714 | 810.5784 | 788.1563 | 585.9084 | 2.1896 | 1.5761 | 2.2611 | 2.2597 | 1.9889
16 | SA-16-LL | 16-SA-16-LL | 691.0277 | 424.5718 | 860.6255 | 836.3502 | 619.8974 | 691.0277 | 424.5718 | 860.6255 | 836.3502 | 619.8974 | 2.3772 | 1.7066 | 2.4411 | 2.4401 | 2.1561
16 | SA-16-LM | 16-SA-16-LM | 694.3069 | 424.705 | 869.0815 | 844.3599 | 622.7082 | 694.3069 | 424.705 | 869.0815 | 844.3599 | 622.7082 | 2.3465 | 1.7063 | 2.413 | 2.4127 | 2.1361
16 | SA-16-NM | 16-SA-16-NM | 660.4311 | 395.0208 | 817.3572 | 793.9291 | 588.1765 | 660.4311 | 395.0208 | 817.3572 | 793.9291 | 588.1765 | 2.1927 | 1.5322 | 2.3014 | 2.2978 | 1.9803
16 | SA-16-TH | 16-SA-16-TH | 788.6552 | 491.3218 | 920.6558 | 897.3217 | 702.5914 | 788.6552 | 491.3218 | 920.6558 | 897.3217 | 702.5914 | 2.6653 | 1.9693 | 2.6707 | 2.6688 | 2.4287
16 | SA-16-TL | 16-SA-16-TL | 709.4147 | 432.1764 | 824.885 | 808.5733 | 628.325 | 709.4147 | 432.1764 | 824.885 | 808.5733 | 628.325 | 2.438 | 1.7433 | 2.4983 | 2.4527 | 2.2079
16 | SA-17-CH | 16-SA-17-CH | 705.6074 | 426.0171 | 864.1807 | 843.3872 | 628.7377 | 705.6074 | 426.0171 | 864.1807 | 843.3872 | 628.7377 | 2.4808 | 1.8163 | 2.4 | 2.4798 | 2.2456
16 | SA-17-CL | 16-SA-17-CL | 708.9094 | 426.4947 | 866.7663 | 844.0823 | 630.9749 | 708.9094 | 426.4947 | 866.7663 | 844.0823 | 630.9749 | 2.5123 | 1.8215 | 2.4409 | 2.5095 | 2.2691
16 | SA-17-CM | 16-SA-17-CM | 715.4217 | 430.5052 | 867.3351 | 845.4532 | 635.9437 | 715.4217 | 430.5052 | 867.3351 | 845.4532 | 635.9437 | 2.5104 | 1.833 | 2.4282 | 2.5025 | 2.2705
16 | SA-17-LH | 16-SA-17-LH | 636.5686 | 392.6928 | 794.8832 | 773.8235 | 571.8399 | 636.5686 | 392.6928 | 794.8832 | 773.8235 | 571.8399 | 2.1801 | 1.5726 | 2.2362 | 2.2338 | 1.9796
16 | SA-17-LL | 16-SA-17-LL | 663.2736 | 406.1743 | 824.7656 | 801.3038 | 594.388 | 663.2736 | 406.1743 | 824.7656 | 801.3038 | 594.388 | 2.2948 | 1.6553 | 2.3506 | 2.3497 | 2.0833
16 | SA-17-LM | 16-SA-17-LM | 671.2841 | 410.8871 | 836.5503 | 813.615 | 601.7228 | 671.2841 | 410.8871 | 836.5503 | 813.615 | 601.7228 | 2.2827 | 1.6532 | 2.3466 | 2.3445 | 2.0756
16 | SA-17-TH | 16-SA-17-TH | 658.8145 | 414.5147 | 788.2494 | 767.9601 | 590.5555 | 658.8145 | 414.5147 | 788.2494 | 767.9601 | 590.5555 | 2.2585 | 1.6826 | 2.2795 | 2.2773 | 2.0646
16 | SA-17-TL | 16-SA-17-TL | 596.9243 | 366.0376 | 714.264 | 694.1591 | 531.8182 | 596.9243 | 366.0376 | 714.264 | 694.1591 | 531.8182 | 2.2041 | 1.5451 | 2.2596 | 2.2536 | 1.9859
16 | SA-17-TM | 16-SA-17-TM | 708.7108 | 434.0143 | 801.187 | 790.5746 | 625.8399 | 708.7108 | 434.0143 | 801.187 | 790.5746 | 625.8399 | 2.3687 | 1.7566 | 2.3066 | 2.3443 | 2.1531
16 | SA-18-LH | 16-SA-18-LH | 620.4157 | 381.6407 | 770.3532 | 748.7772 | 556.4366 | 620.4157 | 381.6407 | 770.3532 | 748.7772 | 556.4366 | 2.1092 | 1.5234 | 2.1726 | 2.1713 | 1.917
16 | SA-18-LL | 16-SA-18-LL | 600.6454 | 367.2849 | 751.5628 | 729.9543 | 538.6268 | 600.6454 | 367.2849 | 751.5628 | 729.9543 | 538.6268 | 2.1019 | 1.5096 | 2.1731 | 2.1716 | 1.9084
16 | SA-18-TH | 16-SA-18-TH | 638.504 | 402.2572 | 752.7876 | 734.2255 | 571.2263 | 638.504 | 402.2572 | 752.7876 | 734.2255 | 571.2263 | 2.1416 | 1.5889 | 2.1387 | 2.1351 | 1.9528
16 | SA-18-TL | 16-SA-18-TL | 671.397 | 416.4223 | 785.7686 | 765.8131 | 597.7328 | 671.397 | 416.4223 | 785.7686 | 765.8131 | 597.7328 | 2.3688 | 1.7762 | 2.3117 | 2.306 | 2.1601
16 | SA-18-TM | 16-SA-18-TM | 663.9509 | 414.5625 | 799.5076 | 777.8334 | 594.6636 | 663.9509 | 414.5625 | 799.5076 | 777.8334 | 594.6636 | 2.2354 | 1.651 | 2.2533 | 2.2508 | 2.0383
16 | SH-10-HH | 16-SH-10-HH | 16022.6376 | 9009.5491 | 9458.1287 | 8636.7383 | 12321.7314 | 914.8272 | 560.8159 | 1215.5204 | 1206.326 | 798.8932 | 3.148 | 2.3675 | 3.3382 | 3.4657 | 2.8411
16 | SH-10-HL | 16-SH-10-HL | 15748.9553 | 8884.3823 | 9455.8639 | 8747.2686 | 12142.1498 | 941.0499 | 574.1137 | 1249.4425 | 1214.9474 | 820.2696 | 3.3048 | 2.466 | 3.4986 | 3.495 | 2.9724
16 | SH-10-HM | 16-SH-10-HM | 15431.8787 | 8745.7938 | 9444.0088 | 8741.5789 | 11934.5408 | 933.1498 | 568.2461 | 1239.5005 | 1207.7308 | 813.0263 | 3.2329 | 2.4123 | 3.3853 | 3.3809 | 2.9036
16 | SH-10-LH | 16-SH-10-LH | 16763.926 | 9456.5674 | 9873.9097 | 9103.8537 | 12902.9913 | 927.3658 | 567.7254 | 1239.7451 | 1208.0567 | 810.1376 | 3.0992 | 2.3536 | 3.2336 | 3.229 | 2.7994
16 | SH-10-LL | 16-SH-10-LL | 17262.9889 | 9756.1052 | 10128.4773 | 9347.9896 | 13290.445 | 929.084 | 563.3753 | 1234.6336 | 1202.4058 | 808.5268 | 3.2165 | 2.3975 | 3.4056 | 3.4026 | 2.8919
16 | SH-10-LM | 16-SH-10-LM | 16485.5193 | 9357.7837 | 9812.5986 | 9063.5698 | 12724.8401 | 914.2293 | 557.9255 | 1208.9247 | 1175.5173 | 796.418 | 3.0828 | 2.321 | 3.2736 | 3.2702 | 2.7826
16 | SH-10-MH | 16-SH-10-MH | 16949.084 | 9560.412 | 9932.2781 | 9165.3151 | 13039.7066 | 924.5174 | 563.5157 | 1235.183 | 1201.9985 | 806.5085 | 3.1756 | 2.3925 | 3.3136 | 3.3081 | 2.8605
16 | SH-10-ML | 16-SH-10-ML | 16656.1884 | 9510.4951 | 9961.2465 | 9205.9398 | 12885.4094 | 934.868 | 566.1556 | 1239.7531 | 1203.8303 | 812.9323 | 3.3205 | 2.4683 | 3.5425 | 3.5377 | 2.9856
16 | SH-10-MM | 16-SH-10-MM | 15997.8252 | 9026.4498 | 9575.506 | 8845.7529 | 12331.3067 | 937.879 | 569.9492 | 1251.5929 | 1220.4832 | 817.3069 | 3.2509 | 2.4508 | 3.3596 | 3.3592 | 2.9254
16 | SH-13-HH | 16-SH-13-HH | 16251.3908 | 9101.0347 | 9427.5513 | 8651.5536 | 12464.0487 | 736.6711 | 453.9841 | 974.0664 | 946.5664 | 643.5917 | 2.6025 | 1.9693 | 2.7917 | 2.7862 | 2.3563
16 | SH-13-HL | 16-SH-13-HL | 14410.5773 | 8046.9426 | 8376.9659 | 7482.5199 | 11042.3208 | 708.7217 | 429.8304 | 947.5653 | 929.0666 | 617.4953 | 2.6382 | 1.9643 | 2.7786 | 2.8762 | 2.3704
16 | SH-13-HM | 16-SH-13-HM | 14857.873 | 8185.594 | 8556.1385 | 7857.9441 | 11331.3643 | 721.9376 | 442.7174 | 957.418 | 929.3504 | 630.102 | 2.5539 | 1.9211 | 2.7479 | 2.7391 | 2.3084
16 | SH-13-LH | 16-SH-13-LH | 18268.4401 | 10218.2909 | 10049.542 | 9198.6473 | 13944.8504 | 729.3994 | 445.0723 | 975.7295 | 949.7094 | 636.64 | 2.5209 | 1.902 | 2.6465 | 2.6414 | 2.2737
16 | SH-13-LL | 16-SH-13-LL | 15588.5214 | 8497.7802 | 8672.7326 | 7937.177 | 11816.4759 | 678.3347 | 414.605 | 890.7232 | 865.1839 | 590.4841 | 2.4231 | 1.8196 | 2.5899 | 2.5862 | 2.187
16 | SH-13-LM | 16-SH-13-LM | 13091.282 | 6998.8024 | 7388.1654 | 6799.0898 | 9877.3913 | 756.3495 | 459.1836 | 1017.7581 | 990.8059 | 659.8455 | 2.6581 | 2.0038 | 2.7973 | 2.7927 | 2.3974
16 | SH-13-MH | 16-SH-13-MH | 16496.2594 | 9148.5163 | 9333.2206 | 8327.9687 | 12585.4685 | 690.7162 | 427.0307 | 918.158 | 908.8124 | 604.7253 | 2.4419 | 1.8527 | 2.5324 | 2.6593 | 2.2046
16 | SH-13-ML | 16-SH-13-ML | 15857.2434 | 8618.7135 | 8838.4901 | 8105.501 | 12011.3535 | 759.6213 | 459.199 | 1027.9397 | 999.5493 | 662.5001 | 2.7714 | 2.0695 | 2.94 | 2.9348 | 2.4939
16 | SH-13-MM | 16-SH-13-MM | 14940.735 | 8298.0213 | 8756.229 | 8047.6461 | 11439.6888 | 716.6917 | 436.4441 | 951.0255 | 923.5593 | 624.3005 | 2.5792 | 1.919 | 2.7513 | 2.7424 | 2.3197
16 | SH-14-HH | 16-SH-14-HH | 15365.3469 | 8483.8359 | 8815.3466 | 8079.6262 | 11722.4427 | 693.3351 | 425.9042 | 917.7998 | 891.2046 | 605.2601 | 2.4856 | 1.8743 | 2.6773 | 2.6713 | 2.2489
16 | SH-14-HL | 16-SH-14-HL | 15830.6444 | 8650.4688 | 8869.4827 | 7822.7563 | 12012.7024 | 673.9682 | 410.1761 | 896.5501 | 881.6876 | 587.3351 | 2.4618 | 1.8377 | 2.6673 | 2.7261 | 2.2219
16 | SH-14-HM | 16-SH-14-HM | 15719.4134 | 8653.2453 | 8868.0845 | 8127.3893 | 11964.8844 | 677.7943 | 415.3229 | 896.8732 | 870.317 | 591.2116 | 2.4063 | 1.8138 | 2.5905 | 2.585 | 2.1768
16 | SH-14-MH | 16-SH-14-MH | 17293.08 | 9622.6946 | 9535.1616 | 8728.9322 | 13181.6776 | 679.8245 | 414.5546 | 909.8514 | 885.2655 | 593.3024 | 2.3439 | 1.764 | 2.462 | 2.4575 | 2.1123
16 | SH-14-ML | 16-SH-14-ML | 18323.7433 | 10057.091 | 9673.2049 | 8838.7914 | 13860.7528 | 667.544 | 403.7865 | 891.4195 | 864.0272 | 580.9457 | 2.4169 | 1.7831 | 2.5589 | 2.5526 | 2.1652
16 | SH-14-MM | 16-SH-14-MM | 15677.8423 | 8503.4489 | 8647.3669 | 7913.8106 | 11857.7073 | 676.3509 | 409.3387 | 907.5556 | 881.2899 | 589.2083 | 2.4167 | 1.7947 | 2.5692 | 2.5662 | 2.1712
16 | SH-15-HH | 16-SH-15-HH | 18023.3481 | 10155.0466 | 9975.0358 | 8711.6155 | 13791.4624 | 625.5544 | 385.5338 | 829.883 | 820.2281 | 546.968 | 2.2174 | 1.6805 | 2.3935 | 2.4829 | 2.0113
16 | SH-15-HL | 16-SH-15-HL | 13645.7895 | 7309.3152 | 7644.535 | 6779.032 | 10292.8954 | 629.3065 | 383.6472 | 836.2636 | 823.0498 | 548.5984 | 2.2716 | 1.7026 | 2.4716 | 2.5313 | 2.0543
16 | SH-15-HM | 16-SH-15-HM | 14316.1663 | 7706.5741 | 8073.8699 | 7118.1179 | 10820.1971 | 614.8561 | 375.7529 | 824.9773 | 813.0775 | 537.2813 | 2.248 | 1.6761 | 2.3356 | 2.4127 | 2.0171
16 | SH-15-MH | 16-SH-15-MH | 16752.2188 | 8978.2718 | 8763.39 | 7996.615 | 12571.7202 | 645.4469 | 392.3304 | 864.8516 | 839.04 | 562.8562 | 2.3581 | 1.7516 | 2.5119 | 2.5074 | 2.1193
16 | SH-15-ML | 16-SH-15-ML | 16588.279 | 8879.8631 | 8652.4858 | 7901.7213 | 12441.5177 | 621.7368 | 375.4711 | 830.3022 | 804.7804 | 540.8303 | 2.2585 | 1.6642 | 2.4089 | 2.3969 | 2.0243
16 | SH-15-MM | 16-SH-15-MM | 16656.189 | 9244.6726 | 9286.507 | 8174.0004 | 12694.3495 | 607.1757 | 371.4832 | 812.4288 | 799.7888 | 530.4896 | 2.2338 | 1.6696 | 2.3512 | 2.4221 | 2.0095
16 | SH-16-CH | 16-SH-16-CH | 17149.0141 | 10009.8793 | 9587.453 | 8548.3415 | 13281.4408 | 745.8301 | 453.6229 | 902.4941 | 884.6812 | 639.816 | 2.5593 | 1.873 | 2.4777 | 2.5673 | 2.2614
16 | SH-16-CL | 16-SH-16-CL | 16318.4001 | 9417.2842 | 9098.9523 | 8083.8596 | 12589.7152 | 740.068 | 447.479 | 897.6836 | 876.1878 | 633.9625 | 2.6047 | 1.913 | 2.5076 | 2.5971 | 2.3028
16 | SH-16-LH | 16-SH-16-LH | 17409.6528 | 9924.4158 | 9279.5179 | 8495.9816 | 13335.0641 | 661.1358 | 412.5701 | 823.1443 | 804.1653 | 574.1259 | 2.1768 | 1.5938 | 2.2525 | 2.2424 | 1.9391
16 | SH-16-LL | 16-SH-16-LL | 16904.2447 | 9496.2774 | 8904.3603 | 8152.1201 | 12877.1194 | 691.6875 | 422.8001 | 868.1443 | 843.4968 | 597.6575 | 2.3895 | 1.7257 | 2.4518 | 2.451 | 2.1163
16 | SH-16-LM | 16-SH-16-LM | 17824.7062 | 10153.7585 | 9469.3697 | 8664.3547 | 13646.3831 | 693.5649 | 430.6906 | 863.7641 | 841.1811 | 601.3946 | 2.3201 | 1.6863 | 2.3772 | 2.3745 | 2.059
16 | SH-16-TH | 16-SH-16-TH | 20099.0102 | 12176.8589 | 11221.1226 | 10195.6884 | 15754.1431 | 693.3305 | 434.6877 | 810.5645 | 805.8515 | 597.2104 | 2.3923 | 1.7263 | 2.3897 | 2.4386 | 2.1114
16 | SH-16-TL | 16-SH-16-TL | 19629.7471 | 11803.1857 | 11037.5274 | 10168.0191 | 15358.6618 | 774.9265 | 472.4407 | 914.3331 | 889.8672 | 662.5817 | 2.7342 | 2.0389 | 2.7106 | 2.7086 | 2.4381
16 | SH-16-TM | 16-SH-16-TM | 19677.0358 | 11852.5972 | 11081.8587 | 10209.9006 | 15406.4919 | 761.7302 | 465.3197 | 898.7974 | 874.9779 | 651.6948 | 2.6753 | 1.9955 | 2.6382 | 2.6353 | 2.3842
16 | SH-17-CM | 16-SH-17-CM | 16246.2104 | 9209.7769 | 8661.8094 | 7648.3936 | 12419.6876 | 698.1241 | 422.1536 | 847.3709 | 827.12 | 598.1105 | 2.4624 | 1.8085 | 2.3686 | 2.4573 | 2.1768
16 | SH-17-LM | 16-SH-17-LM | 16370.2845 | 9139.6048 | 8565.9783 | 7844.9281 | 12440.1276 | 667.8752 | 411.6715 | 828.2809 | 809.5155 | 577.4648 | 2.2631 | 1.667 | 2.3087 | 2.2995 | 2.0165
16 | SH-17-TH | 16-SH-17-TH | 19989.3644 | 12120.3803 | 11182.5911 | 10308.0097 | 15676.3714 | 653.6741 | 408.0341 | 777.7609 | 757.5104 | 563.6528 | 2.2741 | 1.6624 | 2.2888 | 2.2847 | 2.0175
16 | SH-17-TL | 16-SH-17-TL | 20047.1395 | 12134.7464 | 11158.2812 | 10284.9917 | 15706.6745 | 660.2676 | 411.0384 | 784.0956 | 763.2742 | 568.6969 | 2.3237 | 1.6877 | 2.3317 | 2.3269 | 2.0561
16 | SH-18-LH | 16-SH-18-LH | 18488.0438 | 10718.8952 | 9789.3204 | 8954.9212 | 14229.6478 | 616.5971 | 378.0353 | 772.6889 | 751.0869 | 533.1228 | 2.1581 | 1.5739 | 2.2138 | 2.2095 | 1.9177
16 | SH-18-LL | 16-SH-18-LL | 17159.9798 | 9658.9425 | 8973.8523 | 8201.1204 | 13072.5787 | 644.0984 | 394.3312 | 812.2684 | 788.9849 | 557.2265 | 2.2577 | 1.6434 | 2.3178 | 2.3131 | 2.0051
16 | SH-18-LM | 16-SH-18-LM | 19268.7818 | 11273.7996 | 10235.4207 | 9366.7697 | 14877.3734 | 620.5244 | 381.1448 | 771.4855 | 750.2358 | 536.1357 | 2.1681 | 1.5648 | 2.2214 | 2.2198 | 1.9194
16 | SH-18-TM | 16-SH-18-TM | 20269.706 | 12300.6313 | 11240.6665 | 10362.2882 | 15889.6181 | 642.9518 | 405.0332 | 778.171 | 758.2356 | 557.4353 | 2.3394 | 1.8163 | 2.3169 | 2.3155 | 2.1161

## Key
SEER Conversion from ACM:
[9 empty] | Design Day Values | [24 empty] | SEER
[5 empty] | Cooling Season Boundaries: |  |  |  | CDD |  |  | HDD | [20 empty] | CZ index | 10 | 13 | 14 | 15 | 16 | 17 | 18
All Climate Zones Information |  |  | 1=temp,2=mod,3=hot |  | HtEndMon | HtEndDay | ClEndMon | ClEndDay | Temp Hi | Range | WB at Hi | Temp Lo | CoilWB |  |  |  |  | Unit Map |  |  |  | SEER Level | [10 empty] | w01 | 10 | 13 | 14 | 15 | 16 | 17 | 18
1 | w01 | CZ01.bin | 1 | 1 | APR | 15 | SEP | 30 | 72 | 14.8 | 67 | 35 | 60 | Arcata | North Coast |  |  |  | 10 | 13 | 14 | 15 | 16 | 17 | 18 | [7 empty] | w02 | 9.71 | 12.25 | 12.96 | 13.65 | 14.34 | 15 | 15.66
2 | w02 | CZ02.bin | 2 | 2 | APR | 15 | SEP | 30 | 96 | 32.3 | 67 | 30 | 60 | Santa Rosa | North Coast |  |  |  | 9 | 9 | 6 | 6 | 9 | 9 | 2 | [7 empty] | w03 | 9.75 | 12.37 | 13.13 | 13.89 | 14.63 | 15.36 | 16.08
3 | w03 | CZ03.bin | 1 | 3 | APR | 15 | SEP | 30 | 83 | 19.6 | 69 | 36 | 60 | Oakland | North Coast |  |  | AC | SA-10-LL | SA-13-LL | SA-14-ML | SA-15-ML | SA-16-CL | SA-17-CL | SA-18-LL | SA-10-LL (8.87) | SA-13-LL (11.36) | SA-14-ML (12.15) | SA-15-ML (12.72) | SA-16-CL (11.74) | SA-17-CL (12.40) | SA-18-LL (12.97) | w04 | 9.75 | 12.37 | 13.13 | 13.89 | 14.63 | 15.36 | 16.08
4 | w04 | CZ04.bin | 1 | 4 | APR | 15 | SEP | 30 | 89 | 28.6 | 74 | 33 | 60 | Sunnyvale | North Coast |  |  | AC | SA-10-LM | SA-13-LM | SA-14-MM | SA-15-MM | SA-16-CM | SA-17-CM | SA-18-LH | SA-10-LM (9.29) | SA-13-LM (12.04) | SA-14-MM (13.08) | SA-15-MM (12.99) | SA-16-CM (11.86) | SA-17-CM (12.47) | SA-18-LH (13.22) | w05 | 9.91 | 12.78 | 13.7 | 14.61 | 15.53 | 16.44 | 17.34
5 | w05 | CZ05.bin | 1 | 5 | APR | 15 | SEP | 30 | 83 | 22.7 | 69 | 34 | 60 | Santa Maria | North Coast |  |  | AC | SA-10-LH | SA-13-LH | SA-14-MH | SA-15-MH | SA-16-CH | SA-17-CH | SA-18-TL | SA-10-LH (9.51) | SA-13-LH (12.50) | SA-14-MH (13.22) | SA-15-MH (13.11) | SA-16-CH (12.08) | SA-17-CH (12.68) | SA-18-TL (12.73) | w06 | 9.98 | 12.94 | 13.92 | 14.9 | 15.88 | 16.85 | 17.83
6 | w06 | CZ06.bin | 1 | 6 | APR | 15 | SEP | 30 | 82 | 15.1 | 70 | 40 | 60 | Los Angeles | South Coast |  |  | AC | SA-10-ML | SA-13-ML | SA-14-HL | SA-15-HL | SA-16-LL | SA-17-LL | SA-18-TM | SA-10-ML (8.77) | SA-13-ML (11.09) | SA-14-HL (11.70) | SA-15-HL (12.39) | SA-16-LL (11.61) | SA-17-LL (12.28) | SA-18-TM (13.37) | w07 | 9.93 | 12.83 | 13.77 | 14.71 | 15.65 | 16.58 | 17.52
7 | w07 | CZ07.bin | 1 | 7 | APR | 15 | SEP | 30 | 84 | 15.9 | 75 | 39 | 60 | San Diego | South Coast |  |  | AC | SA-10-MM | SA-13-MM | SA-14-HM | SA-15-HM | SA-16-LM | SA-17-LM | SA-18-TH | SA-10-MM (9.08) | SA-13-MM (11.30) | SA-14-HM (11.84) | SA-15-HM (13.01) | SA-16-LM (12.17) | SA-17-LM (12.47) | SA-18-TH (13.75) | w08 | 9.62 | 12.05 | 12.7 | 13.34 | 13.97 | 14.6 | 15.21
8 | w08 | CZ08.bin | 1 | 8 | APR | 15 | SEP | 30 | 92 | 21.5 | 73 | 38 | 60 | El Toro | South Coast |  |  | AC | SA-10-MH | SA-13-MH | SA-14-HH | SA-15-HH | SA-16-LH | SA-17-LH | na | SA-10-MH (9.83) | SA-13-MH (11.72) | SA-14-HH (12.17) | SA-15-HH (12.85) | SA-16-LH (12.23) | SA-17-LH (12.67) | na | w09 | 9.41 | 11.53 | 12 | 12.45 | 12.89 | 13.31 | 13.72
9 | w09 | CZ09.bin | 2 | 9 | APR | 15 | SEP | 30 | 97 | 27.2 | 75 | 39 | 57 | Pasadena | South Inland |  |  | AC | SA-10-HL | SA-13-HL | na | na | SA-16-NM | SA-17-TL | na | SA-10-HL (8.46) | SA-13-HL (10.74) | na | na | SA-16-NM (12.42) | SA-17-TL (11.41) | na | w10 | 9.23 | 11.11 | 11.44 | 11.76 | 12.07 | 12.36 | 12.64
10 | w10 | CZ10.bin | 2 | 10 | APR | 15 | SEP | 30 | 100 | 31 | 71 | 34 | 57 | Riverside | South Inland |  |  | AC | SA-10-HM | SA-13-HM | na | na | SA-16-TL | SA-17-TM | na | SA-10-HM (8.79) | SA-13-HM (10.98) | na | na | SA-16-TL (11.15) | SA-17-TM (12.16) | na | w11 | 9.16 | 10.94 | 11.22 | 11.48 | 11.74 | 11.99 | 12.22
11 | w11 | CZ11.bin | 3 | 11 | APR | 15 | SEP | 30 | 101 | 32.7 | 69 | 30 | 57 | Red Bluff | Central Valley |  |  | AC | SA-10-HH | SA-13-HH | na | na | SA-16-TH | SA-17-TH | na | SA-10-HH (9.17) | SA-13-HH (11.35) | na | na | SA-16-TH (11.33) | SA-17-TH (12.95) | na | w12 | 9.22 | 11.08 | 11.41 | 11.72 | 12.01 | 12.29 | 12.56
12 | w12 | CZ12.bin | 2 | 12 | APR | 15 | SEP | 30 | 100 | 33.2 | 71 | 31 | 57 | Sacramento | Central Valley | [17 empty] | w13 | 9.11 | 10.83 | 11.08 | 11.31 | 11.53 | 11.74 | 11.95
13 | w13 | CZ13.bin | 2 | 13 | APR | 15 | SEP | 30 | 103 | 30.7 | 74 | 32 | 57 | Fresno | Central Valley |  |  |  | 9 | 9 | 6 | 6 | 8 | 4 | 2 | [7 empty] | w14 | 8.85 | 10.24 | 10.31 | 10.38 | 10.45 | 10.51 | 10.58
14 | w14 | CZ14.bin | 3 | 14 | APR | 15 | SEP | 30 | 102 | 33.4 | 64 | 24 | 54 | China Lake | Desert |  |  | HP | SH-10-LL | SH-13-LL | SH-14-ML | SH-15-ML | SH-16-CL | SH-17-CM | SH-18-LL | SH-10-LL (9.12) | SH-13-LL (11.53) | SH-14-ML (12.05) | SH-15-ML (12.70) | SH-16-CL (11.99) | SH-17-CM (12.62) | SH-18-LL (12.80) | w15 | 8.87 | 10.26 | 10.34 | 10.41 | 10.48 | 10.54 | 10.61
15 | w15 | CZ15.bin | 3 | 15 | APR | 15 | SEP | 30 | 112 | 31.3 | 75 | 35 | 54 | El Centro | Desert |  |  | HP | SH-10-LM | SH-13-LM | SH-14-MM | SH-15-MM | SH-16-CH | SH-17-LM | SH-18-LM | SH-10-LM (9.52) | SH-13-LM (11.84) | SH-14-MM (12.55) | SH-15-MM (12.63) | SH-16-CH (12.07) | SH-17-LM (12.75) | SH-18-LM (12.88) | w16 | 9.7 | 12.24 | 12.97 | 13.68 | 14.39 | 15.09 | 15.79
16 | w16 | CZ16.bin | 1 | 16 | APR | 15 | SEP | 30 | 91 | 35.2 | 68 | 17 | 60 | Mount Shasta | North Coast |  |  | HP | SH-10-LH | SH-13-LH | SH-14-MH | SH-15-MH | SH-16-LL | SH-17-TL | SH-18-LH | SH-10-LH (10.01) | SH-13-LH (12.50) | SH-14-MH (13.38) | SH-15-MH (13.01) | SH-16-LL (11.77) | SH-17-TL (12.24) | SH-18-LH (13.17)
[18 empty] | HP | SH-10-ML | SH-13-ML | SH-14-HL | SH-15-HL | SH-16-LM | SH-17-TH | SH-18-TM | SH-10-ML (8.78) | SH-13-ML (11.12) | SH-14-HL (11.60) | SH-15-HL (12.58) | SH-16-LM (12.06) | SH-17-TH (12.52) | SH-18-TM (12.63) | Rated | ACM
[6 empty] | DEER 2001 Calibration data | [11 empty] | HP | SH-10-MM | SH-13-MM | SH-14-HM | SH-15-HM | SH-16-LH | na | na | SH-10-MM (9.01) | SH-13-MM (11.07) | SH-14-HM (12.19) | SH-15-HM (12.77) | SH-16-LH (12.59) | na | na | SEER | Column
| Number of Stories |  |  |  |  | Climate | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 |  |  |  | HP | SH-10-MH | SH-13-MH | SH-14-HH | SH-15-HH | SH-16-TL | na | na | SH-10-MH (9.54) | SH-13-MH (11.96) | SH-14-HH (11.77) | SH-15-HH (13.16) | SH-16-TL (11.06) | na | na | 10 | 1 |  | 10 | 1
Wth File | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 |  | Region | Cooling Calibration Factor |  |  |  | Heating Calibration Factor | [6 empty] | HP | SH-10-HL | SH-13-HL | na | na | SH-16-TM | na | na | SH-10-HL (8.94) | SH-13-HL (10.71) | na | na | SH-16-TM (11.28) | na | na | 12 | 2 |  | 12 | 2
CZ01 | 1.4844 | 1.307 | 1.7 | 1.7 |  | North Coast | 0 | 0 | 0 | 0 | 0.8 | 0.85 | 0.5 | 0.5 |  |  |  | HP | SH-10-HM | SH-13-HM | na | na | SH-16-TH | na | na | SH-10-HM (9.01) | SH-13-HM (11.20) | na | na | SH-16-TH (11.64) | na | na | 13 | 3 |  | 14 | 3
CZ02 | 1.4844 | 1.307 | 1.7 | 1.7 |  | Central Valley | 0.45 | 0.45 | 0.4 | 0.4 | 0.8 | 0.75 | 0.8 | 0.8 |  |  |  | HP | SH-10-HH | SH-13-HH | na | na | na | na | na | SH-10-HH (9.39) | SH-13-HH (11.26) | na | na | na | na | na | 14 | 3 |  | 15 | 4
CZ03 | 1.4844 | 1.307 | 1.7 | 1.7 |  | Central Valley | 0.55 | 0.6 | 0.6 | 0.6 | 0.7 | 0.75 | 0.7 | 0.7 | [18 empty] | 15 | 4
CZ04 | 1.4844 | 1.307 | 1.7 | 1.7 |  | North Coast | 0.55 | 0.6 | 0.4 | 0.4 | 0.85 | 1 | 0.75 | 0.75 | [18 empty] | 18 | 5
CZ05 | 1.4844 | 1.307 | 1.7 | 1.7 |  | North Coast | 0.45 | 0.55 | 0.4 | 0.4 | 0.9 | 1 | 0.8 | 0.8
CZ06 | 1.5494 | 1.6219 | 1.8 | 1.8 |  | South Coast | 0.45 | 0.5 | 0.4 | 0.4 | 1 | 0.95 | 0.95 | 0.95
CZ07 | 1.5494 | 1.6219 | 1.8 | 1.8 |  | South Inland | 0.55 | 0.5 | 0.4 | 0.4 | 1 | 1 | 1 | 1
CZ08 | 1.5494 | 1.6219 | 1.8 | 1.8 |  | Desert | 0.45 | 0.55 | 0.55 | 0.55 | 1 | 1 | 1 | 1 | [18 empty] | 1 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
CZ09 | 1.3259 | 1.4231 | 1.8 | 1.8 |  | South Coast | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 1 | [18 empty] | 2 | 7.79 | 8.75 | 9.71 | 10.67 | 11.52 | 12.25 | 12.96 | 13.65 | 14.34 | 15 | 15.66
CZ10 | 1.3259 | 1.4231 | 1.8 | 1.8 |  | North Coast | 0.5 | 0.55 | 0.4 | 0.4 | 0.8 | 0.85 | 0.5 | 0.5 | [18 empty] | 3 | 7.82 | 8.78 | 9.75 | 10.72 | 11.59 | 12.37 | 13.13 | 13.89 | 14.63 | 15.36 | 16.08
CZ11 | 1.2562 | 1.2296 | 1.4 | 1.4 |  | Desert | 0.5 | 0.55 | 0.4 | 0.4 | 1 | 1 | 1 | 1 | [18 empty] | 4 | 7.82 | 8.78 | 9.75 | 10.72 | 11.59 | 12.37 | 13.13 | 13.89 | 14.63 | 15.36 | 16.08
CZ12 | 1.2562 | 1.2296 | 1.4 | 1.4 | [11 empty] | NEW Adjustments based on DEER2001 and Old v New results | [16 empty] | 5 | 7.94 | 8.92 | 9.91 | 10.9 | 11.86 | 12.78 | 13.7 | 14.61 | 15.53 | 16.44 | 17.34
CZ13 | 1.2562 | 1.2296 | 1.4 | 1.4 |  |  | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 |  | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | [9 empty] | 6 | 7.98 | 8.98 | 9.98 | 10.97 | 11.96 | 12.94 | 13.92 | 14.9 | 15.88 | 16.85 | 17.83
CZ14 | 1.0811 | 1.1188 | 1.2 | 1.2 |  |  | Cooling Calibration Factor |  |  |  | Heating Calibration Factor |  |  |  |  | Cooling Calibration Factor |  |  |  | Heating Calibration Factor | [12 empty] | 7 | 7.95 | 8.94 | 9.93 | 10.92 | 11.89 | 12.83 | 13.77 | 14.71 | 15.65 | 16.58 | 17.52
CZ15 | 1.0811 | 1.1188 | 1.2 | 1.2 |  | North Coast | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 |  | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.96929 | 0.8128 | 0.47567 | 0.45729 | [9 empty] | 8 | 7.72 | 8.67 | 9.62 | 10.57 | 11.38 | 12.05 | 12.7 | 13.34 | 13.97 | 14.6 | 15.21
CZ16 | 1.4844 | 1.307 | 1.7 | 1.7 |  | South Coast | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 1 | 0.975 | 0.975 | 0.975 |  | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 1.4298 | 1.2131 | 1.0919 | 1.118 | [9 empty] | 9 | 7.57 | 8.49 | 9.41 | 10.33 | 11.04 | 11.53 | 12 | 12.45 | 12.89 | 13.31 | 13.72
[6 empty] | South Inland | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 1 | 1 | 1 | 1 |  | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 1.5645 | 1.3004 | 0.69544 | 0.61339 | [9 empty] | 10 | 7.44 | 8.33 | 9.23 | 10.13 | 10.76 | 11.11 | 11.44 | 11.76 | 12.07 | 12.36 | 12.64
[6 empty] | Central Valley | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.75 | 0.75 | 0.75 | 0.75 |  | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.90483 | 0.67698 | 0.59826 | 0.58112 | [9 empty] | 11 | 7.38 | 8.27 | 9.16 | 10.04 | 10.64 | 10.94 | 11.22 | 11.48 | 11.74 | 11.99 | 12.22
[6 empty] | Desert | 0.61506 | 0.59885 | 0.5 | 0.5 | 1 | 1 | 1 | 1 |  | 0.61506 | 0.59885 | 0.42799 | 0.42403 | 1.2943 | 1.0566 | 0.99472 | 1 | [9 empty] | 12 | 7.43 | 8.33 | 9.22 | 10.12 | 10.74 | 11.08 | 11.41 | 11.72 | 12.01 | 12.29 | 12.56
[33 empty] | 13 | 7.35 | 8.23 | 9.11 | 10 | 10.57 | 10.83 | 11.08 | 11.31 | 11.53 | 11.74 | 11.95
DEER 2001 UEC-based Calibration data (translated from forecasting CZs) | [32 empty] | 14 | 7.16 | 8.01 | 8.85 | 9.7 | 10.16 | 10.24 | 10.31 | 10.38 | 10.45 | 10.51 | 10.58
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [24 empty] | 15 | 7.17 | 8.02 | 8.87 | 9.71 | 10.18 | 10.26 | 10.34 | 10.41 | 10.48 | 10.54 | 10.61
| Cooling Calibration Factor |  |  |  | Heating Calibration Factor | [27 empty] | 16 | 7.78 | 8.74 | 9.7 | 10.65 | 11.51 | 12.24 | 12.97 | 13.68 | 14.39 | 15.09 | 15.79
Wth File | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | region
1 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
2 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
3 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
4 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
5 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
6 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 1 | 0.975 | 0.975 | 0.975 | South Coast
7 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 1 | 0.975 | 0.975 | 0.975 | South Coast
8 | 1.0198 | 0.97786 | 0.87477 | 0.88307 | 1 | 0.975 | 0.975 | 0.975 | South Coast
9 | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 1 | 1 | 1 | 1 | South Inland
10 | 0.85959 | 0.75479 | 0.58871 | 0.62877 | 1 | 1 | 1 | 1 | South Inland
11 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.75 | 0.75 | 0.75 | 0.75 | Central Valley
12 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.75 | 0.75 | 0.75 | 0.75 | Central Valley
13 | 0.65989 | 0.59986 | 0.52691 | 0.53808 | 0.75 | 0.75 | 0.75 | 0.75 | Central Valley
14 | 0.61506 | 0.59885 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | Desert
15 | 0.61506 | 0.59885 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | Desert
16 | 0.84694 | 0.98218 | 0.59942 | 0.61088 | 0.85 | 0.95 | 0.68333 | 0.68333 | North Coast
RASS-Based Calibration Factors (filtered with min=0.5, nax=2.0)
| Cooling Calibration Factor |  |  |  | Heating Calibration Factor
Wth File | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 |  | (actual RASS calibration numbers)
1 | 1 | 1 | 1 | 1 | 0.55203 | 0.55339 | 0.5428 | 0.54982 |  | 1 | 1 | 1 | 1 | 0.55203 | 0.55339 | 0.5428 | 0.54982
2 | 1.1318 | 1.3142 | 1.1158 | 1.1326 | 0.54941 | 0.55579 | 0.54717 | 0.5545 |  | 1.1318 | 1.3142 | 1.1158 | 1.1326 | 0.54941 | 0.55579 | 0.54717 | 0.5545
3 | 1.8759 | 2 | 1.68 | 1.7299 | 0.5262 | 0.53431 | 0.52944 | 0.54186 |  | 1.8759 | 2.7245 | 1.68 | 1.7299 | 0.5262 | 0.53431 | 0.52944 | 0.54186
4 | 1.279 | 1.5847 | 1.2176 | 1.2361 | 0.53002 | 0.53705 | 0.53027 | 0.54124 |  | 1.279 | 1.5847 | 1.2176 | 1.2361 | 0.53002 | 0.53705 | 0.53027 | 0.54124
5 | 1.9746 | 2 | 1.6473 | 1.6845 | 0.50881 | 0.51364 | 0.51267 | 0.53234 |  | 1.9746 | 2.9333 | 1.6473 | 1.6845 | 0.50881 | 0.51364 | 0.51267 | 0.53234
6 | 1.3536 | 1.7591 | 1.277 | 1.3106 | 0.56477 | 0.66265 | 0.78452 | 0.91184 |  | 1.3536 | 1.7591 | 1.277 | 1.3106 | 0.56477 | 0.66265 | 0.78452 | 0.91184
7 | 1.2131 | 1.4791 | 1.1802 | 1.2081 | 0.57929 | 0.73122 | 0.89723 | 1.065 |  | 1.2131 | 1.4791 | 1.1802 | 1.2081 | 0.57929 | 0.73122 | 0.89723 | 1.065
8 | 1.024 | 1.168 | 1.0122 | 1.0398 | 0.56809 | 0.66413 | 0.72883 | 0.80906 |  | 1.024 | 1.168 | 1.0122 | 1.0398 | 0.56809 | 0.66413 | 0.72883 | 0.80906
9 | 1.0644 | 1.0563 | 1.0221 | 1.0322 | 0.78922 | 0.93042 | 1.0694 | 1.217 |  | 1.0644 | 1.0563 | 1.0221 | 1.0322 | 0.78922 | 0.93042 | 1.0694 | 1.217
10 | 0.99904 | 0.99969 | 0.98249 | 0.9944 | 0.76668 | 0.85217 | 0.93362 | 1.0353 |  | 0.99904 | 0.99969 | 0.98249 | 0.9944 | 0.76668 | 0.85217 | 0.93362 | 1.0353
11 | 1.0359 | 1.0274 | 1.0659 | 1.0766 | 0.75343 | 0.76253 | 0.79082 | 0.79673 |  | 1.0359 | 1.0274 | 1.0659 | 1.0766 | 0.75343 | 0.76253 | 0.79082 | 0.79673
12 | 1.0892 | 1.0813 | 1.1367 | 1.1547 | 0.75476 | 0.76291 | 0.79121 | 0.79815 |  | 1.0892 | 1.0813 | 1.1367 | 1.1547 | 0.75476 | 0.76291 | 0.79121 | 0.79815
13 | 0.98795 | 0.98059 | 1.0054 | 1.0142 | 0.76125 | 0.77388 | 0.80518 | 0.81401 |  | 0.98795 | 0.98059 | 1.0054 | 1.0142 | 0.76125 | 0.77388 | 0.80518 | 0.81401
14 | 0.99682 | 1.0178 | 1.0396 | 1.0382 | 0.76729 | 0.78064 | 0.81016 | 0.83188 |  | 0.99682 | 1.0178 | 1.0396 | 1.0382 | 0.76729 | 0.78064 | 0.81016 | 0.83188
15 | 0.93239 | 0.93914 | 0.95304 | 0.95128 | 0.83138 | 1.1153 | 2 | 2 |  | 0.93239 | 0.93914 | 0.95304 | 0.95128 | 0.83138 | 1.1153 | 2.1173 | 3.2958
16 | 1.2041 | 1.4412 | 1.1813 | 1.2031 | 0.56846 | 0.58946 | 0.56483 | 0.58457 |  | 1.2041 | 1.4412 | 1.1813 | 1.2031 | 0.56846 | 0.58946 | 0.56483 | 0.58457
| based on a constant cooling setpoint of 78 |  |  |  | based on a constant heating setpoint of 68
| Cooling Weights |  |  |  | Heating Weights
Wth File | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998 | Pre-1978 | 1978-1992 | 1992-1998 | Post-1998
1 | 1 | 0 | 0 | 0 | 0.51086 | 0.19466 | 0.094461 | 0.20002
2 | 0.38461 | 0.4232 | 0.097699 | 0.094488 | 0.59165 | 0.3311 | 0.045098 | 0.032153
3 | 0.36992 | 0.33195 | 0.22729 | 0.070842 | 0.72089 | 0.18123 | 0.075913 | 0.021966
4 | 0.58528 | 0.21826 | 0.068364 | 0.1281 | 0.73575 | 0.18282 | 0.0303 | 0.051126
5 | 0.53336 | 0.3973 | 0.035865 | 0.033477 | 0.60192 | 0.2094 | 0.14074 | 0.047944
6 | 0.44529 | 0.30764 | 0.093307 | 0.15377 | 0.63085 | 0.19542 | 0.079246 | 0.094485
7 | 0.38433 | 0.30005 | 0.24363 | 0.07199 | 0.46432 | 0.35655 | 0.117 | 0.062122
8 | 0.53419 | 0.29756 | 0.10397 | 0.064275 | 0.65445 | 0.22229 | 0.068943 | 0.054316
9 | 0.63321 | 0.26133 | 0.075547 | 0.029914 | 0.70909 | 0.20698 | 0.064666 | 0.019257
10 | 0.24895 | 0.4903 | 0.1135 | 0.14725 | 0.31515 | 0.45209 | 0.10507 | 0.12769
11 | 0.38987 | 0.35714 | 0.13547 | 0.11752 | 0.36057 | 0.39051 | 0.136 | 0.11292
12 | 0.42772 | 0.3637 | 0.11492 | 0.093659 | 0.48841 | 0.33266 | 0.097051 | 0.081877
13 | 0.37598 | 0.35679 | 0.18238 | 0.084856 | 0.45759 | 0.31842 | 0.14806 | 0.07593
14 | 0.09011 | 0.75248 | 0.11994 | 0.037469 | 0.17004 | 0.7053 | 0.089048 | 0.03561
15 | 0.31525 | 0.49623 | 0.14634 | 0.042177 | 0.31169 | 0.49832 | 0.14857 | 0.041411
16 | 0.54164 | 0.34087 | 0.10803 | 0.00946 | 0.46631 | 0.42205 | 0.10173 | 0.009914
type | level | key | unit | EER
AC | SEER 10 | -eSA-10 | SA-10-HH | 9.17 |  | ACSEER 10 | SA-10-HH | SEER 10 (EER 9.17) | 10
AC | SEER 13 | -eSA-13 | SA-13-ML | 11.09 |  | ACSEER 13 | SA-13-ML | SEER 13 (EER 11.09) | 13
AC | SEER 14 | -eSA-14 | SA-14-ML | 12.15 |  | ACSEER 14 | SA-14-ML | SEER 14 (EER 12.15) | 14
AC | SEER 15 | -eSA-15 | SA-15-ML | 12.72 |  | ACSEER 15 | SA-15-ML | SEER 15 (EER 12.72) | 15
AC | SEER 16 | -eSA-16 | SA-16-LL | 11.61 |  | ACSEER 16 | SA-16-LL | SEER 16 (EER 11.61) | 16
AC | SEER 17 | -eSA-17 | SA-17-LL | 12.28 |  | ACSEER 17 | SA-17-LL | SEER 17 (EER 12.28) | 17
AC | SEER 18 | -eSA-18 | SA-18-TM | 13.37 |  | ACSEER 18 | SA-18-TM | SEER 18 (EER 13.37) | 18
HP | SEER 10 | -eSH-10 | SH-10-MM | 9.01 |  | HPSEER 10 | SH-10-MM | SEER 10 (EER 9.01)
HP | SEER 13 | -eSH-13 | SH-13-MM | 11.07 |  | HPSEER 13 | SH-13-MM | SEER 13 (EER 11.07)
HP | SEER 14 | -eSH-14 | SH-14-HM | 12.19 |  | HPSEER 14 | SH-14-HM | SEER 14 (EER 12.19)
HP | SEER 15 | -eSH-15 | SH-15-ML | 12.7 |  | HPSEER 15 | SH-15-ML | SEER 15 (EER 12.70)
HP | SEER 16 | -eSH-16 | SH-16-LM | 12.06 |  | HPSEER 16 | SH-16-LM | SEER 16 (EER 12.06)
HP | SEER 17 | -eSH-17 | SH-17-TH | 12.52 |  | HPSEER 17 | SH-17-TH | SEER 17 (EER 12.52)
HP | SEER 18 | -eSH-18 | SH-18-LM | 12.88 |  | HPSEER 18 | SH-18-LM | SEER 18 (EER 12.88)
OA drybulb hour bins |  |  |  | OA wetbulb hour bins (db≥72)
DB <72 (venting) | 72≤ DB < 82 | 82≤ DB < 95 | DB≥ 95 | WB <62 | 62≤ WB < 67 | 67≤ WB < 72 | WB≥ 72
8701 | 59 | 0 | 0 | 2285 | 244 | 34 | 0
7391 | 793 | 527 | 49 | 2025 | 467 | 71 | 0
8268 | 424 | 68 | 0 | 1906 | 565 | 92 | 0
7428 | 1044 | 278 | 10 | 1026 | 778 | 601 | 158
7995 | 690 | 75 | 0 | 1836 | 651 | 63 | 13
7807 | 903 | 50 | 0 | 1089 | 1180 | 279 | 15
7566 | 1082 | 112 | 0 | 932 | 1031 | 508 | 92
7090 | 1210 | 453 | 7 | 863 | 1078 | 530 | 92
6762 | 1197 | 727 | 74 | 1028 | 925 | 493 | 117
6386 | 1260 | 961 | 153 | 1194 | 979 | 370 | 20
6624 | 1025 | 914 | 197 | 1748 | 693 | 122 | 0
7041 | 903 | 696 | 120 | 1387 | 842 | 317 | 17
6021 | 1283 | 1106 | 350 | 1002 | 972 | 507 | 82
6197 | 1167 | 1054 | 342 | 2294 | 263 | 6 | 0
4190 | 1609 | 1722 | 1239 | 867 | 806 | 521 | 369
7713 | 674 | 370 | 3 | 2265 | 216 | 79 | 3
OA Drybulb hours between 72-82, 82-95, >95
OA Wetbulb hours between 62-67, 67-72, >72 when the OA drybulb is > 72F