## Sheet1
c:\d\e\TaxCredits\DOE-22
Output spreadsheet for HVAC BESTEST
DOE-2.2 version 47d (also used in eQUEST 3.63b), J.J. Hirsch & Assoc., July 21, 2009
DOE22-47d/JJH
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
Raw data entered Rows 48-61
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity |  | Qfan,heat | (del Qfan) | (del Qfan) | Calculated mean COP from monthly summary
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio | Qfan,heat | - Qfan | /Qfan | /Qcoil | COP | slight difference from use of hourly concurrent values
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | (kWh) | (kWh) | (frac) | (frac)
E100 | 1520.839 | 1312.06 | 141.301 | 67.478 | 3796.126 | 3796.126 | 0 | 3655.2685 | 3655.2685 | 0 | 2.403 | 22.3333 | 0.00741 | 2.404 | 22.3333 | 0.00741 | 2.403 | 22.3333 | 0.0074 | 140.8576 | -0.44344 | -0.0031481 | -0.00011681 | 2.4035
E110 | 1065.98 | 883.688 | 122.202 | 60.09 | 3758.5894 | 3758.5894 | 0 | 3636.7802 | 3636.7802 | 0 | 3.412 | 22.2778 | 0.00642 | 3.412 | 22.2778 | 0.00642 | 3.411 | 22.2778 | 0.00642 | 121.8092 | -0.3928 | -0.0032247 | -0.00010451 | 3.4117
E120 | 1003.17 | 838.369 | 109.767 | 55.034 | 3741.2705 | 3741.2705 | 0 | 3631.7544 | 3631.7544 | 0 | 3.62 | 26.7222 | 0.00782 | 3.621 | 26.7222 | 0.00782 | 3.62 | 26.7222 | 0.00782 | 109.5161 | -0.25088 | -0.0022908 | -6.7058e-05 | 3.623
E130 | 106.197 | 93.334 | 8.057 | 4.806 | 215.1348 | 215.1348 | 0 | 207.2046 | 207.2046 | 0 | 1.951 | 22.1111 | 0.00732 | 1.952 | 22.1111 | 0.00733 | 1.95 | 22.1111 | 0.00731 | 7.9302 | -0.12675 | -0.015984 | -0.00058918 | 1.953
E140 | 66.19 | 56 | 6.375 | 3.815 | 194.9385 | 194.9385 | 0 | 188.6797 | 188.6797 | 0 | 2.851 | 22.1111 | 0.00636 | 2.851 | 22.1111 | 0.00636 | 2.85 | 22.1111 | 0.00636 | 6.2588 | -0.11621 | -0.018567 | -0.00059612 | 2.854
E150 | 1183.406 | 982.141 | 135.85 | 65.415 | 4527.07 | 3787.6489 | 739.4212 | 4376.158 | 3636.75 | 739.408 | 3.698 | 22.3333 | 0.00825 | 3.705 | 22.3333 | 0.00825 | 3.691 | 22.3333 | 0.00824 | 150.8989 | 15.0489 | 0.099728 | 0.0033242 | 3.7
E160 | 1106.636 | 926.393 | 120.738 | 59.505 | 4508.6272 | 3769.2049 | 739.4223 | 4371.1392 | 3631.7312 | 739.408 | 3.95 | 26.7222 | 0.00986 | 3.954 | 26.7222 | 0.00988 | 3.946 | 26.7222 | 0.00984 | 137.4736 | 16.7356 | 0.12174 | 0.0037119 | 3.95
E165 | 1470.457 | 1256.202 | 145.289 | 68.966 | 4548.5868 | 3809.1729 | 739.4138 | 4387.221 | 3647.813 | 739.408 | 2.984 | 23.4444 | 0.00918 | 2.987 | 23.4444 | 0.00919 | 2.98 | 23.4444 | 0.00917 | 161.3599 | 16.0709 | 0.099597 | 0.0035332 | 2.9836
E170 | 620.703 | 523.688 | 62.947 | 34.068 | 2237.2336 | 1497.8063 | 739.4273 | 2158.0803 | 1418.6723 | 739.408 | 3.477 | 22.2222 | 0.01049 | 3.482 | 22.2222 | 0.01052 | 3.471 | 22.2222 | 0.01046 | 79.1339 | 16.1869 | 0.20455 | 0.0072352 | 3.477
E180 | 1087.062 | 918.411 | 112.521 | 56.13 | 4564.1275 | 1606.4379 | 2957.6896 | 4376.1993 | 1418.568 | 2957.6313 | 4.026 | 22.2778 | 0.01641 | 4.05 | 22.2778 | 0.01649 | 4.021 | 22.2778 | 0.01633 | 187.8699 | 75.3489 | 0.40107 | 0.016509 | 4.026
E185 | 1556.523 | 1352.904 | 137.64 | 65.979 | 4609.8382 | 1652.1509 | 2957.6873 | 4394.672 | 1437.0407 | 2957.6313 | 2.823 | 22.3333 | 0.01626 | 2.841 | 22.3333 | 0.01635 | 2.821 | 22.3333 | 0.01618 | 215.1102 | 77.4702 | 0.36014 | 0.016805 | 2.8234
E190 | 161.908 | 138.905 | 14.468 | 8.535 | 582.0826 | 212.3321 | 369.7506 | 558.3672 | 188.6632 | 369.704 | 3.449 | 22.1111 | 0.01598 | 3.474 | 22.1111 | 0.01608 | 3.437 | 22.1111 | 0.01588 | 23.6688 | 9.2008 | 0.38873 | 0.015807 | 3.457
E195 | 247.108 | 218.173 | 18.246 | 10.689 | 604.5648 | 234.8265 | 369.7383 | 576.8877 | 207.1838 | 369.704 | 2.335 | 22.1111 | 0.01551 | 2.365 | 22.1111 | 0.01566 | 2.322 | 22.1111 | 0.01542 | 27.6427 | 9.3967 | 0.33993 | 0.015543 | 2.337
E200 | 1441.371 | 1219.2 | 151.079 | 71.092 | 5523.2632 | 4301.874 | 1221.3892 | 5343.1741 | 4121.8136 | 1221.3605 | 3.707 | 26.7778 | 0.01106 | 3.714 | 26.7778 | 0.01109 | 3.7 | 26.7778 | 0.01103 | 180.0604 | 28.9814 | 0.16095 | 0.0052471 | 3.708
COP=(net refr effect)/(total elec)=((env sens)+(coil lat)); sens coil = (tot coil)-(lat coil); compr elec = (compr+odfan elec)-(odfan elec)
Envelope sensible includes adjustment for simulated zone temp (delta 0-0.1 C), from "QNOW" [sensible zone extraction].
Note: (fan elec) .NE. (total coil)-(sens coil), worsens with increasing humidity, check with jjh. | [13 empty] | max,min COP not directly available from out (requires writing an hourly post-processor)
raw data here |  |  |  |  | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  | SKWQC | SFKW | OFKW | QC |  | QCLAT |  | QNOW | QL |  | TAVE | WR |  | TAVE | WR |  | TAVE | WR
INSTRUCTIONS |  | Compressor | Supply | Condenser |  | Fan heat | [6 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | + od fan | Fan | (od) Fan | Total | (tot-sns-lat) | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Wh) | (Btu) | (Btu) | (Btu) | (Btu) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100 |  | 1379.538 | 141.301 | 67.478 | 12952382 | 140857.5615 | 0 |  | 12471776 | 0 | 2.403 | 72.2 | 0.00741 | 2.404 | 72.2 | 0.00741 | 2.403 | 72.2 | 0.0074
E110 |  | 943.778 | 122.202 | 60.09 | 12824307 | 121809.2028 | 0 |  | 12408694 | 0 | 3.412 | 72.1 | 0.00642 | 3.412 | 72.1 | 0.00642 | 3.411 | 72.1 | 0.00642
E120 |  | 893.403 | 109.767 | 55.034 | 12765215 | 109516.1196 | 0 |  | 12391546 | 0 | 3.62 | 80.1 | 0.00782 | 3.621 | 80.1 | 0.00782 | 3.62 | 80.1 | 0.00782
E130 |  | 98.14 | 8.057 | 4.806 | 734040 | 7930.2462 | 0 |  | 706982 | 0 | 1.951 | 71.8 | 0.00732 | 1.952 | 71.8 | 0.00733 | 1.95 | 71.8 | 0.00731
E140 |  | 59.815 | 6.375 | 3.815 | 665130 | 6258.7925 | 0 |  | 643775 | 0 | 2.851 | 71.8 | 0.00636 | 2.851 | 71.8 | 0.00636 | 2.85 | 71.8 | 0.00636
E150 |  | 1047.556 | 135.85 | 65.415 | 15446363 | 150898.8863 | 2522905 |  | 12408591 | 2522860 | 3.698 | 72.2 | 0.00825 | 3.705 | 72.2 | 0.00825 | 3.691 | 72.2 | 0.00824
E160 |  | 985.898 | 120.738 | 59.505 | 15383436 | 137473.6225 | 2522909 |  | 12391467 | 2522860 | 3.95 | 80.1 | 0.00986 | 3.954 | 80.1 | 0.00988 | 3.946 | 80.1 | 0.00984
E165 |  | 1325.168 | 145.289 | 68.966 | 15519778 | 161359.9062 | 2522880 |  | 12446338 | 2522860 | 2.984 | 74.2 | 0.00918 | 2.987 | 74.2 | 0.00919 | 2.98 | 74.2 | 0.00917
E170 |  | 557.756 | 62.947 | 34.068 | 7633441 | 79133.939 | 2522926 |  | 4840510 | 2522860 | 3.477 | 72 | 0.01049 | 3.482 | 72 | 0.01052 | 3.471 | 72 | 0.01046
E180 |  | 974.541 | 112.521 | 56.13 | 15572803 | 187869.871 | 10091637 |  | 4840154 | 10091438 | 4.026 | 72.1 | 0.01641 | 4.05 | 72.1 | 0.01649 | 4.021 | 72.1 | 0.01633
E185 |  | 1418.883 | 137.64 | 65.979 | 15728768 | 215110.1993 | 10091629 |  | 4903183 | 10091438 | 2.823 | 72.2 | 0.01626 | 2.841 | 72.2 | 0.01635 | 2.821 | 72.2 | 0.01618
E190 |  | 147.44 | 14.468 | 8.535 | 1986066 | 23668.8159 | 1261589 |  | 643719 | 1261430 | 3.449 | 71.8 | 0.01598 | 3.474 | 71.8 | 0.01608 | 3.437 | 71.8 | 0.01588
E195 |  | 228.862 | 18.246 | 10.689 | 2062775 | 27642.7315 | 1261547 |  | 706911 | 1261430 | 2.335 | 71.8 | 0.01551 | 2.365 | 71.8 | 0.01566 | 2.322 | 71.8 | 0.01542
E200 |  | 1290.292 | 151.079 | 71.092 | 18845374 | 180060.3751 | 4167380 |  | 14063628 | 4167282 | 3.707 | 80.2 | 0.01106 | 3.714 | 80.2 | 0.01109 | 3.7 | 80.2 | 0.01103
Table "tkfanheat". Fan Heat Discrepancy
d:\e\iea22\hvabtest\results\doe2\21ejna2a.wk3 a:63; 31 jan 00
F e b r u a r y T o t a l s
| Supply | Evaporator Coil Load |  |  |  | Envelope Load |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Fan | Total | Sensible | Latent | Sensible | Latent | Qfan,heat | - Qfan | /Qfan | /Qcoil
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (frac) | (frac)
E100 | 141.301 | 3796.126 | 3796.126 | 0 | 3655.2685 | 0 | 140.8576 | -0.44344 | -0.0031481 | -0.00011681
E110 | 122.202 | 3758.5894 | 3758.5894 | 0 | 3636.7802 | 0 | 121.8092 | -0.3928 | -0.0032247 | -0.00010451
E120 | 109.767 | 3741.2705 | 3741.2705 | 0 | 3631.7544 | 0 | 109.5161 | -0.25088 | -0.0022908 | -6.7058e-05
E130 | 8.057 | 215.1348 | 215.1348 | 0 | 207.2046 | 0 | 7.9302 | -0.12675 | -0.015984 | -0.00058918
E140 | 6.375 | 194.9385 | 194.9385 | 0 | 188.6797 | 0 | 6.2588 | -0.11621 | -0.018567 | -0.00059612
E150 | 135.85 | 4527.07 | 3787.6489 | 739.4212 | 3636.75 | 739.408 | 150.8989 | 15.0489 | 0.099728 | 0.0033242
E160 | 120.738 | 4508.6272 | 3769.2049 | 739.4223 | 3631.7312 | 739.408 | 137.4736 | 16.7356 | 0.12174 | 0.0037119
E165 | 145.289 | 4548.5868 | 3809.1729 | 739.4138 | 3647.813 | 739.408 | 161.3599 | 16.0709 | 0.099597 | 0.0035332
E170 | 62.947 | 2237.2336 | 1497.8063 | 739.4273 | 1418.6723 | 739.408 | 79.1339 | 16.1869 | 0.20455 | 0.0072352
E180 | 112.521 | 4564.1275 | 1606.4379 | 2957.6896 | 1418.568 | 2957.6313 | 187.8699 | 75.3489 | 0.40107 | 0.016509
E185 | 137.64 | 4609.8382 | 1652.1509 | 2957.6873 | 1437.0407 | 2957.6313 | 215.1102 | 77.4702 | 0.36014 | 0.016805
E190 | 14.468 | 582.0826 | 212.3321 | 369.7506 | 188.6632 | 369.704 | 23.6688 | 9.2008 | 0.38873 | 0.015807
E195 | 18.246 | 604.5648 | 234.8265 | 369.7383 | 207.1838 | 369.704 | 27.6427 | 9.3967 | 0.33993 | 0.015543
E200 | 151.079 | 5523.2632 | 4301.874 | 1221.3892 | 4121.8136 | 1221.3605 | 180.0604 | 28.9814 | 0.16095 | 0.0052471
E100R2EP | 141 | 3794.2556 | 3794.2556 | 0 | 3655.3341 | 0 | 138.9215 | -2.0785 | -0.014962 | -0.00054781
E180R2EP | 112 | 4534.8769 | 1606.9754 | 2927.9015 | 1418.5229 | 2957.5029 | 188.4525 | 76.4525 | 0.40569 | 0.016859