## Sheet1
Output spreadsheet for HVAC BESTEST
DOE-2.2, 48y (also used in eQUEST v3.65), J.J. Hirsch & Assoc., April 16, 2016
DOE-2.2, 48y/JJH
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
Raw data entered Rows 48-61
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity |  | Qfan,heat | (del Qfan) | (del Qfan) | Calculated mean COP from monthly summary
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio | Qfan,heat | - Qfan | /Qfan | /Qcoil | COP | slight difference from use of hourly concurrent values
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | (kWh) | (kWh) | (frac) | (frac)
E100 | 1520.424 | 1311.599 | 141.287 | 67.538 | 3796.1372 | 3796.1372 | 0 | 3655.2904 | 3655.2904 | 0 | 2.753 | 22.3333 | 0.00741 | 2.753 | 22.3333 | 0.00741 | 2.752 | 22.3333 | 0.0074 | 140.8467 | -0.44028 | -0.003126 | -0.00011598 | 2.4041
E110 | 1066.012 | 883.626 | 122.226 | 60.16 | 3758.631 | 3758.631 | 0 | 3636.8013 | 3636.8013 | 0 | 3.983 | 22.2778 | 0.00642 | 3.983 | 22.2778 | 0.00642 | 3.982 | 22.2778 | 0.00642 | 121.8297 | -0.39628 | -0.0032527 | -0.00010543 | 3.4116
E120 | 1002.627 | 837.781 | 109.758 | 55.088 | 3741.2814 | 3741.2814 | 0 | 3631.7737 | 3631.7737 | 0 | 4.19 | 26.7222 | 0.00782 | 4.191 | 26.7222 | 0.00783 | 4.19 | 26.7222 | 0.00782 | 109.5076 | -0.25038 | -0.0022864 | -6.6924e-05 | 3.623
E130 | 106.212 | 93.342 | 8.057 | 4.813 | 215.1591 | 215.1591 | 0 | 207.2286 | 207.2286 | 0 | 2.192 | 22.1111 | 0.00732 | 2.193 | 22.1111 | 0.00733 | 2.191 | 22.1111 | 0.00731 | 7.9305 | -0.12646 | -0.015946 | -0.00058775 | 1.953
E140 | 66.219 | 56.021 | 6.377 | 3.821 | 194.9598 | 194.9598 | 0 | 188.699 | 188.699 | 0 | 3.258 | 22.1111 | 0.00636 | 3.258 | 22.1111 | 0.00636 | 3.257 | 22.1111 | 0.00636 | 6.2608 | -0.11616 | -0.018553 | -0.00059579 | 2.854
E150 | 1183.6 | 982.149 | 135.939 | 65.512 | 4527.1779 | 3787.757 | 739.4209 | 4376.182 | 3636.774 | 739.408 | 4.321 | 22.3333 | 0.00825 | 4.329 | 22.3333 | 0.00825 | 4.314 | 22.3333 | 0.00825 | 150.983 | 15.044 | 0.09964 | 0.003323 | 3.7
E160 | 1106.908 | 926.439 | 120.856 | 59.613 | 4508.7743 | 3769.352 | 739.4223 | 4371.1609 | 3631.7529 | 739.408 | 4.573 | 26.7222 | 0.00987 | 4.577 | 26.7222 | 0.00989 | 4.568 | 26.7222 | 0.00985 | 137.5991 | 16.7431 | 0.12168 | 0.0037134 | 3.95
E165 | 1471.006 | 1256.491 | 145.432 | 69.083 | 4548.7594 | 3809.3453 | 739.4141 | 4387.2412 | 3647.8332 | 739.408 | 3.432 | 23.4444 | 0.00919 | 3.436 | 23.4444 | 0.0092 | 3.428 | 23.4444 | 0.00918 | 161.512 | 16.08 | 0.099559 | 0.003535 | 2.9825
E170 | 620.998 | 523.852 | 63.009 | 34.137 | 2237.3183 | 1497.891 | 739.4273 | 2158.1002 | 1418.6923 | 739.408 | 4.01 | 22.2222 | 0.01049 | 4.015 | 22.2222 | 0.01052 | 4.004 | 22.2222 | 0.01046 | 79.1987 | 16.1897 | 0.20442 | 0.0072362 | 3.477
E180 | 1086.695 | 917.91 | 112.586 | 56.199 | 4564.2186 | 1606.529 | 2957.6896 | 4376.2186 | 1418.5873 | 2957.6313 | 4.686 | 22.2778 | 0.0164 | 4.712 | 22.2778 | 0.01649 | 4.681 | 22.2778 | 0.01632 | 187.9417 | 75.3557 | 0.40095 | 0.01651 | 4.026
E185 | 1556.022 | 1352.124 | 137.833 | 66.065 | 4610.0677 | 1652.3836 | 2957.6841 | 4394.6978 | 1437.0665 | 2957.6313 | 3.251 | 22.3333 | 0.01626 | 3.266 | 22.3333 | 0.01635 | 3.248 | 22.3333 | 0.01618 | 215.3171 | 77.4841 | 0.35986 | 0.016808 | 2.8243
E190 | 161.935 | 138.907 | 14.478 | 8.55 | 582.1137 | 212.3631 | 369.7506 | 558.3866 | 188.6826 | 369.704 | 3.948 | 22.1111 | 0.01598 | 3.976 | 22.1111 | 0.01608 | 3.937 | 22.1111 | 0.01588 | 23.6805 | 9.2025 | 0.38861 | 0.015809 | 3.457
E195 | 247.335 | 218.343 | 18.275 | 10.717 | 604.6187 | 234.8804 | 369.7383 | 576.9115 | 207.2075 | 369.704 | 2.64 | 22.1111 | 0.01551 | 2.672 | 22.1111 | 0.01566 | 2.628 | 22.1111 | 0.01542 | 27.6729 | 9.3979 | 0.33961 | 0.015544 | 2.337
E200 | 1441.487 | 1219.062 | 151.217 | 71.208 | 5523.4385 | 4302.0492 | 1221.3892 | 5343.1981 | 4121.8376 | 1221.3605 | 4.281 | 26.7778 | 0.01107 | 4.288 | 26.7778 | 0.0111 | 4.273 | 26.7778 | 0.01103 | 180.2116 | 28.9946 | 0.16089 | 0.0052494 | 3.708
COP=(net refr effect)/(total elec)=((env sens)+(coil lat)); sens coil = (tot coil)-(lat coil); compr elec = (compr+odfan elec)-(odfan elec)
Envelope sensible includes adjustment for simulated zone temp (delta 0-0.1 C), from "QNOW" [sensible zone extraction].
Note: (fan elec) .NE. (total coil)-(sens coil), worsens with increasing humidity, check with jjh. | [13 empty] | max,min COP not directly available from out (requires writing an hourly post-processor)
raw data here |  |  |  |  | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  | SKWQC | SFKW | OFKW | QC |  | QCLAT |  | QNOW | QL |  | TAVE | WR |  | TAVE | WR |  | TAVE | WR
INSTRUCTIONS |  | Compressor | Supply | Condenser |  | Fan heat | [6 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | + od fan | Fan | (od) Fan | Total | (tot-sns-lat) | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Wh) | (Btu) | (Btu) | (Btu) | (Btu) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100 |  | 1379.137 | 141.287 | 67.538 | 12952420 | 140846.7175 | 0 |  | 12471851 | 0 | 2.753 | 72.2 | 0.00741 | 2.753 | 72.2 | 0.00741 | 2.752 | 72.2 | 0.0074
E110 |  | 943.786 | 122.226 | 60.16 | 12824449 | 121829.7186 | 0 |  | 12408766 | 0 | 3.983 | 72.1 | 0.00642 | 3.983 | 72.1 | 0.00642 | 3.982 | 72.1 | 0.00642
E120 |  | 892.869 | 109.758 | 55.088 | 12765252 | 109507.6202 | 0 |  | 12391612 | 0 | 4.19 | 80.1 | 0.00782 | 4.191 | 80.1 | 0.00783 | 4.19 | 80.1 | 0.00782
E130 |  | 98.155 | 8.057 | 4.813 | 734123 | 7930.5393 | 0 |  | 707064 | 0 | 2.192 | 71.8 | 0.00732 | 2.193 | 71.8 | 0.00733 | 2.191 | 71.8 | 0.00731
E140 |  | 59.842 | 6.377 | 3.821 | 665203 | 6260.8441 | 0 |  | 643841 | 0 | 3.258 | 71.8 | 0.00636 | 3.258 | 71.8 | 0.00636 | 3.257 | 71.8 | 0.00636
E150 |  | 1047.661 | 135.939 | 65.512 | 15446731 | 150983.0012 | 2522904 |  | 12408673 | 2522860 | 4.321 | 72.2 | 0.00825 | 4.329 | 72.2 | 0.00825 | 4.314 | 72.2 | 0.00825
E160 |  | 986.052 | 120.856 | 59.613 | 15383938 | 137599.0621 | 2522909 |  | 12391541 | 2522860 | 4.573 | 80.1 | 0.00987 | 4.577 | 80.1 | 0.00989 | 4.568 | 80.1 | 0.00985
E165 |  | 1325.574 | 145.432 | 69.083 | 15520367 | 161512.0164 | 2522881 |  | 12446407 | 2522860 | 3.432 | 74.2 | 0.00919 | 3.436 | 74.2 | 0.0092 | 3.428 | 74.2 | 0.00918
E170 |  | 557.989 | 63.009 | 34.137 | 7633730 | 79198.7104 | 2522926 |  | 4840578 | 2522860 | 4.01 | 72 | 0.01049 | 4.015 | 72 | 0.01052 | 4.004 | 72 | 0.01046
E180 |  | 974.109 | 112.586 | 56.199 | 15573114 | 187941.6764 | 10091637 |  | 4840220 | 10091438 | 4.686 | 72.1 | 0.0164 | 4.712 | 72.1 | 0.01649 | 4.681 | 72.1 | 0.01632
E185 |  | 1418.189 | 137.833 | 66.065 | 15729551 | 215317.1161 | 10091618 |  | 4903271 | 10091438 | 3.251 | 72.2 | 0.01626 | 3.266 | 72.2 | 0.01635 | 3.248 | 72.2 | 0.01618
E190 |  | 147.457 | 14.478 | 8.55 | 1986172 | 23680.5393 | 1261589 |  | 643785 | 1261430 | 3.948 | 71.8 | 0.01598 | 3.976 | 71.8 | 0.01608 | 3.937 | 71.8 | 0.01588
E195 |  | 229.06 | 18.275 | 10.717 | 2062959 | 27672.9191 | 1261547 |  | 706992 | 1261430 | 2.64 | 71.8 | 0.01551 | 2.672 | 71.8 | 0.01566 | 2.628 | 71.8 | 0.01542
E200 |  | 1290.27 | 151.217 | 71.208 | 18845972 | 180211.6061 | 4167380 |  | 14063710 | 4167282 | 4.281 | 80.2 | 0.01107 | 4.288 | 80.2 | 0.0111 | 4.273 | 80.2 | 0.01103
Table "tkfanheat". Fan Heat Discrepancy
F e b r u a r y T o t a l s
| Supply | Evaporator Coil Load |  |  |  | Envelope Load |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Fan | Total | Sensible | Latent | Sensible | Latent | Qfan,heat | - Qfan | /Qfan | /Qcoil
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (frac) | (frac)
E100 | 141.287 | 3796.1372 | 3796.1372 | 0 | 3655.2904 | 0 | 140.8467 | -0.44028 | -0.003126 | -0.00011598
E110 | 122.226 | 3758.631 | 3758.631 | 0 | 3636.8013 | 0 | 121.8297 | -0.39628 | -0.0032527 | -0.00010543
E120 | 109.758 | 3741.2814 | 3741.2814 | 0 | 3631.7737 | 0 | 109.5076 | -0.25038 | -0.0022864 | -6.6924e-05
E130 | 8.057 | 215.1591 | 215.1591 | 0 | 207.2286 | 0 | 7.9305 | -0.12646 | -0.015946 | -0.00058775
E140 | 6.377 | 194.9598 | 194.9598 | 0 | 188.699 | 0 | 6.2608 | -0.11616 | -0.018553 | -0.00059579
E150 | 135.939 | 4527.1779 | 3787.757 | 739.4209 | 3636.774 | 739.408 | 150.983 | 15.044 | 0.09964 | 0.003323
E160 | 120.856 | 4508.7743 | 3769.352 | 739.4223 | 3631.7529 | 739.408 | 137.5991 | 16.7431 | 0.12168 | 0.0037134
E165 | 145.432 | 4548.7594 | 3809.3453 | 739.4141 | 3647.8332 | 739.408 | 161.512 | 16.08 | 0.099559 | 0.003535
E170 | 63.009 | 2237.3183 | 1497.891 | 739.4273 | 1418.6923 | 739.408 | 79.1987 | 16.1897 | 0.20442 | 0.0072362
E180 | 112.586 | 4564.2186 | 1606.529 | 2957.6896 | 1418.5873 | 2957.6313 | 187.9417 | 75.3557 | 0.40095 | 0.01651
E185 | 137.833 | 4610.0677 | 1652.3836 | 2957.6841 | 1437.0665 | 2957.6313 | 215.3171 | 77.4841 | 0.35986 | 0.016808
E190 | 14.478 | 582.1137 | 212.3631 | 369.7506 | 188.6826 | 369.704 | 23.6805 | 9.2025 | 0.38861 | 0.015809
E195 | 18.275 | 604.6187 | 234.8804 | 369.7383 | 207.2075 | 369.704 | 27.6729 | 9.3979 | 0.33961 | 0.015544
E200 | 151.217 | 5523.4385 | 4302.0492 | 1221.3892 | 4121.8376 | 1221.3605 | 180.2116 | 28.9946 | 0.16089 | 0.0052494
E100R2EP | 141 | 3794.2556 | 3794.2556 | 0 | 3655.3341 | 0 | 138.9215 | -2.0785 | -0.014962 | -0.00054781
E180R2EP | 112 | 4534.8769 | 1606.9754 | 2927.9015 | 1418.5229 | 2957.5029 | 188.4525 | 76.4525 | 0.40569 | 0.016859