## A
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
DOE-2.2, 48y (also used in eQUEST v3.65), J.J. Hirsch & Assoc., April 16, 2016
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
DOE-2.2, 48y |  | JJH | 16April2016
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 36539 | 23347 | 2312 | 10880 | 77515.5708 | 55988.2551 | 21527.3157 | 3.021 | 24.0556 | 0.00921 | 48.27 | 19.8889 | 0.0116 | E300 | 12771 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15 | 35 | 2016-07-20 | 15 | 0.0225 | 2016-10-02 | 9
E310 | 39492 | 25914 | 2698 | 10880 | 97611.6792 | 56468.9391 | 41142.7401 | 3.4116 | 24.1111 | 0.01126 | 58.5 | ODB, OHR |  | E310 | 13509 | 2016-07-20 | 15 | 23137 | 2016-06-04 | 16 | 15239 | 2016-09-03 | 15 | 37061 | 2016-09-03 | 16 | from E500 |  |  | from E530
E320 | 38855 | 25348 | 2627 | 10880 | 96901.4979 | 63046.1031 | 33855.3948 | 3.4639 | 24.3889 | 0.01006 | 51.24 | from E500 |  | E320 | 13834 | 2016-07-20 | 15 | 31079 | 2016-04-24 | 16 | 31753 | 2016-10-02 | 9 | 54277 | 2016-10-02 | 9
E330 | 39446 | 25925 | 2641 | 10880 | 101440.4445 | 63628.4928 | 37811.9517 | 3.5511 | 24.2778 | 0.00987 | 50.64 |  |  | E330 | 14264 | 2016-07-20 | 15 | 34584 | 2016-06-14 | 15 | 42069 | 2016-10-02 | 9 | 66568 | 2016-10-02 | 9
E340 | 39311 | 25782 | 2649 | 10880 | 99647.8449 | 63408.0816 | 36239.7633 | 3.5049 | 24.2778 | 0.0099 | 50.72 |  |  | E340 | 14050 | 2016-07-20 | 15 | 32075 | 2016-05-16 | 16 | 36603 | 2016-10-02 | 9 | 60540 | 2016-10-02 | 9
E350 | 30903 | 18126 | 1897 | 10880 | 64834.5993 | 48554.0667 | 16280.5326 | 3.238 | 26.1667 | 0.00994 | 45.41 |  |  | E350 | 12481 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9396 | 2016-09-03 | 15 | 31475 | 2016-07-20 | 15
E360 | 54038 | 38974 | 4184 | 10880 | 160258.5801 | 135252.1674 | 25006.4127 | 3.7133 | 25.5556 | 0.0087 | 41.48 |  |  | E360 | 13618 | 2016-07-20 | 15 | 32075 | 2016-05-16 | 15 | 10378 | 2016-10-02 | 9 | 41228 | 2016-10-02 | 9
E400 | 30938 | 18187 | 1871 | 10880 | 65130.0441 | 41472.1845 | 23657.8596 | 3.2471 | 24.0556 | 0.01002 | 52.25 |  |  | E400 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 32593 | 2016-09-18 | 15 | 50141 | 2016-09-18 | 15
E410 | 31762 | 18908 | 1974 | 10880 | 66949.0227 | 47690.5941 | 19258.4286 | 3.2061 | 24.0556 | 0.00948 | 49.58 |  |  | E410 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E420 | 32604 | 19662 | 2062 | 10880 | 69720.2832 | 49720.8978 | 19999.3854 | 3.2094 | 24.0556 | 0.00938 | 49.13 |  |  | E420 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E430 | 31987 | 19109 | 1998 | 10880 | 67709.3241 | 47786.7309 | 19922.5932 | 3.2079 | 24.0556 | 0.00939 | 49.17 |  |  | E430 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 11147 | 2016-05-21 | 15 | 31476 | 2016-07-20 | 15
E440 | 33091 | 20096 | 2115 | 10880 | 71450.7456 | 50638.5939 | 20812.1517 | 3.2169 | 24.0556 | 0.00925 | 48.46 |  |  | E440 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E500 | 22836 | 18491 | 1979 | 2366 | 65929.0347 | 47687.9562 | 18241.0785 | 3.2208 | 20.6667 |  |  |  |  | E500 | 11226 | 2016-07-20 | 15 | 20017 | 2016-06-04 | 16 | 7621 | 2016-09-03 | 15 | 27638 | 2016-06-04 | 16
E500 May-Sep | 22836 | 18491 | 1979 | 2366 | 65929.0347 | 47687.9562 | 18241.0785 | 3.2208 | 25 | 0.01133 | 57.34 |  |  | E510 | 12468 | 2016-07-20 | 15 | 22529 | 2016-07-20 | 15 | 8573 | 2016-09-09 | 8 | 31102 | 2016-07-20 | 15
E510 May-Sep | 43268 | 34624 | 3720 | 4924 | 137837.6025 | 99702.6546 | 38134.9479 | 3.5948 | 25.1111 | 0.0114 | 57.21 |  |  | E520 | 11920 | 2016-07-20 | 15 | 20163 | 2016-05-29 | 16 | 7621 | 2016-08-11 | 16 | 27784 | 2016-05-29 | 16
E520 | 25268 | 20029 | 2385 | 2854 | 66407.0808 | 48165.123 | 18241.9578 | 2.9628 | 13.7778 |  |  |  |  | E522 | 11834 | 2016-07-20 | 15 | 20153 | 2016-08-16 | 16 | 7621 | 2016-08-13 | 16 | 27774 | 2016-08-16 | 16
E522 | 24291 | 19412 | 2185 | 2694 | 66255.8412 | 48013.8834 | 18241.9578 | 3.0678 | 17.2778 |  |  |  |  | E525 | 10224 | 2016-07-20 | 15 | 19834 | 2016-06-04 | 16 | 7621 | 2016-09-18 | 15 | 27455 | 2016-06-04 | 16
E525 | 20485 | 16944 | 1649 | 1892 | 65455.6782 | 47216.6514 | 18239.0268 | 3.5204 | 27.3889 |  |  |  |  | E530 | 8735 | 2016-07-20 | 15 | 19585 | 2016-07-29 | 16 | 0 | 2016-09-03 | 16 | 19585 | 2016-07-29 | 16
E530 | 17608 | 14185 | 1588 | 1835 | 46715.4504 | 46715.4504 | 0 | 2.9617 | 20.6111 |  |  |  |  | E540 | 9745 | 2016-07-20 | 15 | 19802 | 2016-07-14 | 16 | 0 | 2016-08-15 | 15 | 19803 | 2016-07-14 | 16
E540 | 19944 | 15736 | 1947 | 2261 | 47241.2718 | 47241.2718 | 0 | 2.6716 | 13.7778 |  |  |  |  | E545 | 7920 | 2016-04-24 | 16 | 19463 | 2016-04-24 | 16 | 0 | 2016-08-11 | 15 | 19463 | 2016-04-24 | 16
E545 | 15857 | 13011 | 1340 | 1506 | 46288.1106 | 46288.1106 | 0 | 3.2254 | 27.3889
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 | [5 empty] | A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor | [5 empty] | C O P 2 |  |  |  |  | Indoor Drybulb Temperature | [5 empty] | Humidity Ratio | [5 empty] | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2075 | 238 | 7551.7215 | 5891.31 | 1660.4115 | 0.0094 | 3.2649 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.628 | 2016-04-30 | 16 | 2.744 | 2016-12-28 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.17 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4
2 | 2118 | 241 | 7636.1343 | 6073.6182 | 1562.5161 | 0.0093 | 3.237 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.141 | 2016-04-30 | 16 | 2.842 | 2016-12-01 | 14 | 26.7 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0157 | 2016-10-02 | 1 | 0.0017 | 2016-01-04 | 24 | 78.57 | 2016-10-02 | 8 | 11.99 | 2016-11-06 | 4
3 | 2075 | 238 | 7554.6525 | 5883.9825 | 1670.67 | 0.0094 | 3.2662 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E320 | 5.183 | 2016-10-02 | 9 | 2.796 | 2016-12-01 | 14 | 31.4889 | 2016-07-08 | 16 | 10.8444 | 2016-01-06 | 7 | 0.0176 | 2016-07-10 | 12 | 0.0017 | 2016-01-04 | 24 | 83.63 | 2016-10-02 | 9 | 11.99 | 2016-11-06 | 4
4 | 2073 | 237 | 7539.7044 | 5881.6377 | 1658.0667 | 0.0094 | 3.2639 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E330 | 6.304 | 2016-10-02 | 9 | 2.79 | 2016-12-01 | 14 | 32.0111 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0177 | 2016-07-10 | 13 | 0.0017 | 2016-01-04 | 24 | 78 | 2016-09-18 | 9 | 11.99 | 2016-11-06 | 4
5 | 1850 | 213 | 6751.2654 | 5669.7264 | 1081.539 | 0.009 | 3.2725 | 17.2222 | 23.7778 | 16.85 | 0.0103 | 0.0091 | 101593.5104 | E340 | 5.734 | 2016-10-02 | 9 | 2.79 | 2016-12-01 | 14 | 31.5611 | 2016-07-08 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0174 | 2016-07-10 | 12 | 0.0017 | 2016-01-04 | 24 | 81.17 | 2016-09-18 | 9 | 11.99 | 2016-11-06 | 4
6 | 2293 | 263 | 8206.8 | 6454.6482 | 1752.1518 | 0.0092 | 3.2108 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.9 | 2016-04-27 | 5 | 2.79 | 2016-12-01 | 14 | 34.9167 | 2016-06-25 | 7 | 8.9056 | 2016-01-06 | 6 | 0.0198 | 2016-10-01 | 21 | 0.0017 | 2016-01-04 | 24 | 81.1 | 2016-08-07 | 21 | 11.99 | 2016-11-06 | 4
7 | 3372 | 364 | 11291.0913 | 8389.4013 | 2901.69 | 0.0098 | 3.0222 | 25 | 24.9444 | 18.39 | 0.0133 | 0.0105 | 101593.5104 | E360 | 4.424 | 2016-10-04 | 24 | 2.79 | 2016-12-01 | 14 | 32.5222 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.17 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4
8 | 3242 | 331 | 10276.6722 | 9071.445 | 1205.2272 | 0.0094 | 2.8762 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.873 | 2016-09-18 | 15 | 2.731 | 2016-12-03 | 14 | 28.7889 | 2016-09-18 | 16 | 8.9056 | 2016-01-06 | 6 | 0.017 | 2016-04-05 | 22 | 0.0017 | 2016-01-04 | 24 | 85.74 | 2016-04-05 | 21 | 11.99 | 2016-11-06 | 4
9 | 4593 | 474 | 14873.3595 | 11899.2738 | 2974.0857 | 0.0099 | 2.9353 | 28.8889 | 25.5556 | 18.36 | 0.0117 | 0.0102 | 101593.5104 | E410 | 3.864 | 2016-04-30 | 16 | 2.79 | 2016-12-01 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0169 | 2016-04-02 | 5 | 0.0017 | 2016-01-04 | 24 | 84.76 | 2016-04-02 | 5 | 11.99 | 2016-11-06 | 4
10 | 4781 | 483 | 15409.4394 | 12054.6168 | 3354.8226 | 0.0102 | 2.9273 | 28.8889 | 25.5556 | 18.68 | 0.0125 | 0.0106 | 101593.5104 | E420 | 3.77 | 2016-09-27 | 15 | 2.79 | 2016-12-01 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0147 | 2016-04-02 | 1 | 0.0017 | 2016-01-04 | 24 | 74.53 | 2016-04-17 | 7 | 11.99 | 2016-11-06 | 4
11 | 5571 | 549 | 17657.2233 | 12858.0039 | 4799.2194 | 0.0107 | 2.8852 | 31.1111 | 25.8889 | 19.48 | 0.0148 | 0.0115 | 101593.5104 | E430 | 3.808 | 2016-10-24 | 15 | 2.731 | 2016-12-03 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0156 | 2016-04-02 | 4 | 0.0017 | 2016-01-04 | 24 | 78.41 | 2016-04-02 | 4 | 11.99 | 2016-11-06 | 4
12 | 5199 | 497 | 16187.3268 | 12609.7482 | 3577.5786 | 0.0108 | 2.8419 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.769 | 2016-09-27 | 15 | 2.731 | 2016-12-03 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.15 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4
13 | 6168 | 591 | 19608.6831 | 17122.0227 | 2486.6604 | 0.0102 | 2.9011 | 31.1111 | 25.9444 | 18.56 | 0.0115 | 0.0103 | 101593.5104 | E500 | 8.586 | 2016-03-11 | 10 | 2.687 | 2016-07-29 | 12 | 25.1 | 2016-07-29 | 16 | 6.6056 | 2016-01-14 | 9 | 0.0118 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.81 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1
14 | 6465 | 634 | 20828.8584 | 17647.2579 | 3181.6005 | 0.01 | 2.9341 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 8.585 | 2016-03-11 | 10 | 2.808 | 2016-04-05 | 17 | 25.1333 | 2016-07-20 | 15 | 6.6056 | 2016-01-14 | 9 | 0.0118 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.81 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1
15 | 7661 | 753 | 25401.2184 | 22203.4974 | 3197.721 | 0.0098 | 3.0189 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 6.455 | 2016-03-28 | 20 | 2.201 | 2016-11-16 | 11 | 15.7722 | 2016-08-16 | 16 | 5.3944 | 2016-01-06 | 9 | 0.0075 | 2016-08-16 | 16 | 0 | 2016-01-01 | 1 | 70.13 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1
16 | 8207 | 811 | 27760.0872 | 22568.1138 | 5191.9734 | 0.0098 | 3.0783 | 32.2222 | 26.1667 | 18.84 | 0.0144 | 0.0106 | 101254.8653 | E522 | 6.182 | 2016-03-11 | 10 | 2.565 | 2016-07-29 | 12 | 20.1333 | 2016-08-16 | 16 | 6.0667 | 2016-01-06 | 9 | 0.0094 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.49 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1
17 | 5794 | 566 | 18271.5609 | 13621.5294 | 4650.0315 | 0.0107 | 2.8729 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 9.876 | 2016-03-11 | 10 | 2.937 | 2016-07-30 | 12 | 35.05 | 2016-06-04 | 16 | 6.9667 | 2016-01-14 | 9 | 0.0179 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 53.59 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1
18 | 5742 | 548 | 17998.6848 | 12848.3316 | 5150.3532 | 0.0112 | 2.8615 | 31.1111 | 25.9444 | 19.75 | 0.0157 | 0.0119 | 101254.8653 | E530 | 4.81 | 2016-03-11 | 10 | 2.491 | 2016-07-29 | 12 | 25.0444 | 2016-07-29 | 16 | 6.6056 | 2016-01-14 | 9 | 0.0089 | 2016-10-23 | 9 | 0 | 2016-01-01 | 1 | 46.07 | 2016-10-23 | 9 | 0 | 2016-01-01 | 1
19 | 5007 | 476 | 15895.3992 | 11856.4812 | 4038.918 | 0.0111 | 2.899 | 28.3333 | 25.5 | 19.32 | 0.0143 | 0.0115 | 101254.8653 | E540 | 6.453 | 2016-03-28 | 20 | 2.201 | 2016-11-16 | 11 | 15.0889 | 2016-08-16 | 16 | 5.3944 | 2016-01-06 | 9 | 0.0052 | 2016-11-16 | 11 | 0 | 2016-01-01 | 1 | 50 | 2016-11-16 | 11 | 0 | 2016-01-01 | 1
20 | 5241 | 508 | 17135.5053 | 11547.8469 | 5587.6584 | 0.0113 | 2.9806 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 6.155 | 2016-03-11 | 10 | 2.717 | 2016-07-29 | 12 | 35.0222 | 2016-04-28 | 16 | 6.9667 | 2016-01-14 | 9 | 0.0142 | 2016-10-25 | 9 | 0 | 2016-01-01 | 1 | 41.26 | 2016-10-25 | 9 | 0 | 2016-01-01 | 1
21 | 4255 | 406 | 13460.0313 | 9310.0284 | 4150.0029 | 0.0113 | 2.8878 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 4174 | 401 | 13299.4125 | 8981.1702 | 4318.2423 | 0.0114 | 2.907 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 4120 | 396 | 13206.4998 | 8795.0517 | 4411.4481 | 0.0115 | 2.9244 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 4284 | 411 | 13780.0965 | 8815.2756 | 4964.8209 | 0.0117 | 2.9351 | 26.1111 | 25.1111 | 20.14 | 0.0178 | 0.0127 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3981.375 | 3125.2083 | 389.625 | 466.5417 | 13735.6308 | 9923.8042 | 3811.8266 | 0.011 | 3.9079 | 16.8333 | 24.9444
June 25 | 5202.2083 | 4263.7917 | 426.4583 | 511.9583 | 13805.4252 | 9993.5865 | 3811.8388 | 0.0115 | 2.9434 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3068.0417 | 2395.7917 | 311.8333 | 360.4167 | 9728.0501 | 9728.0501 | 0 | 0.0071 | 3.5928 | 16.8333 | 24.9444
June 25 | 3991.875 | 3256.4583 | 341.125 | 394.2917 | 9783.4338 | 9783.4093 | 0.024425 | 0.0077 | 2.7194 | 29.5 | 24.9444
DOE-2.2 NT42j, 17 Nov 2003
enter raw doe2 results below
bold entries not changed
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kBtu) | (Btu) | (kBtu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 25659 | 2312 | 10880 | 264468 |  | 73447 | 3.021 | 75.3 | 0.00921 | 48.27 | 67.8 | 0.0116 | E300 | 12771 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15 | 95 | 2016-07-20 | 15 | 0.0225 | 2016-10-02 | 9
E310 |  | 28612 | 2698 | 10880 | 333032 |  | 140371 | 3.4116 | 75.4 | 0.01126 | 58.5 |  |  | E310 | 13509 | 2016-07-20 | 15 | 23137 | 2016-06-04 | 16 | 15239 | 2016-09-03 | 15 | 37061 | 2016-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27975 | 2627 | 10880 | 330609 |  | 115508 | 3.4639 | 75.9 | 0.01006 | 51.24 |  |  | E320 | 13834 | 2016-07-20 | 15 | 31079 | 2016-04-24 | 16 | 31753 | 2016-10-02 | 9 | 54277 | 2016-10-02 | 9
E330 |  | 28566 | 2641 | 10880 | 346095 |  | 129007 | 3.5511 | 75.7 | 0.00987 | 50.64 |  |  | E330 | 14264 | 2016-07-20 | 15 | 34584 | 2016-06-14 | 15 | 42069 | 2016-10-02 | 9 | 66568 | 2016-10-02 | 9
E340 |  | 28431 | 2649 | 10880 | 339979 |  | 123643 | 3.5049 | 75.7 | 0.0099 | 50.72 |  |  | E340 | 14050 | 2016-07-20 | 15 | 32075 | 2016-05-16 | 16 | 36603 | 2016-10-02 | 9 | 60540 | 2016-10-02 | 9
E350 |  | 20023 | 1897 | 10880 | 221203 |  | 55546 | 3.238 | 79.1 | 0.00994 | 45.41 |  |  | E350 | 12481 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9396 | 2016-09-03 | 15 | 31475 | 2016-07-20 | 15
E360 |  | 43158 | 4184 | 10880 | 546771 |  | 85317 | 3.7133 | 78 | 0.0087 | 41.48 |  |  | E360 | 13618 | 2016-07-20 | 15 | 32075 | 2016-05-16 | 15 | 10378 | 2016-10-02 | 9 | 41228 | 2016-10-02 | 9
E400 |  | 20058 | 1871 | 10880 | 222211 |  | 80716 | 3.2471 | 75.3 | 0.01002 | 52.25 |  |  | E400 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 32593 | 2016-09-18 | 15 | 50141 | 2016-09-18 | 15
E410 |  | 20882 | 1974 | 10880 | 228417 |  | 65706 | 3.2061 | 75.3 | 0.00948 | 49.58 |  |  | E410 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E420 |  | 21724 | 2062 | 10880 | 237872 |  | 68234 | 3.2094 | 75.3 | 0.00938 | 49.13 |  |  | E420 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E430 |  | 21107 | 1998 | 10880 | 231011 |  | 67972 | 3.2079 | 75.3 | 0.00939 | 49.17 |  |  | E430 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 11147 | 2016-05-21 | 15 | 31476 | 2016-07-20 | 15
E440 |  | 22211 | 2115 | 10880 | 243776 |  | 71007 | 3.2169 | 75.3 | 0.00925 | 48.46 |  |  | E440 | 12482 | 2016-07-20 | 15 | 23226 | 2016-07-20 | 15 | 9397 | 2016-09-03 | 15 | 31476 | 2016-07-20 | 15
E500 |  | 20470 | 1979 | 2366 | 224937 |  | 62235 | 3.2208 | 69.2 | 0.00625 | 31.66 |  |  | E500 | 11226 | 2016-07-20 | 15 | 20017 | 2016-06-04 | 16 | 7621 | 2016-09-03 | 15 | 27638 | 2016-06-04 | 16
E500 May-Sep |  | 20470 | 1979 | 2366 | 224937 |  | 62235 | 3.2208 | 77 | 0.01133 | 57.34 |  |  | E510 | 12468 | 2016-07-20 | 15 | 22529 | 2016-07-20 | 15 | 8573 | 2016-09-09 | 8 | 31102 | 2016-07-20 | 15
E510 May-Sep |  | 38344 | 3720 | 4924 | 470275 |  | 130109 | 3.5948 | 77.2 | 0.0114 | 57.21 |  |  | E520 | 11920 | 2016-07-20 | 15 | 20163 | 2016-05-29 | 16 | 7621 | 2016-08-11 | 16 | 27784 | 2016-05-29 | 16
E520 |  | 22414 | 2385 | 2854 | 226568 |  | 62238 | 2.9628 | 56.8 | 0.00424 | 40.18 |  |  | E522 | 11834 | 2016-07-20 | 15 | 20153 | 2016-08-16 | 16 | 7621 | 2016-08-13 | 16 | 27774 | 2016-08-16 | 16
E522 |  | 21597 | 2185 | 2694 | 226052 |  | 62238 | 3.0678 | 63.1 | 0.00509 | 35.06 |  |  | E525 | 10224 | 2016-07-20 | 15 | 19834 | 2016-06-04 | 16 | 7621 | 2016-09-18 | 15 | 27455 | 2016-06-04 | 16
E525 |  | 18593 | 1649 | 1892 | 223322 |  | 62228 | 3.5204 | 81.3 | 0.00938 | 26.56 |  |  | E530 | 8735 | 2016-07-20 | 15 | 19585 | 2016-07-29 | 16 | 0 | 2016-09-03 | 16 | 19585 | 2016-07-29 | 16
E530 |  | 15773 | 1588 | 1835 | 159384 |  | 0 | 2.9617 | 69.1 | 0.00415 | 21.16 |  |  | E540 | 9745 | 2016-07-20 | 15 | 19802 | 2016-07-14 | 16 | 0 | 2016-08-15 | 15 | 19803 | 2016-07-14 | 16
E540 |  | 17683 | 1947 | 2261 | 161178 |  | 0 | 2.6716 | 56.8 | 0.00292 | 27.84 |  |  | E545 | 7920 | 2016-04-24 | 16 | 19463 | 2016-04-24 | 16 | 0 | 2016-08-11 | 15 | 19463 | 2016-04-24 | 16
E545 |  | 14351 | 1340 | 1506 | 157926 |  | 0 | 3.2254 | 81.3 | 0.00605 | 17.3
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 | [5 empty] | A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor | [5 empty] | C O P 2 |  |  |  |  | Indoor Drybulb Temperature | [5 empty] | Humidity Ratio | [5 empty] | Relative Humidity |  |  |  |  | Indoor Drybulb Temperature
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  | Maximum | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour | °F | °F
1 | 2313 | 238 | 25765 |  | 5665 | 0.0094 | 3.2649 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.628 | 2016-04-30 | 16 | 2.744 | 2016-12-28 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.17 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4 | 77.24 | 48.03
2 | 2359 | 241 | 26053 |  | 5331 | 0.0093 | 3.237 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.141 | 2016-04-30 | 16 | 2.842 | 2016-12-01 | 14 | 26.7 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0157 | 2016-10-02 | 1 | 0.0017 | 2016-01-04 | 24 | 78.57 | 2016-10-02 | 8 | 11.99 | 2016-11-06 | 4 | 80.06 | 48.03
3 | 2313 | 238 | 25775 |  | 5700 | 0.0094 | 3.2662 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 5.183 | 2016-10-02 | 9 | 2.796 | 2016-12-01 | 14 | 31.4889 | 2016-07-08 | 16 | 10.8444 | 2016-01-06 | 7 | 0.0176 | 2016-07-10 | 12 | 0.0017 | 2016-01-04 | 24 | 83.63 | 2016-10-02 | 9 | 11.99 | 2016-11-06 | 4 | 88.68 | 51.52
4 | 2310 | 237 | 25724 |  | 5657 | 0.0094 | 3.2639 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 6.304 | 2016-10-02 | 9 | 2.79 | 2016-12-01 | 14 | 32.0111 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0177 | 2016-07-10 | 13 | 0.0017 | 2016-01-04 | 24 | 78 | 2016-09-18 | 9 | 11.99 | 2016-11-06 | 4 | 89.62 | 48.03
5 | 2063 | 213 | 23034 |  | 3690 | 0.009 | 3.2725 | 63 | 74.8 |  | 0.0103 | 0.0091 | 30 | E340 | 5.734 | 2016-10-02 | 9 | 2.79 | 2016-12-01 | 14 | 31.5611 | 2016-07-08 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0174 | 2016-07-10 | 12 | 0.0017 | 2016-01-04 | 24 | 81.17 | 2016-09-18 | 9 | 11.99 | 2016-11-06 | 4 | 88.81 | 48.03
6 | 2556 | 263 | 28000 |  | 5978 | 0.0092 | 3.2108 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.9 | 2016-04-27 | 5 | 2.79 | 2016-12-01 | 14 | 34.9167 | 2016-06-25 | 7 | 8.9056 | 2016-01-06 | 6 | 0.0198 | 2016-10-01 | 21 | 0.0017 | 2016-01-04 | 24 | 81.1 | 2016-08-07 | 21 | 11.99 | 2016-11-06 | 4 | 94.85 | 48.03
7 | 3736 | 364 | 38523 |  | 9900 | 0.0098 | 3.0222 | 77 | 76.9 |  | 0.0133 | 0.0105 | 30 | E360 | 4.424 | 2016-10-04 | 24 | 2.79 | 2016-12-01 | 14 | 32.5222 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.17 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4 | 90.54 | 48.03
8 | 3573 | 331 | 35062 |  | 4112 | 0.0094 | 2.8762 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.873 | 2016-09-18 | 15 | 2.731 | 2016-12-03 | 14 | 28.7889 | 2016-09-18 | 16 | 8.9056 | 2016-01-06 | 6 | 0.017 | 2016-04-05 | 22 | 0.0017 | 2016-01-04 | 24 | 85.74 | 2016-04-05 | 21 | 11.99 | 2016-11-06 | 4 | 83.82 | 48.03
9 | 5067 | 474 | 50745 |  | 10147 | 0.0099 | 2.9353 | 84 | 78 |  | 0.0117 | 0.0102 | 30 | E410 | 3.864 | 2016-04-30 | 16 | 2.79 | 2016-12-01 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0169 | 2016-04-02 | 5 | 0.0017 | 2016-01-04 | 24 | 84.76 | 2016-04-02 | 5 | 11.99 | 2016-11-06 | 4 | 77.24 | 48.03
10 | 5264 | 483 | 52574 |  | 11446 | 0.0102 | 2.9273 | 84 | 78 |  | 0.0125 | 0.0106 | 30 | E420 | 3.77 | 2016-09-27 | 15 | 2.79 | 2016-12-01 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0147 | 2016-04-02 | 1 | 0.0017 | 2016-01-04 | 24 | 74.53 | 2016-04-17 | 7 | 11.99 | 2016-11-06 | 4 | 77.24 | 48.03
11 | 6120 | 549 | 60243 |  | 16374 | 0.0107 | 2.8852 | 88 | 78.6 |  | 0.0148 | 0.0115 | 30 | E430 | 3.808 | 2016-10-24 | 15 | 2.731 | 2016-12-03 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0156 | 2016-04-02 | 4 | 0.0017 | 2016-01-04 | 24 | 78.41 | 2016-04-02 | 4 | 11.99 | 2016-11-06 | 4 | 77.24 | 48.03
12 | 5696 | 497 | 55228 |  | 12206 | 0.0108 | 2.8419 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.769 | 2016-09-27 | 15 | 2.731 | 2016-12-03 | 14 | 25.1333 | 2016-07-20 | 16 | 8.9056 | 2016-01-06 | 6 | 0.0137 | 2016-11-16 | 16 | 0.0017 | 2016-01-04 | 24 | 69.15 | 2016-11-16 | 16 | 11.99 | 2016-11-06 | 4 | 77.24 | 48.03
13 | 6759 | 591 | 66901 |  | 8484 | 0.0102 | 2.9011 | 88 | 78.7 |  | 0.0115 | 0.0103 | 30 | E500 | 8.586 | 2016-03-11 | 10 | 2.687 | 2016-07-29 | 12 | 25.1 | 2016-07-29 | 16 | 6.6056 | 2016-01-14 | 9 | 0.0118 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.81 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1 | 77.18 | 43.89
14 | 7099 | 634 | 71064 |  | 10855 | 0.01 | 2.9341 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 8.585 | 2016-03-11 | 10 | 2.808 | 2016-04-05 | 17 | 25.1333 | 2016-07-20 | 15 | 6.6056 | 2016-01-14 | 9 | 0.0118 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.81 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1 | 77.24 | 43.89
15 | 8414 | 753 | 86664 |  | 10910 | 0.0098 | 3.0189 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 6.455 | 2016-03-28 | 20 | 2.201 | 2016-11-16 | 11 | 15.7722 | 2016-08-16 | 16 | 5.3944 | 2016-01-06 | 9 | 0.0075 | 2016-08-16 | 16 | 0 | 2016-01-01 | 1 | 70.13 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1 | 60.39 | 41.71
16 | 9018 | 811 | 94712 |  | 17714 | 0.0098 | 3.0783 | 90 | 79.1 |  | 0.0144 | 0.0106 | 29.9 | E522 | 6.182 | 2016-03-11 | 10 | 2.565 | 2016-07-29 | 12 | 20.1333 | 2016-08-16 | 16 | 6.0667 | 2016-01-06 | 9 | 0.0094 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 73.49 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1 | 68.24 | 42.92
17 | 6360 | 566 | 62339 |  | 15865 | 0.0107 | 2.8729 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 9.876 | 2016-03-11 | 10 | 2.937 | 2016-07-30 | 12 | 35.05 | 2016-06-04 | 16 | 6.9667 | 2016-01-14 | 9 | 0.0179 | 2016-07-20 | 15 | 0 | 2016-01-01 | 1 | 53.59 | 2016-03-11 | 10 | 0 | 2016-01-01 | 1 | 95.09 | 44.54
18 | 6290 | 548 | 61408 |  | 17572 | 0.0112 | 2.8615 | 88 | 78.7 |  | 0.0157 | 0.0119 | 29.9 | E530 | 4.81 | 2016-03-11 | 10 | 2.491 | 2016-07-29 | 12 | 25.0444 | 2016-07-29 | 16 | 6.6056 | 2016-01-14 | 9 | 0.0089 | 2016-10-23 | 9 | 0 | 2016-01-01 | 1 | 46.07 | 2016-10-23 | 9 | 0 | 2016-01-01 | 1 | 77.08 | 43.89
19 | 5483 | 476 | 54232 |  | 13780 | 0.0111 | 2.899 | 83 | 77.9 |  | 0.0143 | 0.0115 | 29.9 | E540 | 6.453 | 2016-03-28 | 20 | 2.201 | 2016-11-16 | 11 | 15.0889 | 2016-08-16 | 16 | 5.3944 | 2016-01-06 | 9 | 0.0052 | 2016-11-16 | 11 | 0 | 2016-01-01 | 1 | 50 | 2016-11-16 | 11 | 0 | 2016-01-01 | 1 | 59.16 | 41.71
20 | 5749 | 508 | 58463 |  | 19064 | 0.0113 | 2.9806 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 6.155 | 2016-03-11 | 10 | 2.717 | 2016-07-29 | 12 | 35.0222 | 2016-04-28 | 16 | 6.9667 | 2016-01-14 | 9 | 0.0142 | 2016-10-25 | 9 | 0 | 2016-01-01 | 1 | 41.26 | 2016-10-25 | 9 | 0 | 2016-01-01 | 1 | 95.04 | 44.54
21 | 4661 | 406 | 45923 |  | 14159 | 0.0113 | 2.8878 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30
22 | 4575 | 401 | 45375 |  | 14733 | 0.0114 | 2.907 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4516 | 396 | 45058 |  | 15051 | 0.0115 | 2.9244 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4695 | 411 | 47015 |  | 16939 | 0.0117 | 2.9351 | 79 | 77.2 |  | 0.0178 | 0.0127 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84356 | 9351 | 11197 | 1124719 |  | 312125 | 0.011 | 3.9079 | 62.3 | 76.9
June 25 |  | 112566 | 10235 | 12287 | 1130434 |  | 312126 | 0.0115 | 2.9434 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64983 | 7484 | 8650 | 796565 |  | 0 | 0.0071 | 3.5928 | 62.3 | 76.9
June 25 |  | 86342 | 8187 | 9463 | 801100 |  | 2 | 0.0077 | 2.7194 | 85.1 | 76.9