## A
Sec5-3Bout.xls
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
eQUEST 3.63b, build 6510 (contains DOE-2.2 version 47d), J.J. Hirsch & Assoc., July 21, 2009
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
eQUEST 3.63b |  | JJH | 21July2009
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34821 | 21632 | 2309 | 10880 | 77511.7605 | 55988.5482 | 21523.2123 | 3.2376 | 24.0556 | 0.00921 | 48.27 | 19.8889 | 0.0116 | E300 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15 | 35 | 2009-07-20 | 15 | 0.0225 | 2009-10-02 | 9
E310 | 39446 | 25872 | 2694 | 10880 | 97607.2827 | 56468.3529 | 41138.9298 | 3.4169 | 24.1111 | 0.01126 | 58.5 | ODB, OHR |  | E310 | 13493 | 2009-07-20 | 15 | 23136 | 2009-06-04 | 16 | 15237 | 2009-09-03 | 15 | 37057 | 2009-09-03 | 16 | from E500 |  |  | from E530
E320 | 38812 | 25308 | 2624 | 10880 | 96886.8429 | 63042.2928 | 33844.5501 | 3.4687 | 24.3889 | 0.01006 | 51.24 | from E500 |  | E320 | 13817 | 2009-07-20 | 15 | 31078 | 2009-04-24 | 16 | 31748 | 2009-10-02 | 9 | 54268 | 2009-10-02 | 9
E330 | 39399 | 25882 | 2637 | 10880 | 101421.9792 | 63624.3894 | 37797.5898 | 3.5563 | 24.2778 | 0.00987 | 50.64 |  |  | E330 | 14245 | 2009-07-20 | 15 | 34579 | 2009-06-14 | 15 | 42069 | 2009-10-02 | 9 | 66568 | 2009-10-02 | 9
E340 | 39266 | 25740 | 2646 | 10880 | 99631.7244 | 63403.9782 | 36227.7462 | 3.5099 | 24.2778 | 0.0099 | 50.72 |  |  | E340 | 14033 | 2009-07-20 | 15 | 32075 | 2009-05-16 | 16 | 36603 | 2009-10-02 | 9 | 60539 | 2009-10-02 | 9
E350 | 30871 | 18096 | 1895 | 10880 | 64830.789 | 48554.3598 | 16276.4292 | 3.243 | 26.1667 | 0.00994 | 45.41 |  |  | E350 | 12465 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9395 | 2009-09-03 | 15 | 31473 | 2009-07-20 | 15
E360 | 53976 | 38916 | 4180 | 10880 | 160236.8907 | 135243.9606 | 24992.9301 | 3.7181 | 25.5556 | 0.0087 | 41.48 |  |  | E360 | 13602 | 2009-07-20 | 15 | 32074 | 2009-05-16 | 15 | 10374 | 2009-10-02 | 9 | 41222 | 2009-10-02 | 9
E400 | 30889 | 18142 | 1867 | 10880 | 65059.9932 | 41461.3398 | 23598.6534 | 3.2515 | 24.0556 | 0.01002 | 52.25 |  |  | E400 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 32584 | 2009-09-18 | 15 | 50127 | 2009-09-18 | 15
E410 | 31703 | 18854 | 1969 | 10880 | 66862.8513 | 47687.6631 | 19175.1882 | 3.211 | 24.0556 | 0.00949 | 49.64 |  |  | E410 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E420 | 32569 | 19630 | 2059 | 10880 | 69716.4729 | 49720.6047 | 19995.8682 | 3.2144 | 24.0556 | 0.00938 | 49.13 |  |  | E420 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E430 | 31953 | 19078 | 1995 | 10880 | 67705.8069 | 47786.7309 | 19919.076 | 3.2129 | 24.0556 | 0.00939 | 49.18 |  |  | E430 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 11147 | 2009-05-21 | 15 | 31475 | 2009-07-20 | 15
E440 | 33055 | 20063 | 2112 | 10880 | 71446.9353 | 50638.3008 | 20808.6345 | 3.222 | 24.0556 | 0.00925 | 48.46 |  |  | E440 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E500 | 22805 | 18462 | 1976 | 2367 | 65929.6209 | 47688.5424 | 18241.0785 | 3.2258 | 20.6667 |  |  |  |  | E500 | 11213 | 2009-07-20 | 15 | 20018 | 2009-06-04 | 16 | 7621 | 2009-08-11 | 15 | 27639 | 2009-06-04 | 16
E500 May-Sep | 22805 | 18462 | 1976 | 2367 | 65929.6209 | 47688.5424 | 18241.0785 | 3.2258 | 25 | 0.01133 | 57.34 |  |  | E510 | 12454 | 2009-07-20 | 15 | 22530 | 2009-07-20 | 15 | 8573 | 2009-10-02 | 9 | 31103 | 2009-07-20 | 15
E510 May-Sep | 43217 | 34575 | 3716 | 4926 | 137838.7749 | 99703.827 | 38134.9479 | 3.5998 | 25.1111 | 0.0114 | 57.22 |  |  | E520 | 11908 | 2009-07-20 | 15 | 20163 | 2009-05-14 | 16 | 7621 | 2009-08-11 | 15 | 27784 | 2009-05-14 | 16
E520 | 25241 | 20004 | 2382 | 2855 | 66407.3739 | 48165.4161 | 18241.9578 | 2.9665 | 13.7778 |  |  |  |  | E522 | 11821 | 2009-07-20 | 15 | 20153 | 2009-08-16 | 16 | 7621 | 2009-08-15 | 15 | 27774 | 2009-08-16 | 16
E522 | 24260 | 19383 | 2182 | 2695 | 66256.4274 | 48014.4696 | 18241.9578 | 3.0724 | 17.2778 |  |  |  |  | E525 | 10210 | 2009-07-20 | 15 | 19834 | 2009-06-04 | 16 | 7621 | 2009-09-03 | 15 | 27455 | 2009-06-04 | 16
E525 | 20456 | 16916 | 1647 | 1893 | 65456.2644 | 47217.2376 | 18239.0268 | 3.5262 | 27.3889 |  |  |  |  | E530 | 8724 | 2009-07-20 | 15 | 19585 | 2009-07-29 | 16 | 0 | 2009-09-03 | 15 | 19585 | 2009-07-29 | 16
E530 | 17585 | 14163 | 1586 | 1836 | 46715.7435 | 46715.7435 | 0 | 2.9663 | 20.6111 |  |  |  |  | E540 | 9735 | 2009-07-20 | 15 | 19803 | 2009-07-14 | 16 | 0 | 2009-09-03 | 16 | 19803 | 2009-07-14 | 16
E540 | 19920 | 15714 | 1945 | 2261 | 47241.2718 | 47241.2718 | 0 | 2.6752 | 13.7778 |  |  |  |  | E545 | 7910 | 2009-04-24 | 16 | 19463 | 2009-04-24 | 16 | 0 | 2009-09-03 | 15 | 19463 | 2009-04-24 | 16
E545 | 15833 | 12989 | 1338 | 1506 | 46288.4037 | 46288.4037 | 0 | 3.2309 | 27.3333
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 | [5 empty] | A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor | [5 empty] | C O P 2 |  |  |  |  | Indoor Drybulb Temperature | [5 empty] | Humidity Ratio | [5 empty] | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1897 | 237 | 7551.4284 | 5891.6031 | 1659.8253 | 0.0094 | 3.5386 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.875 | 2009-04-30 | 16 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.18 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4
2 | 1941 | 241 | 7635.5481 | 6073.3251 | 1562.223 | 0.0093 | 3.4993 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.147 | 2009-04-30 | 16 | 2.847 | 2009-12-01 | 14 | 26.7056 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0157 | 2009-10-02 | 1 | 0.0017 | 2009-01-04 | 24 | 78.57 | 2009-10-02 | 8 | 11.99 | 2009-11-06 | 4
3 | 1897 | 238 | 7554.0663 | 5883.6894 | 1670.3769 | 0.0094 | 3.5382 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E320 | 5.189 | 2009-10-02 | 9 | 2.8 | 2009-12-01 | 14 | 31.4944 | 2009-07-08 | 16 | 10.8444 | 2009-01-06 | 7 | 0.0176 | 2009-07-10 | 12 | 0.0017 | 2009-01-04 | 24 | 83.63 | 2009-10-02 | 9 | 11.99 | 2009-11-06 | 4
4 | 1892 | 237 | 7539.1182 | 5881.3446 | 1657.7736 | 0.0094 | 3.5412 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E330 | 6.313 | 2009-10-02 | 9 | 2.795 | 2009-12-01 | 14 | 32.0167 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0177 | 2009-07-10 | 13 | 0.0017 | 2009-01-04 | 24 | 78 | 2009-09-18 | 9 | 11.99 | 2009-11-06 | 4
5 | 1682 | 212 | 6750.6792 | 5669.4333 | 1081.2459 | 0.009 | 3.5642 | 17.2222 | 23.7778 | 16.85 | 0.0103 | 0.0091 | 101593.5104 | E340 | 5.741 | 2009-10-02 | 9 | 2.795 | 2009-12-01 | 14 | 31.5667 | 2009-07-08 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0174 | 2009-07-10 | 12 | 0.0017 | 2009-01-04 | 24 | 81.17 | 2009-09-18 | 9 | 11.99 | 2009-11-06 | 4
6 | 2149 | 263 | 8206.5069 | 6454.6482 | 1751.8587 | 0.0092 | 3.4024 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.906 | 2009-04-27 | 5 | 2.795 | 2009-12-01 | 14 | 34.9167 | 2009-06-25 | 7 | 8.9056 | 2009-01-06 | 6 | 0.0198 | 2009-10-01 | 21 | 0.0017 | 2009-01-04 | 24 | 81.1 | 2009-08-07 | 21 | 11.99 | 2009-11-06 | 4
7 | 3280 | 364 | 11290.5051 | 8389.4013 | 2901.1038 | 0.0098 | 3.0984 | 25 | 24.9444 | 18.39 | 0.0133 | 0.0105 | 101593.5104 | E360 | 4.43 | 2009-10-04 | 24 | 2.795 | 2009-12-01 | 14 | 32.5278 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.18 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4
8 | 3129 | 331 | 10275.7929 | 9071.1519 | 1204.641 | 0.0094 | 2.9699 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.878 | 2009-09-18 | 15 | 2.735 | 2009-12-03 | 14 | 28.9556 | 2009-09-18 | 16 | 8.9056 | 2009-01-06 | 6 | 0.017 | 2009-04-05 | 22 | 0.0017 | 2009-01-04 | 24 | 85.74 | 2009-04-05 | 21 | 11.99 | 2009-11-06 | 4
9 | 4561 | 474 | 14872.4802 | 11899.2738 | 2973.2064 | 0.0099 | 2.9538 | 28.8889 | 25.5556 | 18.36 | 0.0117 | 0.0102 | 101593.5104 | E410 | 3.871 | 2009-04-30 | 16 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0169 | 2009-04-02 | 5 | 0.0017 | 2009-01-04 | 24 | 84.75 | 2009-04-02 | 5 | 11.99 | 2009-11-06 | 4
10 | 4679 | 482 | 15408.5601 | 12054.6168 | 3353.9433 | 0.0102 | 2.9856 | 28.8889 | 25.5556 | 18.68 | 0.0125 | 0.0106 | 101593.5104 | E420 | 3.775 | 2009-09-27 | 15 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0147 | 2009-04-01 | 21 | 0.0017 | 2009-01-04 | 24 | 74.53 | 2009-04-17 | 7 | 11.99 | 2009-11-06 | 4
11 | 5515 | 548 | 17656.344 | 12858.0039 | 4798.3401 | 0.0107 | 2.9121 | 31.1111 | 25.8889 | 19.48 | 0.0148 | 0.0115 | 101593.5104 | E430 | 3.814 | 2009-10-24 | 15 | 2.736 | 2009-12-03 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0156 | 2009-04-02 | 4 | 0.0017 | 2009-01-04 | 24 | 78.41 | 2009-04-02 | 4 | 11.99 | 2009-11-06 | 4
12 | 5008 | 496 | 16186.4475 | 12609.7482 | 3576.6993 | 0.0108 | 2.9409 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.775 | 2009-09-27 | 15 | 2.736 | 2009-12-03 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.15 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4
13 | 5995 | 591 | 19607.5107 | 17122.0227 | 2485.488 | 0.0102 | 2.9772 | 31.1111 | 25.9444 | 18.56 | 0.0115 | 0.0103 | 101593.5104 | E500 | 8.6 | 2009-03-11 | 10 | 2.691 | 2009-07-29 | 12 | 25.1 | 2009-07-29 | 16 | 6.5889 | 2009-01-14 | 9 | 0.0118 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.81 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1
14 | 6427 | 634 | 20827.3929 | 17646.9648 | 3180.4281 | 0.01 | 2.9496 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 8.599 | 2009-03-11 | 10 | 2.885 | 2009-10-18 | 15 | 25.1333 | 2009-07-20 | 15 | 6.5889 | 2009-01-14 | 9 | 0.0118 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.81 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1
15 | 7674 | 752 | 25399.7529 | 22203.4974 | 3196.2555 | 0.0098 | 3.0144 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 4.757 | 2009-03-11 | 10 | 2.464 | 2009-04-05 | 17 | 15.7778 | 2009-08-16 | 16 | 5.3778 | 2009-01-06 | 9 | 0.0075 | 2009-08-16 | 16 | 0 | 2009-01-01 | 1 | 70.15 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1
16 | 8256 | 811 | 27758.6217 | 22567.8207 | 5190.801 | 0.0098 | 3.0615 | 32.2222 | 26.1667 | 18.84 | 0.0144 | 0.0106 | 101254.8653 | E522 | 6.19 | 2009-03-11 | 10 | 2.569 | 2009-07-29 | 12 | 20.1333 | 2009-08-16 | 16 | 6.05 | 2009-01-06 | 9 | 0.0094 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.52 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1
17 | 5739 | 565 | 18270.3885 | 13621.2363 | 4649.1522 | 0.0107 | 2.8982 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 5.897 | 2009-04-12 | 9 | 2.941 | 2009-07-30 | 12 | 35.05 | 2009-06-04 | 16 | 6.95 | 2009-01-14 | 9 | 0.0179 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 53.59 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1
18 | 5562 | 547 | 17997.5124 | 12848.0385 | 5149.4739 | 0.0112 | 2.9461 | 31.1111 | 25.9444 | 19.75 | 0.0157 | 0.0119 | 101254.8653 | E530 | 4.818 | 2009-03-11 | 10 | 2.495 | 2009-07-29 | 12 | 25.0444 | 2009-07-29 | 16 | 6.5889 | 2009-01-14 | 9 | 0.0089 | 2009-10-23 | 9 | 0 | 2009-01-01 | 1 | 46.07 | 2009-10-23 | 9 | 0 | 2009-01-01 | 1
19 | 4666 | 475 | 15894.2268 | 11856.1881 | 4038.0387 | 0.0111 | 3.0917 | 28.3333 | 25.5 | 19.32 | 0.0143 | 0.0115 | 101254.8653 | E540 | 3.456 | 2009-04-30 | 16 | 2.262 | 2009-07-29 | 12 | 15.0889 | 2009-08-16 | 16 | 5.3778 | 2009-01-06 | 9 | 0.0052 | 2009-11-16 | 11 | 0 | 2009-01-01 | 1 | 50.02 | 2009-11-16 | 11 | 0 | 2009-01-01 | 1
20 | 4879 | 507 | 17134.626 | 11547.8469 | 5586.7791 | 0.0113 | 3.1813 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 4.142 | 2009-10-05 | 1 | 2.721 | 2009-07-29 | 12 | 35.0222 | 2009-04-28 | 16 | 6.95 | 2009-01-14 | 9 | 0.0142 | 2009-10-25 | 9 | 0 | 2009-01-01 | 1 | 41.26 | 2009-10-25 | 9 | 0 | 2009-01-01 | 1
21 | 3921 | 406 | 13459.152 | 9309.7353 | 4149.4167 | 0.0113 | 3.1105 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 3830 | 400 | 13298.5332 | 8981.1702 | 4317.363 | 0.0114 | 3.1439 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 3754 | 395 | 13205.9136 | 8795.3448 | 4410.5688 | 0.0115 | 3.1829 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 3898 | 410 | 13779.5103 | 8815.2756 | 4964.2347 | 0.0117 | 3.1986 | 26.1111 | 25.1111 | 20.14 | 0.0178 | 0.0127 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3976.0417 | 3120.25 | 389.1667 | 466.625 | 13735.7041 | 9923.8775 | 3811.8266 | 0.011 | 3.914 | 16.8333 | 24.9444
June 25 | 5195.1667 | 4257.0417 | 426 | 512.125 | 13805.5596 | 9993.7208 | 3811.8388 | 0.0115 | 2.948 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3064 | 2392.0417 | 311.4583 | 360.5 | 9728.0989 | 9728.0989 | 0 | 0.0071 | 3.5983 | 16.8333 | 24.9444
June 25 | 3986.4583 | 3251.375 | 340.7083 | 394.375 | 9783.4948 | 9783.4704 | 0.024425 | 0.0077 | 2.7236 | 29.5 | 24.9444
DOE-2.2 NT42j, 17 Nov 2003
enter raw doe2 results below
bold entries not changed
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kBtu) | (Btu) | (kBtu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 23941 | 2309 | 10880 | 264455 |  | 73433 | 3.2376 | 75.3 | 0.00921 | 48.27 | 67.8 | 0.0116 | E300 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15 | 95 | 2009-07-20 | 15 | 0.0225 | 2009-10-02 | 9
E310 |  | 28566 | 2694 | 10880 | 333017 |  | 140358 | 3.4169 | 75.4 | 0.01126 | 58.5 |  |  | E310 | 13493 | 2009-07-20 | 15 | 23136 | 2009-06-04 | 16 | 15237 | 2009-09-03 | 15 | 37057 | 2009-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27932 | 2624 | 10880 | 330559 |  | 115471 | 3.4687 | 75.9 | 0.01006 | 51.24 |  |  | E320 | 13817 | 2009-07-20 | 15 | 31078 | 2009-04-24 | 16 | 31748 | 2009-10-02 | 9 | 54268 | 2009-10-02 | 9
E330 |  | 28519 | 2637 | 10880 | 346032 |  | 128958 | 3.5563 | 75.7 | 0.00987 | 50.64 |  |  | E330 | 14245 | 2009-07-20 | 15 | 34579 | 2009-06-14 | 15 | 42069 | 2009-10-02 | 9 | 66568 | 2009-10-02 | 9
E340 |  | 28386 | 2646 | 10880 | 339924 |  | 123602 | 3.5099 | 75.7 | 0.0099 | 50.72 |  |  | E340 | 14033 | 2009-07-20 | 15 | 32075 | 2009-05-16 | 16 | 36603 | 2009-10-02 | 9 | 60539 | 2009-10-02 | 9
E350 |  | 19991 | 1895 | 10880 | 221190 |  | 55532 | 3.243 | 79.1 | 0.00994 | 45.41 |  |  | E350 | 12465 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9395 | 2009-09-03 | 15 | 31473 | 2009-07-20 | 15
E360 |  | 43096 | 4180 | 10880 | 546697 |  | 85271 | 3.7181 | 78 | 0.0087 | 41.48 |  |  | E360 | 13602 | 2009-07-20 | 15 | 32074 | 2009-05-16 | 15 | 10374 | 2009-10-02 | 9 | 41222 | 2009-10-02 | 9
E400 |  | 20009 | 1867 | 10880 | 221972 |  | 80514 | 3.2515 | 75.3 | 0.01002 | 52.25 |  |  | E400 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 32584 | 2009-09-18 | 15 | 50127 | 2009-09-18 | 15
E410 |  | 20823 | 1969 | 10880 | 228123 |  | 65422 | 3.211 | 75.3 | 0.00949 | 49.64 |  |  | E410 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E420 |  | 21689 | 2059 | 10880 | 237859 |  | 68222 | 3.2144 | 75.3 | 0.00938 | 49.13 |  |  | E420 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E430 |  | 21073 | 1995 | 10880 | 230999 |  | 67960 | 3.2129 | 75.3 | 0.00939 | 49.18 |  |  | E430 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 11147 | 2009-05-21 | 15 | 31475 | 2009-07-20 | 15
E440 |  | 22175 | 2112 | 10880 | 243763 |  | 70995 | 3.222 | 75.3 | 0.00925 | 48.46 |  |  | E440 | 12466 | 2009-07-20 | 15 | 23226 | 2009-07-20 | 15 | 9396 | 2009-09-03 | 15 | 31475 | 2009-07-20 | 15
E500 |  | 20438 | 1976 | 2367 | 224939 |  | 62235 | 3.2258 | 69.2 | 0.00625 | 31.66 |  |  | E500 | 11213 | 2009-07-20 | 15 | 20018 | 2009-06-04 | 16 | 7621 | 2009-08-11 | 15 | 27639 | 2009-06-04 | 16
E500 May-Sep |  | 20438 | 1976 | 2367 | 224939 |  | 62235 | 3.2258 | 77 | 0.01133 | 57.34 |  |  | E510 | 12454 | 2009-07-20 | 15 | 22530 | 2009-07-20 | 15 | 8573 | 2009-10-02 | 9 | 31103 | 2009-07-20 | 15
E510 May-Sep |  | 38291 | 3716 | 4926 | 470279 |  | 130109 | 3.5998 | 77.2 | 0.0114 | 57.22 |  |  | E520 | 11908 | 2009-07-20 | 15 | 20163 | 2009-05-14 | 16 | 7621 | 2009-08-11 | 15 | 27784 | 2009-05-14 | 16
E520 |  | 22386 | 2382 | 2855 | 226569 |  | 62238 | 2.9665 | 56.8 | 0.00424 | 40.16 |  |  | E522 | 11821 | 2009-07-20 | 15 | 20153 | 2009-08-16 | 16 | 7621 | 2009-08-15 | 15 | 27774 | 2009-08-16 | 16
E522 |  | 21565 | 2182 | 2695 | 226054 |  | 62238 | 3.0724 | 63.1 | 0.00509 | 35.06 |  |  | E525 | 10210 | 2009-07-20 | 15 | 19834 | 2009-06-04 | 16 | 7621 | 2009-09-03 | 15 | 27455 | 2009-06-04 | 16
E525 |  | 18563 | 1647 | 1893 | 223324 |  | 62228 | 3.5262 | 81.3 | 0.00938 | 26.57 |  |  | E530 | 8724 | 2009-07-20 | 15 | 19585 | 2009-07-29 | 16 | 0 | 2009-09-03 | 15 | 19585 | 2009-07-29 | 16
E530 |  | 15749 | 1586 | 1836 | 159385 |  | 0 | 2.9663 | 69.1 | 0.00415 | 21.17 |  |  | E540 | 9735 | 2009-07-20 | 15 | 19803 | 2009-07-14 | 16 | 0 | 2009-09-03 | 16 | 19803 | 2009-07-14 | 16
E540 |  | 17659 | 1945 | 2261 | 161178 |  | 0 | 2.6752 | 56.8 | 0.00292 | 27.83 |  |  | E545 | 7910 | 2009-04-24 | 16 | 19463 | 2009-04-24 | 16 | 0 | 2009-09-03 | 15 | 19463 | 2009-04-24 | 16
E545 |  | 14327 | 1338 | 1506 | 157927 |  | 0 | 3.2309 | 81.2 | 0.00605 | 17.3
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 | [5 empty] | A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor | [5 empty] | C O P 2 |  |  |  |  | Indoor Drybulb Temperature | [5 empty] | Humidity Ratio | [5 empty] | Relative Humidity |  |  |  |  | Indoor Drybulb Temperature
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum |  | Maximum | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour | °F | °F
1 | 2134 | 237 | 25764 |  | 5663 | 0.0094 | 3.5386 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.875 | 2009-04-30 | 16 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.18 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4 | 77.24 | 48.03
2 | 2182 | 241 | 26051 |  | 5330 | 0.0093 | 3.4993 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.147 | 2009-04-30 | 16 | 2.847 | 2009-12-01 | 14 | 26.7056 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0157 | 2009-10-02 | 1 | 0.0017 | 2009-01-04 | 24 | 78.57 | 2009-10-02 | 8 | 11.99 | 2009-11-06 | 4 | 80.07 | 48.03
3 | 2135 | 238 | 25773 |  | 5699 | 0.0094 | 3.5382 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 5.189 | 2009-10-02 | 9 | 2.8 | 2009-12-01 | 14 | 31.4944 | 2009-07-08 | 16 | 10.8444 | 2009-01-06 | 7 | 0.0176 | 2009-07-10 | 12 | 0.0017 | 2009-01-04 | 24 | 83.63 | 2009-10-02 | 9 | 11.99 | 2009-11-06 | 4 | 88.69 | 51.52
4 | 2129 | 237 | 25722 |  | 5656 | 0.0094 | 3.5412 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 6.313 | 2009-10-02 | 9 | 2.795 | 2009-12-01 | 14 | 32.0167 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0177 | 2009-07-10 | 13 | 0.0017 | 2009-01-04 | 24 | 78 | 2009-09-18 | 9 | 11.99 | 2009-11-06 | 4 | 89.63 | 48.03
5 | 1894 | 212 | 23032 |  | 3689 | 0.009 | 3.5642 | 63 | 74.8 |  | 0.0103 | 0.0091 | 30 | E340 | 5.741 | 2009-10-02 | 9 | 2.795 | 2009-12-01 | 14 | 31.5667 | 2009-07-08 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0174 | 2009-07-10 | 12 | 0.0017 | 2009-01-04 | 24 | 81.17 | 2009-09-18 | 9 | 11.99 | 2009-11-06 | 4 | 88.82 | 48.03
6 | 2412 | 263 | 27999 |  | 5977 | 0.0092 | 3.4024 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.906 | 2009-04-27 | 5 | 2.795 | 2009-12-01 | 14 | 34.9167 | 2009-06-25 | 7 | 8.9056 | 2009-01-06 | 6 | 0.0198 | 2009-10-01 | 21 | 0.0017 | 2009-01-04 | 24 | 81.1 | 2009-08-07 | 21 | 11.99 | 2009-11-06 | 4 | 94.85 | 48.03
7 | 3644 | 364 | 38521 |  | 9898 | 0.0098 | 3.0984 | 77 | 76.9 |  | 0.0133 | 0.0105 | 30 | E360 | 4.43 | 2009-10-04 | 24 | 2.795 | 2009-12-01 | 14 | 32.5278 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.18 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4 | 90.55 | 48.03
8 | 3460 | 331 | 35059 |  | 4110 | 0.0094 | 2.9699 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.878 | 2009-09-18 | 15 | 2.735 | 2009-12-03 | 14 | 28.9556 | 2009-09-18 | 16 | 8.9056 | 2009-01-06 | 6 | 0.017 | 2009-04-05 | 22 | 0.0017 | 2009-01-04 | 24 | 85.74 | 2009-04-05 | 21 | 11.99 | 2009-11-06 | 4 | 84.12 | 48.03
9 | 5035 | 474 | 50742 |  | 10144 | 0.0099 | 2.9538 | 84 | 78 |  | 0.0117 | 0.0102 | 30 | E410 | 3.871 | 2009-04-30 | 16 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0169 | 2009-04-02 | 5 | 0.0017 | 2009-01-04 | 24 | 84.75 | 2009-04-02 | 5 | 11.99 | 2009-11-06 | 4 | 77.24 | 48.03
10 | 5161 | 482 | 52571 |  | 11443 | 0.0102 | 2.9856 | 84 | 78 |  | 0.0125 | 0.0106 | 30 | E420 | 3.775 | 2009-09-27 | 15 | 2.795 | 2009-12-01 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0147 | 2009-04-01 | 21 | 0.0017 | 2009-01-04 | 24 | 74.53 | 2009-04-17 | 7 | 11.99 | 2009-11-06 | 4 | 77.24 | 48.03
11 | 6063 | 548 | 60240 |  | 16371 | 0.0107 | 2.9121 | 88 | 78.6 |  | 0.0148 | 0.0115 | 30 | E430 | 3.814 | 2009-10-24 | 15 | 2.736 | 2009-12-03 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0156 | 2009-04-02 | 4 | 0.0017 | 2009-01-04 | 24 | 78.41 | 2009-04-02 | 4 | 11.99 | 2009-11-06 | 4 | 77.24 | 48.03
12 | 5504 | 496 | 55225 |  | 12203 | 0.0108 | 2.9409 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.775 | 2009-09-27 | 15 | 2.736 | 2009-12-03 | 14 | 25.1333 | 2009-07-20 | 16 | 8.9056 | 2009-01-06 | 6 | 0.0137 | 2009-11-16 | 16 | 0.0017 | 2009-01-04 | 24 | 69.15 | 2009-11-16 | 16 | 11.99 | 2009-11-06 | 4 | 77.24 | 48.03
13 | 6586 | 591 | 66897 |  | 8480 | 0.0102 | 2.9772 | 88 | 78.7 |  | 0.0115 | 0.0103 | 30 | E500 | 8.6 | 2009-03-11 | 10 | 2.691 | 2009-07-29 | 12 | 25.1 | 2009-07-29 | 16 | 6.5889 | 2009-01-14 | 9 | 0.0118 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.81 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1 | 77.18 | 43.86
14 | 7061 | 634 | 71059 |  | 10851 | 0.01 | 2.9496 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 8.599 | 2009-03-11 | 10 | 2.885 | 2009-10-18 | 15 | 25.1333 | 2009-07-20 | 15 | 6.5889 | 2009-01-14 | 9 | 0.0118 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.81 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1 | 77.24 | 43.86
15 | 8426 | 752 | 86659 |  | 10905 | 0.0098 | 3.0144 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 4.757 | 2009-03-11 | 10 | 2.464 | 2009-04-05 | 17 | 15.7778 | 2009-08-16 | 16 | 5.3778 | 2009-01-06 | 9 | 0.0075 | 2009-08-16 | 16 | 0 | 2009-01-01 | 1 | 70.15 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1 | 60.4 | 41.68
16 | 9067 | 811 | 94707 |  | 17710 | 0.0098 | 3.0615 | 90 | 79.1 |  | 0.0144 | 0.0106 | 29.9 | E522 | 6.19 | 2009-03-11 | 10 | 2.569 | 2009-07-29 | 12 | 20.1333 | 2009-08-16 | 16 | 6.05 | 2009-01-06 | 9 | 0.0094 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 73.52 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1 | 68.24 | 42.89
17 | 6304 | 565 | 62335 |  | 15862 | 0.0107 | 2.8982 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 5.897 | 2009-04-12 | 9 | 2.941 | 2009-07-30 | 12 | 35.05 | 2009-06-04 | 16 | 6.95 | 2009-01-14 | 9 | 0.0179 | 2009-07-20 | 15 | 0 | 2009-01-01 | 1 | 53.59 | 2009-03-11 | 10 | 0 | 2009-01-01 | 1 | 95.09 | 44.51
18 | 6109 | 547 | 61404 |  | 17569 | 0.0112 | 2.9461 | 88 | 78.7 |  | 0.0157 | 0.0119 | 29.9 | E530 | 4.818 | 2009-03-11 | 10 | 2.495 | 2009-07-29 | 12 | 25.0444 | 2009-07-29 | 16 | 6.5889 | 2009-01-14 | 9 | 0.0089 | 2009-10-23 | 9 | 0 | 2009-01-01 | 1 | 46.07 | 2009-10-23 | 9 | 0 | 2009-01-01 | 1 | 77.08 | 43.86
19 | 5141 | 475 | 54228 |  | 13777 | 0.0111 | 3.0917 | 83 | 77.9 |  | 0.0143 | 0.0115 | 29.9 | E540 | 3.456 | 2009-04-30 | 16 | 2.262 | 2009-07-29 | 12 | 15.0889 | 2009-08-16 | 16 | 5.3778 | 2009-01-06 | 9 | 0.0052 | 2009-11-16 | 11 | 0 | 2009-01-01 | 1 | 50.02 | 2009-11-16 | 11 | 0 | 2009-01-01 | 1 | 59.16 | 41.68
20 | 5386 | 507 | 58460 |  | 19061 | 0.0113 | 3.1813 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 4.142 | 2009-10-05 | 1 | 2.721 | 2009-07-29 | 12 | 35.0222 | 2009-04-28 | 16 | 6.95 | 2009-01-14 | 9 | 0.0142 | 2009-10-25 | 9 | 0 | 2009-01-01 | 1 | 41.26 | 2009-10-25 | 9 | 0 | 2009-01-01 | 1 | 95.04 | 44.51
21 | 4327 | 406 | 45920 |  | 14157 | 0.0113 | 3.1105 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30
22 | 4230 | 400 | 45372 |  | 14730 | 0.0114 | 3.1439 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4149 | 395 | 45056 |  | 15048 | 0.0115 | 3.1829 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4308 | 410 | 47013 |  | 16937 | 0.0117 | 3.1986 | 79 | 77.2 |  | 0.0178 | 0.0127 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84226 | 9340 | 11199 | 1124725 |  | 312125 | 0.011 | 3.914 | 62.3 | 76.9
June 25 |  | 112393 | 10224 | 12291 | 1130445 |  | 312126 | 0.0115 | 2.948 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64884 | 7475 | 8652 | 796569 |  | 0 | 0.0071 | 3.5983 | 62.3 | 76.9
June 25 |  | 86210 | 8177 | 9465 | 801105 |  | 2 | 0.0077 | 2.7236 | 85.1 | 76.9